## Sheet1
Subsystem | Tag Number | Punch Item | Status Text | Description | Category | Discipline | Resp.Champion | Action by | Created Date | Raised By | Raised During Phase | Cleared Date | Cleared by: | Verified Date | Verified by:
AFS-01 | AFS-01 | PI17127 | Verified | Missing caps on fill line at Ammonia Unloading Skid | C | P | William Mitchell | McD | 2020-02-19 | William Mitchell | Comm | 2020-04-20 | William Mitchell | 2020-05-12 | Randy Carpenter
AFS-01 | AFS-01 | PI17128 | Verified | Clean out containment under Ammonia Unloading grating platform | C | C | Alan Huntsman | McD | 2020-02-19 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-03-26 | John Watts
AFS-01 | AFS-01 | PI17129 | Verified | Remove unused metal materials from Ammonia Unloading grating platform | C | C | Alan Huntsman | McD | 2020-02-19 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-03-26 | John Watts
AFS-01 | AFS-01 | PI18109 | Cleared | 10-AFS-LIT-0105 - The local level is about 6% off from the level transmitter, which is correct reading. | C | I | Albert Burge | McD | 2020-03-20 | Albert Burge | Comm | 2020-04-21 | Chris Colvin | 2021-07-28 | John Watts
AFS-01 | AFS-01 | PI17126 | Verified | Quad Scan label is upside down | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-05-12 | Randy Carpenter
AFS-01 | AFS-01 | PI17125 | Verified | Install permanent labels at Control Panel, West side of Ammonia Unloading Skid | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-05-12 | Randy Carpenter
AFS-01 | AFS-01 | PI15840 | Verified | 1A-CTS-PD-P41-0320-03 Modify piping Vent per REV FR-01 | B | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Const | 2020-02-02 | Charlie English | 2020-02-03 | Kelvin Cook
AFS-01 | AFS-01 | PI04820 | Verified | The ladder on the ammonia tank does not meet OSHA regulations. Angle Iron within 7" of ladder rungs. The top rung of ladder is not level with platform causing tripping hazard. | B | S | Bobby Williams | McD | 2019-09-09 | Bobby Williams | Comm |  |  | 2019-12-09 | Michael Law
AFS-01 | AFS-01 | PI04718 | Verified | 10-AFS-SKD-0130 Aqueous Ammonia Skid is labeled for Saint Charles, needs the correct name plate. | C | M | Joshua Sturgeon | McD | 2019-09-03 | Joshua Sturgeon | Const | 2019-10-18 | Joshua Sturgeon | 2019-10-28 | Shannon Scott
AFS-01 | AFS-01 | PI03817 | Verified | Complete pipe test & submit CCFs to turnover. | A | P | Terry Deaton | McD | 2019-08-13 | Terry Deaton | Const | 2019-08-13 | Ed Gober | 2019-08-13 | Ed Gober
AFS-01 | AFS-01 | PI03412 | Verified | 2" blind flange to be installed at nozzle #1 from the north to south | A | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-14 | Kelvin Cook
AFS-01 | AFS-01 | PI03411 | Verified | 10-AFS-RC-0100 Not installed "Rain Cap" | B | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-14 | Kelvin Cook
AFS-01 | AFS-01 | PI03410 | Verified | AFS valve 610 Blind flange | A | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-14 | Kelvin Cook
AFS-01 | AFS-01 | PI03409 | Verified | 1" flange. 8th from North valve ( No blind) | A | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-14 | Kelvin Cook
AFS-01 | AFS-01 | PI03408 | Verified | 2" Blind flange. 4th from North not installed | A | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-14 | Kelvin Cook
AFS-01 | AFS-01 | PI03407 | Verified | Complete rework on level gauge 10-AFS-LG-0103. | A | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
AFS-01 | AFS-01 | PI03406 | Verified | Missing "Pull To Activate" button on unloading panel. | A | E | Mike Tabbert | McD | 2019-08-09 | Mike Tabbert | Const | 2019-08-21 | Mike Tabbert | 2019-08-21 | Mike Tabbert
AFS-01 | AFS-01 | PI03405 | Verified | Remove trash from ammonia tank top platform. | B | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-14 | Kelvin Cook
AFS-01 | AFS-01 | PI03404 | Verified | Need longer bolts on conduit support on ammonia skid platform. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-14 | Mike Tabbert
AFS-01 | AFS-01 | PI03403 | Verified | Conduit ground clamp beeds a bolt - in ammonia storage containment. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-14 | Mike Tabbert
AFS-01 | AFS-01 | PI03402 | Verified | Install weights on vacuum breaker. | B | M | Joshua Sturgeon | McD | 2019-08-09 | Joshua Sturgeon | Const | 2019-08-20 | Joshua Sturgeon | 2019-12-09 | J.L. Bickham
AFS-01 | AFS-01 | PI03401 | Verified | Tighten ammonia tank anchor bolts - 10-AFS-T-0150. | B | M | Shane Crowe | McD | 2019-08-09 | Shane Crowe | Const | 2019-08-09 | Shane Crowe | 2019-09-18 | Kelvin Cook
AFS-01 | AFS-01 | PI03400 | Verified | Resolve positioner indicator colors on 10-AFS-AOV-0135, 145 & 155. | B | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-11-08 | Gonzalo Pena | 2019-11-21 | Albert Burge
AFS-01 | AFS-01 | PI03399 | Verified | Install grounds on motors 10-AFS-M-0150A & B. | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-15 | Martin Perry
AFS-01 | AFS-01 | PI03398 | Verified | Install emergency pull cable / handle. The "handle holder" welded to guardrail is in contact with a PRV and should be moved. | A | M | Joshua Sturgeon | McD | 2019-08-09 | Joshua Sturgeon | Const | 2019-08-23 | Joshua Sturgeon | 2019-08-24 | Albert Burge
AFS-01 | AFS-01 | PI12810 | Verified | 10-AFS-PD-P41-0106-01 install check valve to remove high point in piping | B | P | Bobby Williams | McD | 2019-11-06 | Bobby Williams | Comm | 2019-11-22 | Bobby Williams | 2019-11-23 | Kelvin Cook
AFS-01 | AFS-01 | PI09731 | Verified | Ammonia Emergency Pull Station needs relocated to southeast side of stairs, current location in front of the ammonia unloading station. | D | M | Michael Law | McD | 2019-10-21 | Michael Law | Comm | 2020-02-10 | Fred Michael | 2020-03-26 | John Watts
AFS-01 | AFS-01 | PI09730 | Verified | 10-AFS-P-0150A & 10-AFS-P-0150B - was an issue @ SCPS with priming the pumps, construction to re-route suction piping to remove high point @ LCPS. | B | P | Bobby Williams | McD | 2019-10-21 | Bobby Williams | Comm | 2019-11-22 | Bobby Williams | 2019-12-11 | Shannon Scott
AFS-02 | AFS-02 | PI02956 | Verified | 1AAFSK0001, Motor space heater cable for 1A-AFS-M-8101A, terminate after temp power removed. | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
AFS-02 | AFS-02 | PI03018 | Verified | Unplug drains under skid | B | M | Johnny Campbell | McD | 2019-08-01 | Johnny Campbell | Const | 2019-08-09 | Johnny Campbell | 2019-12-09 | J.L. Bickham
AFS-02 | AFS-02 | PI03020 | Verified | Spring can need to set to cold setting | A | P | Bobby Williams | McD | 2019-08-01 | Bobby Williams | Const | 2019-08-06 | Bobby Williams | 2019-08-06 | John Schanno
AFS-02 | AFS-02 | PI03022 | Verified | Drill holes in base of skid so it can drain properly | D | C | Michael Law | McD | 2019-08-01 | Michael Law | Const | 2019-09-24 | Michael Law | 2020-01-15 | Michael Law
AFS-02 | AFS-02 | PI03026 | Verified | Remove debris from piping | B | P | James Beech | McD | 2019-08-01 | James Beech | Const | 2019-08-09 | Terry Deaton | 2019-12-09 | J.L. Bickham
AFS-02 | AFS-02 | PI03029 | Verified | Pressure gauge on distribution header is out of calibration | B | I | John Schanno | McD | 2019-08-01 | John Schanno | Const |  |  | 2019-08-24 | Albert Burge
AFS-02 | AFS-02 | PI03031 | Verified | Complete installation of all differential gauges | A | I | Gonzalo Pena | McD | 2019-08-01 | Gonzalo Pena | Const | 2019-08-06 | Gonzalo Pena | 2019-12-09 | J.L. Bickham
AFS-02 | AFS-02 | PI02957 | Verified | 1AAFSK0002, Motor space heater cable for 1A-AFS-M-8101B, terminate after temp power removed. | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
AFS-02 | AFS-02 | PI02958 | Verified | 1A-AFS-M-8101B, ground motor to skid. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-02 | AFS-02 | PI02959 | Verified | 1A-AFS-M-8101B, ground not long enough on motor feeder sealtight. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-02 | AFS-02 | PI03005 | Verified | Cannot read grid differential. PDI's are unaccessible | D | I | Gonzalo Pena | McD | 2019-08-01 | Gonzalo Pena | Const | 2019-09-24 | Michael Law | 2019-12-01 | Albert Burge
AFS-02 | AFS-02 | PI03009 | Verified | Both gear boxes on skid need oil | B | M | Jonathan Lishka | McD | 2019-08-01 | Jonathan Lishka | Const | 2019-08-09 | Joshua Sturgeon | 2019-12-09 | J.L. Bickham
AFS-02 | AFS-02 | PI03016 | Verified | Clean and pump out foundation underneath skid | B | M | Johnny Campbell | McD | 2019-08-01 | Johnny Campbell | Const | 2019-08-09 | Johnny Campbell | 2019-12-09 | J.L. Bickham
AFS-02 | AFS-02 | PI02960 | Verified | 1A-AFS-M-8101B, install 3" plug motor connection box. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-02 | AFS-02 | PI02961 | Verified | 1A-AFS-M-8101B, Cut point off of motor termination boot keeper pin, all three phases. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-07 | Mike Tabbert
AFS-02 | AFS-02 | PI02962 | Verified | 1A-AFS-M-8101B, install correct ground lug at motor connection box. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-07 | Mike Tabbert
AFS-02 | AFS-02 | PI02963 | Verified | 1A-AFS-M-8101A, ground motor to skid. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-02 | AFS-02 | PI17762 | Verified | 1A-AFS-FV-8103 needs vendor valve tag replaced with the new CV Rating of 1.0 | C | P | Mike Tabbert | McD | 2020-03-10 | Mike Tabbert | Const | 2020-05-06 | Mike Tabbert | 2020-05-12 | Randy Carpenter
AFS-02 | AFS-02 | PI02964 | Verified | 1A-AFS-M-8101A, Cut point off of motor termination boot keeper pin, all three phases. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-07 | Mike Tabbert
AFS-03 | AFS-03 | PI02978 | Verified | 1BAFSK0001, 1B-AFS-M-8101A space heater cable to be terminated when temporary power removed from heater. | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
AFS-03 | AFS-03 | PI02979 | Verified | 1BAFSK0002, 1B-AFS-M-8101B space heater cable to be terminated when temporary power removed from heater. | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
AFS-03 | AFS-03 | PI02980 | Verified | 1B-AFS-M-8101B, missing bolts in motor connection box | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-09 | Mike Tabbert
AFS-03 | AFS-03 | PI02981 | Verified | 1B-AFS-M-8101B, Cut points off of term kit keepers for all three phases. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI02982 | Verified | 1B-AFS-M-8101B, ground motor feed sealtight | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI02983 | Verified | 1B-AFS-M-8101B, ground motor heater sealtight term cable. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI02984 | Verified | 1B-AFS-M-8101B, feeder cables need to be straightened out in cable tarys going to HRSG PDC B. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-06 | Dustin Futrell | 2019-08-09 | Mike Tabbert
AFS-03 | AFS-03 | PI02985 | Verified | 1B-AFS-M-8101B, install correct ground lug inside motor connection box | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI02986 | Verified | 1B-AFS-M-8101B, plug 3" hole in motor connection box. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI02987 | Verified | 1B-AFS-M-8101B, ground motor to skid. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI02988 | Verified | 1B-AFS-M-8101A, Cut points off of term kit keepers for all three phases. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-07 | Mike Tabbert
AFS-03 | AFS-03 | PI02989 | Verified | 1B-AFS-M-8101A, ground motor to skid. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI02990 | Verified | 1B-AFS-M-8101A, plug 3" hole in motor connection box. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI02991 | Verified | 1B-AFS-M-8101A, install correct ground lug inside motor connection box | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI02992 | Verified | 1B-AFS-M-8101A, ground motor heater sealtight term cable. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI02993 | Verified | 1B-AFS-M-8101A, feeder cables need to be straightened out | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-06 | Dustin Futrell | 2019-08-09 | Mike Tabbert
AFS-03 | AFS-03 | PI02994 | Verified | 1B-AFS-JB-8101, Seal Conduits in J-Box. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI02995 | Verified | 1B-AFS-JB-8101, ground term points in j-box as per marked-up drawing. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-09 | Mike Tabbert
AFS-03 | AFS-03 | PI02996 | Verified | 1B-AFS-JB-8101 clean out inside of panel | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI02997 | Verified | 1BTL121001 and 1BTC121001, Cable tray needs lables back to PDC | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-07 | Ken Mundy | 2019-08-09 | Mike Tabbert
AFS-03 | AFS-03 | PI02998 | Verified | 1BTL121001 and 1BTC121001, All cable tray supports need to be grouted. | C | C | Johnny Campbell | McD | 2019-08-01 | Johnny Campbell | Const | 2019-10-10 | Jack Fields | 2019-12-01 | Fred Michael
AFS-03 | AFS-03 | PI02999 | Verified | 1BTL121001 and 1BTC121001, Cable tray needs to be grounded back to HRSG PDC. | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-07 | Ken Mundy | 2019-08-09 | Mike Tabbert
AFS-03 | AFS-03 | PI03000 | Verified | 1BTL121001 and 1BTC121001, Top cable tray missing barrier. | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-09 | Dustin Futrell | 2019-08-09 | Mike Tabbert
AFS-03 | AFS-03 | PI03001 | Verified | 1BTL121001 and 1BTC121001, Cable trays need hold down clamps installed back to HRSG PDC. | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI03002 | Verified | Turn in all completion paperwork | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-15 | Mike Tabbert
AFS-03 | AFS-03 | PI03003 | Verified | Install condulet covers on all conduits at AFS-03 skid | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-03 | AFS-03 | PI03004 | Verified | Remove rope from piping | C | P | James Beech | McD | 2019-08-01 | James Beech | Const | 2019-08-12 | Terry Deaton | 2020-01-21 | Michael Law
AFS-03 | AFS-03 | PI03006 | Verified | Cannot read grid differential. PDI's are unaccessible | D | I | Michael Law | McD | 2019-08-01 | Michael Law | Const | 2019-09-24 | Michael Law | 2019-12-01 | Albert Burge
AFS-03 | AFS-03 | PI03008 | Verified | Connect motor heater on skid to permanent power | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-19 | Albert Burge
AFS-03 | AFS-03 | PI03010 | Verified | Both gear boxes on skid need oil | B | M | Jonathan Lishka | McD | 2019-08-01 | Jonathan Lishka | Const | 2019-08-09 | Jonathan Lishka | 2019-12-09 | J.L. Bickham
AFS-03 | AFS-03 | PI03011 | Verified | Missing condulet covers around skid | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-07 | Mike Tabbert
AFS-03 | AFS-03 | PI03012 | Verified | Missing valve handle VB2253 | B | M | Joshua Sturgeon | McD | 2019-08-01 | Joshua Sturgeon | Const | 2019-08-22 | Joshua Sturgeon | 2019-08-24 | Albert Burge
AFS-02 | AFS-02 | PI02965 | Verified | 1A-AFS-M-8101A, install correct ground lug at motor connection box. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-07 | Mike Tabbert
AFS-02 | AFS-02 | PI02966 | Verified | 1A-AFS-M-8101A, install 3" plug motor connection box. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-02 | AFS-02 | PI02967 | Verified | 1ATL121001 and 1ATC121001, Ground cable tray back to HRSG PDC. | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-09 | Dustin Futrell | 2019-08-13 | Mike Tabbert
AFS-02 | AFS-02 | PI02968 | Verified | 1ATL121001 and 1ATC121001, Install cable tray hold down clamps on vertical tray going to HRSG PDC. | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-02 | AFS-02 | PI02969 | Verified | 1ATL121001 and 1ATC121001, Trim all tie raps in cable tray. | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-13 | Mike Tabbert
AFS-02 | AFS-02 | PI02970 | Verified | Motor feeder cables under HRSG B need to be straightened out and tie rap neatly in place. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-21 | Mike Tabbert
AFS-02 | AFS-02 | PI02971 | Verified | 1ATL121001 and 1ATC121001, Cable tray needs threaded rods cut to length. | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-13 | Mike Tabbert
AFS-02 | AFS-02 | PI02972 | Verified | 1ATL121001 and 1ATC121001, All cable tray supports need to be grouted. | C | C | Johnny Campbell | McD | 2019-08-01 | Johnny Campbell | Const | 2019-10-10 | Johnny Campbell | 2019-12-13 | Mike Tabbert
AFS-02 | AFS-02 | PI02973 | Verified | 1A-AFS-JB-8101, clean inside panel. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-02 | AFS-02 | PI02974 | Verified | 1A-AFS-JB-8101, Seal conduits in panel. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-02 | AFS-02 | PI02975 | Verified | 1A-AFS-JB-8101, ground terminal points in JB as per marked up drawing. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-13 | Mike Tabbert
AFS-02 | AFS-02 | PI02976 | Verified | Install condulet covers on all conduits at AFS-02 skid. | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-05 | Mike Tabbert
AFS-02 | AFS-02 | PI02977 | Verified | Turn in all completion paper work. | A | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-14 | Mike Tabbert
AFS-02 | AFS-02 | PI03033 | Verified | All pipe supports around skid need to be grouted | C | C | Johnny Campbell | McD | 2019-08-01 | Johnny Campbell | Const | 2019-10-22 | Johnny Campbell | 2020-01-15 | Michael Law
AFS-02 | AFS-02 | PI03035 | Verified | Nuts missing off of pipe support | B | P | James Beech | McD | 2019-08-01 | James Beech | Const | 2019-08-12 | Terry Deaton | 2019-12-09 | J.L. Bickham
AFS-02 | AFS-02 | PI03036 | Verified | No tags on valves - Tag All Valves | C | P | Bobby Williams | McD | 2019-08-01 | Bobby Williams | Const | 2020-02-19 | Bobby Williams | 2020-03-09 | Michael Law
AFS-02 | AFS-02 | PI03037 | Verified | Valve 8111A and 8110B had broken pressure gauges | A | I | Gonzalo Pena | McD | 2019-08-01 | Gonzalo Pena | Const | 2019-08-20 | Gonzalo Pena | 2019-08-24 | Albert Burge
AFS-02 | AFS-02 | PI03038 | Verified | Expansion joint SPEJ-021 has too much deflection | A | P | Bobby Williams | McD | 2019-08-01 | Bobby Williams | Const | 2019-08-09 | Bobby Williams | 2019-09-23 | Shannon Scott
AFS-02 | AFS-02 | PI03039 | Verified | Instrument Air line on the skid is not tight | A | P | Terry Deaton | McD | 2019-08-01 | Terry Deaton | Const | 2019-08-02 | Terry Deaton | 2019-08-07 | Albert Burge
AFS-02 | AFS-02 | PI03060 | Verified | Grease motors. | B | M | Jonathan Lishka | McD | 2019-08-02 | Jonathan Lishka | Const | 2019-08-09 | Jonathan Lishka | 2019-08-09 | Joshua Sturgeon
AFS-02 | AFS-02 | PI03316 | Verified | Testing of pipe | A | P | Bobby Williams | McD | 2019-08-07 | Bobby Williams | Const | 2019-08-13 | Bobby Williams | 2019-08-13 | Michael Law
AFS-02 | AFS-02 | PI04246 | Verified | After commissioning motor run-in, construction to complete alignment and submit CCFs M14A & M49A for 1AFS-BLW-8101A. | B | M | Shane Crowe | McD | 2019-08-14 | Shane Crowe | Const | 2019-08-28 | Joshua Sturgeon | 2019-10-04 | Joshua Sturgeon
AFS-02 | AFS-02 | PI04248 | Verified | After commissioning motor run-in, construction to complete alignment and submit CCFs M14A & M49A for 1AFS-BLW-8101B. | B | M | Shane Crowe | McD | 2019-08-14 | Shane Crowe | Const | 2019-08-28 | Joshua Sturgeon | 2019-10-04 | Joshua Sturgeon
AFS-02 | AFS-02 | PI17856 | Verified | 1A-MBS-TI-8904B 1A CO Catalyst Inlet Temp reads 57.8 deg F and Bad Quality. | C | E | Albert Burge | McD | 2020-03-16 | Albert Burge | Comm | 2020-03-19 | Albert Burge | 2020-03-26 | Keith Pollock
AFS-03 | AFS-03 | PI03013 | Verified | Strainer 8101A & 8101B should be stainless | B | M | Joshua Sturgeon | McD | 2019-08-01 | Joshua Sturgeon | Const | 2019-08-15 | Joshua Sturgeon | 2019-08-15 | Martin Perry
AFS-03 | AFS-03 | PI03014 | Verified | Clean inside 1B-AFS-JB-8101 | B | E | Dustin Futrell | McD | 2019-08-01 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-08-07 | Mike Tabbert
AFS-03 | AFS-03 | PI03015 | Verified | Tag all devices & hoses on skid | C | I | Tim Gallegos | McD | 2019-08-01 | Tim Gallegos | Const | 2020-05-07 | Tim Gallegos | 2020-05-12 | Randy Carpenter
AFS-03 | AFS-03 | PI03017 | Verified | Clean and pump out sump | B | M | Johnny Campbell | McD | 2019-08-01 | Johnny Campbell | Const | 2019-08-13 | Johnny Campbell | 2019-12-09 | J.L. Bickham
AFS-03 | AFS-03 | PI03019 | Verified | Unplug drains under skid | B | M | Johnny Campbell | McD | 2019-08-01 | Johnny Campbell | Const | 2019-08-13 | Johnny Campbell | 2019-12-09 | J.L. Bickham
AFS-03 | AFS-03 | PI03021 | Verified | Spring can need to set to cold setting | A | P | Bobby Williams | McD | 2019-08-01 | Bobby Williams | Const | 2019-08-06 | Bobby Williams | 2019-08-06 | John Schanno
AFS-03 | AFS-03 | PI03023 | Verified | Drill holes in base of skid so it can drain properly | D | C | Michael Law | McD | 2019-08-01 | Michael Law | Const | 2019-09-24 | Michael Law | 2020-01-15 | Michael Law
AFS-03 | AFS-03 | PI03027 | Verified | Remove debris from piping | B | P | James Beech | McD | 2019-08-01 | James Beech | Const | 2019-08-09 | Terry Deaton | 2019-12-09 | J.L. Bickham
AFS-03 | AFS-03 | PI03028 | Verified | Fix wire tags to prevent puncturing on skid | C | M | Joshua Sturgeon | McD | 2019-08-01 | Joshua Sturgeon | Const | 2019-09-13 | Joshua Sturgeon | 2019-09-25 | Shannon Scott
AFS-03 | AFS-03 | PI03030 | Verified | Install all tubing from orifice flanes to differential gauges on all 12 locations | A | I | Gonzalo Pena | McD | 2019-08-01 | Gonzalo Pena | Const | 2019-08-06 | Gonzalo Pena | 2019-12-09 | J.L. Bickham
AFS-03 | AFS-03 | PI03032 | Verified | Complete installation of all differential gauges | A | I | Gonzalo Pena | McD | 2019-08-01 | Gonzalo Pena | Const | 2019-08-07 | Gonzalo Pena | 2019-12-09 | J.L. Bickham
AFS-03 | AFS-03 | PI03034 | Verified | All pipe supports around skid need to be grouted | C | C | Johnny Campbell | McD | 2019-08-01 | Johnny Campbell | Const | 2019-10-22 | Johnny Campbell | 2020-01-15 | Michael Law
AFS-03 | AFS-03 | PI03061 | Verified | Grease motors. | B | M | Jonathan Lishka | McD | 2019-08-02 | Jonathan Lishka | Const | 2019-08-09 | Jonathan Lishka | 2019-08-09 | Joshua Sturgeon
AFS-03 | AFS-03 | PI03317 | Verified | Testing of pipe | A | P | Bobby Williams | McD | 2019-08-07 | Bobby Williams | Const | 2019-08-13 | Bobby Williams | 2019-08-13 | Michael Law
AFS-03 | AFS-03 | PI04247 | Verified | After commissioning motor run-in, construction to complete alignment and submit CCFs M14A & M49A for 1BFS-BLW-8101A. | B | M | Shane Crowe | McD | 2019-08-14 | Shane Crowe | Const | 2019-08-28 | Joshua Sturgeon | 2019-10-04 | Joshua Sturgeon
AFS-03 | AFS-03 | PI04249 | Verified | After commissioning motor run-in, construction to complete alignment and submit CCFs M14A & M49A for 1BFS-BLW-8101B. | B | M | Shane Crowe | McD | 2019-08-14 | Shane Crowe | Const | 2019-08-28 | Joshua Sturgeon | 2019-10-04 | Joshua Sturgeon
AFS-03 | AFS-03 | PI17130 | Verified | PaintAmmonia Flow Control Unit B skid components | C | X | Johnny Campbell | McD | 2020-02-19 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
AFS-03 | AFS-03 | PI17131 | Verified | Tag all .5 inch valves | C | P | James Beech | McD | 2020-02-19 | James Beech | Comm | 2020-04-13 | James Beech | 2020-05-12 | Randy Carpenter
AFS-03 | AFS-03 | PI17132 | Verified | Clean up skid | C | C | Johnny Campbell | McD | 2020-02-19 | Johnny Campbell | Comm | 2020-04-08 | Johnny Campbell | 2020-05-12 | Randy Carpenter
AFS-03 | AFS-03 | PI17133 | Verified | Jacking bolt not flush with frame at Ammonia Blower B Motor | C | M | Shane Crowe | McD | 2020-02-19 | Shane Crowe | Comm | 2020-03-19 | Shane Crowe | 2020-03-31 | Randy Carpenter
AFS-03 | AFS-03 | PI17134 | Verified | Ammonia Blower A & B Motor cables need bushing ground at cable tray | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-05-15 | Chris Colvin | 2020-05-26 | Randy Carpenter
AFS-03 | AFS-03 | PI17662 | Verified | 1B-AFS-PI-8107 - 1B's Ammonia Dilution Blower local gauge is broken - need to order 4/7 | C | I | James Beech | McD | 2020-03-04 | James Beech | Comm | 2020-05-19 | Tim Green | 2020-06-03 | John Watts
AFS-03 | AFS-03 | PI17763 | Verified | 1B-AFS-FV-8103 needs vendor valve tag replaced with the new CV Rating of 1.0 | C | P | Mike Tabbert | McD | 2020-03-10 | Mike Tabbert | Const | 2020-05-06 | Mike Tabbert | 2020-05-12 | Randy Carpenter
ARC-01 | ARC-01 | PI02577 | Verified | LK-1C-ARC-PD-P41-0003-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-03 | Damon Turner | 2019-08-03 | Tom Noble
ARC-01 | ARC-01 | PI02578 | Verified | LK-1C-ARC-PD-P41-0016-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-03 | Damon Turner | 2019-08-03 | Tom Noble
ARC-01 | ARC-01 | PI03062 | Verified | Grout pipe supports at skids 1C-ARC-SKD-0100A & B. | C | C | Johnny Campbell | McD | 2019-08-03 | Johnny Campbell | Const | 2019-10-10 | Jack Fields | 2019-11-23 | Kelvin Cook
ARC-01 | ARC-01 | PI03063 | Verified | Seal conduit in 1C-ARC-CP-0101A & B at the Condenser Vacuum Pump Skids. | B | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-13 | Mike Tabbert
ARC-01 | ARC-01 | PI03064 | Verified | Ground seal tite on Condenser Vacuum Pump Skids - 1C-ARC-SKD-0100A & B. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-06 | Dustin Futrell | 2019-08-13 | Mike Tabbert
ARC-01 | ARC-01 | PI03065 | Verified | Seal/caulk grounds at concrete penetrations at Condenser Vacuum Pump Skids 1C-ARC-SKD-0100A & B. | C | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-14 | Mike Tabbert | 2019-08-14 | Mike Tabbert
ARC-01 | ARC-01 | PI03066 | Verified | Install sight glass on Condenser Vacuum Pump Skids 1C-ARC-SKD-0100A & B. | B | M | Joshua Sturgeon | McD | 2019-08-03 | Joshua Sturgeon | Const | 2019-08-07 | Kelvin Cook | 2019-08-07 | Kelvin Cook
ARC-01 | ARC-01 | PI03067 | Verified | Drain line (tubing) is bent on Condenser Vacuum Pump Skid 1C-ARC-0100B. | B | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2020-01-31 | Gonzalo Pena | 2020-02-25 | John Watts
ARC-01 | ARC-01 | PI03068 | Verified | Install cap on drains on Condenser Vacuum Pump Skids 1C-ARC-SKD-0100A & B. | B | P | Damon Turner | McD | 2019-08-03 | Damon Turner | Const | 2019-08-20 | Terry Deaton | 2019-08-27 | Kelvin Cook
ARC-01 | ARC-01 | PI03069 | Verified | Install bird screens on 1" vent line on Condenser Vacuum Pump Skids 1C-ARC-SKD-0100A & B. | C | P | Damon Turner | McD | 2019-08-03 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-27 | Kelvin Cook
ARC-01 | ARC-01 | PI03073 | Verified | 1CARCK0001, Terminate Cable | B | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-21 | Fred Michael
ARC-01 | ARC-01 | PI03074 | Verified | 1CARCK0003, Terminate Cable | B | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-21 | Fred Michael
ARC-01 | ARC-01 | PI03075 | Verified | 1CARCK0005, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-24 | Dustin Futrell | 2019-08-24 | Mike Tabbert
ARC-01 | ARC-01 | PI03076 | Verified | 1CARCK0006, Terminate Cable | B | E | Chris Boudreaux | McD | 2019-08-03 | Chris Boudreaux | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
ARC-01 | ARC-01 | PI03077 | Verified | 1CARCX0001, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-24 | Dustin Futrell | 2019-08-24 | Mike Tabbert
ARC-01 | ARC-01 | PI03078 | Verified | 1CARCX0002, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-24 | Dustin Futrell | 2019-08-24 | Mike Tabbert
ARC-01 | ARC-01 | PI03079 | Verified | 1CARCX0003, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-24 | Dustin Futrell | 2019-08-24 | Mike Tabbert
ARC-01 | ARC-01 | PI03080 | Verified | 1CARCX0004, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-24 | Dustin Futrell | 2019-08-24 | Mike Tabbert
ARC-01 | ARC-01 | PI03081 | Verified | 1CARCX0005, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-24 | Dustin Futrell | 2019-08-24 | Mike Tabbert
ARC-01 | ARC-01 | PI03082 | Verified | 10DCSX0152, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-24 | Dustin Futrell | 2019-08-24 | Mike Tabbert
ARC-01 | ARC-01 | PI03083 | Verified | 10DCSX0153, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-24 | Dustin Futrell | 2019-08-24 | Mike Tabbert
ARC-01 | ARC-01 | PI03084 | Verified | 1CARCX0006, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-26 | Mike Tabbert
ARC-01 | ARC-01 | PI03085 | Verified | 1C-ARC-CP-1000 not installed | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Mike Tabbert
ARC-01 | ARC-01 | PI03086 | Verified | 1C-ARC-JB-0001 not installed | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Mike Tabbert
ARC-01 | ARC-01 | PI03087 | Verified | 1C-ARC-JB-0002 not installed | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Mike Tabbert
ARC-01 | ARC-01 | PI03088 | Verified | 1C-ARC-JB-0003 not installed | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Mike Tabbert
ARC-01 | ARC-01 | PI03089 | Verified | 1C-ARC-AIT-0001 not installed | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-23 | Gonzalo Pena | 2019-08-23 | Mike Tabbert
ARC-01 | ARC-01 | PI03090 | Verified | 1C-ARC-AIT-0002 not installed | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-23 | Gonzalo Pena | 2019-08-23 | Mike Tabbert
ARC-01 | ARC-01 | PI03091 | Verified | 1C-ARC-AIT-0003 not installed | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-23 | Gonzalo Pena | 2019-08-23 | Mike Tabbert
ARC-01 | ARC-01 | PI03092 | Verified | 1C-ARC-PNL-0001 not installed | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-23 | Gonzalo Pena | 2019-08-23 | Mike Tabbert
ARC-01 | ARC-01 | PI03093 | Verified | Vacuum skid A & B, Tie duct bank ground to ground grid and tie sealtight ground to duct ban ground. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-06 | Dustin Futrell | 2019-08-09 | Mike Tabbert
ARC-01 | ARC-01 | PI03094 | Verified | Vacuum skid A & B, Grounds not installed on vendor supplied sealtight. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-09 | Dustin Futrell | 2019-08-09 | Mike Tabbert
ARC-01 | ARC-01 | PI03095 | Verified | Vacuum skid A, Ground door panels of 1C-ARC-CP-0101A/B | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-09 | Dustin Futrell | 2019-08-09 | Mike Tabbert
ARC-01 | ARC-01 | PI03096 | Verified | Vacuum skid B vendor conduit straps broken and conduit deformed. | B | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-07 | Ken Mundy | 2019-08-09 | Mike Tabbert
ARC-01 | ARC-01 | PI03097 | Verified | Vacuum skid B needs grid ground connected at north west corner. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-14 | Mike Tabbert
ARC-01 | ARC-01 | PI03098 | Verified | Turn in all completion paperwork. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-28 | Mike Tabbert | 2019-08-28 | Mike Tabbert
ARC-01 | ARC-01 | PI03099 | Verified | Install, 1C-ARC-AOV-0128A | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-06 | Gonzalo Pena | 2019-08-14 | Mike Tabbert
ARC-01 | ARC-01 | PI03100 | Verified | Install, 1C-ARC-AOV-0128B | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-06 | Gonzalo Pena | 2019-08-14 | Mike Tabbert
ARC-01 | ARC-01 | PI03101 | Verified | Install, 1C-ARC-LG-0126A | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-06 | Gonzalo Pena | 2019-08-14 | Mike Tabbert
ARC-01 | ARC-01 | PI03102 | Verified | Install, 1C-ARC-LG-0126B | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-06 | Gonzalo Pena | 2019-08-14 | Mike Tabbert
ARC-01 | ARC-01 | PI03103 | Verified | Install, 1C-ARC-TI-0129B | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-06 | Gonzalo Pena | 2019-08-09 | Mike Tabbert
ARC-01 | ARC-01 | PI03104 | Verified | Install, 1C-ARC-TI-0129A | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-06 | Gonzalo Pena | 2019-08-09 | Mike Tabbert
ARC-01 | ARC-01 | PI03105 | Verified | Install, 1C-ARC-PI-0133A | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-06 | Gonzalo Pena | 2019-08-14 | Mike Tabbert
ARC-01 | ARC-01 | PI03106 | Verified | Install, 1C-ARC-PI-0133B | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-06 | Gonzalo Pena | 2019-08-14 | Mike Tabbert
ARC-01 | ARC-01 | PI03216 | Verified | 1C-ARC-LV-0135A solenoid coil is missing plate and red hat. This allows the coil to fall off. Should coil come off it will burn up. | A | I | Gonzalo Pena | McD | 2019-08-06 | Gonzalo Pena | Const | 2019-08-20 | Gonzalo Pena | 2019-08-21 | Albert Burge
ARC-01 | ARC-01 | PI03217 | Verified | 1C-ARC-FV-0105A/B and 1C-ARC-AOV-0128A/B these 4 valves have the wrong indicators on the valves. Presently they are green is open and red is closed. | B | I | Gonzalo Pena | McD | 2019-08-06 | Gonzalo Pena | Const |  |  | 2019-12-03 | James Tanner
ARC-01 | ARC-01 | PI03818 | Verified | Complete pipe test & submit CCFs to turnover. | A | P | Damon Turner | McD | 2019-08-13 | Damon Turner | Const | 2019-08-28 | Kelvin Cook | 2019-08-28 | Ed Gober
ARC-01 | ARC-01 | PI04598 | Verified | On ISO 1C-ARC-PD-P40-0002-03 install eng supports per iso detail | B | P | Damon Turner | McD | 2019-08-24 | Damon Turner | Const | 2019-08-28 | Damon Turner | 2019-09-18 | Kelvin Cook
ARC-01 | ARC-01 | PI04609 | Verified | Missing fuse RHEO VAC Inst. Box on the STG mezz level. | B | I | Billy Williams | McD | 2019-08-24 | Billy Williams | Const |  |  | 2020-02-18 | Albert Burge
ARC-01 | ARC-01 | PI04610 | Verified | Replace media converter in 1C-ARC-PNL-0001 on the STG mezz level. | A | I | Sheri Fritz | ITS | 2019-08-24 | Sheri Fritz | Const | 2019-08-27 | Michael Law | 2019-08-27 | Mike Tabbert
ARC-01 | ARC-01 | PI04611 | Verified | Ground door on 1C-ARC-PNL-0001 and back plate on the STG mezz level. | A | E | Dustin Futrell | McD | 2019-08-24 | Dustin Futrell | Const | 2019-08-24 | Dustin Futrell | 2019-08-28 | Mike Tabbert
ARC-01 | ARC-01 | PI04612 | Verified | Install power jumper in 1C-ARC-PNL-0001 on the STG mezz level. | B | E | Jonathan Donham | McD | 2019-08-24 | Jonathan Donham | Const |  |  | 2020-02-19 | Michael Law
ARC-01 | ARC-01 | PI04613 | Verified | Terminate Cat 6 cable in RHEO VAC Inst. Box on the STG mezz level. | A | E | Sheri Fritz | ITS | 2019-08-24 | Sheri Fritz | Const | 2019-08-27 | Michael Law | 2019-08-27 | Mike Tabbert
ARC-01 | ARC-01 | PI04614 | Verified | Ground 1C-ARC-CP-0101A at ARC skid. | A | E | Dustin Futrell | McD | 2019-08-24 | Dustin Futrell | Const | 2019-08-24 | Dustin Futrell | 2019-09-04 | Logan Holland
ARC-01 | ARC-01 | PI04615 | Verified | Ground 1C-ARC-CP-0101B at ARC skid. | A | E | Dustin Futrell | McD | 2019-08-24 | Dustin Futrell | Const | 2019-08-24 | Dustin Futrell | 2019-09-04 | Logan Holland
ARC-01 | ARC-01 | PI04616 | Verified | Termination box for 1C-ARC-M-0100B missing 1 screw. | A | E | Dustin Futrell | McD | 2019-08-24 | Dustin Futrell | Const | 2019-08-24 | Dustin Futrell | 2019-09-04 | Logan Holland
ARC-01 | ARC-01 | PI04617 | Verified | Ground center conduit on duct bank for 1C-ARC-M-0100B. | A | E | Dustin Futrell | McD | 2019-08-24 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-04 | Logan Holland
ARC-01 | ARC-01 | PI04618 | Verified | Conduit to 1C-ARC-CP-0101B needs low point drain or weep hole. | A | E | Dustin Futrell | McD | 2019-08-24 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-04 | Logan Holland
ARC-01 | ARC-01 | PI04619 | Verified | Conduit to 1C-ARC-CP-0101A needs low point drain or weep hole. | A | E | Dustin Futrell | McD | 2019-08-24 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-04 | Logan Holland
ARC-01 | ARC-01 | PI04620 | Verified | Conduit to 1C-ARC-LSL-127B needs low point drain or weep hole. | A | E | Dustin Futrell | McD | 2019-08-24 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-04 | Logan Holland
ARC-01 | ARC-01 | PI04621 | Verified | Conduit to 1C-ARC-LSL-127A needs low point drain or weep hole. | A | E | Dustin Futrell | McD | 2019-08-24 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-04 | Logan Holland
ARC-01 | ARC-01 | PI16891 | Verified | Fitting leaking at .5 inch vent line upstream of, at 1st joint below top of vent, 1C-RD-P-0118A, Vacuum Pump A skid | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-03-31 | James Beech | 2020-04-07 | Bernard Stasse
ARC-01 | ARC-01 | PI16892 | Verified | 6" System Discharge Vent needs birdscreen, Line No. 6-1C-ARC-0005, at 1C Condenser Vacuum Pump Skid A | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-03-27 | James Beech | 2020-04-02 | John Watts
ARC-01 | ARC-01 | PI16893 | Verified | 6" System Discharge Vent needs birdscreen, Line No. 6-1C-ARC-0015, at 1C Condenser Vacuum Pump Skid B | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-03-27 | James Beech | 2020-04-02 | John Watts
ARC-01 | ARC-01 | PI16894 | Verified | Remove rope, wire, tie wraps, and old unused tags througout system | C | P | Johnny Campbell | McD | 2020-02-18 | Johnny Campbell | Comm | 2020-03-11 | Alan Huntsman | 2020-04-02 | John Watts
ARC-01 | ARC-01 | PI16895 | Verified | All valve actuator position indicators need to be changed, RED to should indicate OPEN and GREEN should indicate CLOSED | C | I | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-04-29 | James Beech | 2020-05-12 | Keith Pollock
ARC-01 | ARC-01 | PI16896 | Verified | Touch up paint at both skids | C | X | Jerry Smith | McD | 2020-02-18 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-04-02 | John Watts
ARC-01 | ARC-01 | PI16897 | Verified | Heat shrink wire tags inside 1C-ARC-CP-0101A; Vacuum Pump A Control Panel | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-04-01 | Chris Colvin | 2020-04-07 | Bernard Stasse
ARC-01 | ARC-01 | PI16898 | Verified | Heat shrink wire tags inside 1C-ARC-CP-0101B; Vacuum Pump B Control Panel | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-04-01 | Chris Colvin | 2020-04-07 | Bernard Stasse
ASF-01 | ASF-01 | PI09777 | Verified | Test Package ASF-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-25 | Kelvin Cook
ASF-01 | ASF-01 | PI09778 | Verified | Test Package ASF-T-02 need to be in service | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-10 | Kelvin Cook
ASF-01 | ASF-01 | PI12704 | Verified | Rotate handwheel 180 deg. on valve 1C-ASF-V-0010. | A | P | James Beech | McD | 2019-11-01 | James Beech | Const | 2019-11-15 | James Beech | 2019-11-16 | Alex Isaac
ASF-01 | ASF-01 | PI12705 | Verified | Rotate handwheel 180 deg. on valve 1C-ASF-V-0017. | A | P | James Beech | McD | 2019-11-01 | James Beech | Const | 2019-11-15 | James Beech | 2019-11-16 | Alex Isaac
ASF-01 | ASF-01 | PI13070 | Verified | Remove start-up trim and install final trim on valve 1C-ASF-AOV-0085 (AFTER STEAM BLOW) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-10 | Shane Copeland
ASF-01 | ASF-01 | PI13071 | Verified | Remove start-up trim and install final trim on valve 1C-ASF-PV-0015 (AFTER STEAM BLOW) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-10 | Shane Copeland
ASF-01 | ASF-01 | PI13072 | Verified | Remove start-up trim and install final trim on valve 1C-ASF-PV-0035 (AFTER STEAM BLOW) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-10 | Shane Copeland
ASF-01 | ASF-01 | PI13166 | Verified | Missing threaded cap on drain at 1C-ASF-V-0069. STG mezz east side. | A | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-08 | James Beech | 2019-12-14 | Kelvin Cook
ASF-01 | ASF-01 | PI13167 | Verified | Complete all insulation required for first fire PPE. | C | Q | Sheri Fritz | PCI | 2019-11-20 | Sheri Fritz | Const | 2019-12-23 | Michael Law | 2020-01-08 | Blake Boudreaux
ASF-01 | ASF-01 | PI13168 | Verified | ISO 1C-ASF-0060 - first support off of "T" - install shim. STG mezz east side. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2020-01-07 | James Beech | 2020-01-08 | Ethan Byrd
ASF-01 | ASF-01 | PI13169 | Verified | ISO 1C-ASF-0060 - replace bent all thread rod. STG mezz east side. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2020-01-07 | James Beech | 2020-01-08 | Ethan Byrd
ASF-01 | ASF-01 | PI13170 | Verified | 4" pipe - plumb all supports, tighten all nuts per detail. STG mezz side. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2020-01-07 | James Beech | 2020-01-08 | Ethan Byrd
ASF-01 | ASF-01 | PI13171 | Verified | Grout all pipe supports on the STG operating deck. | C | C | Alan Huntsman | McD | 2019-11-20 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-02-19 | Michael Law
ASF-01 | ASF-01 | PI13172 | Verified | ASF-HRG-0021 - two missing clamps & loose clamp. STG operating deck north side. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2020-01-07 | James Beech | 2020-01-08 | Ethan Byrd
ASF-01 | ASF-01 | PI13173 | Verified | Line 1C-ASF-0020 - verify all supports are installed per design. STG operating deck north side. | A | P | Kelvin Cook | McD | 2019-11-20 | Kelvin Cook | Const | 2019-11-25 | Kelvin Cook | 2019-12-13 | Blake Boudreaux
ASF-01 | ASF-01 | PI13174 | Verified | 1C-ASF-0026-P41 not installed. STG operating deck north side. | A | P | James Beech | McD | 2019-11-20 | James Beech | Const |  |  | 2019-11-25 | Kelvin Cook
ASF-01 | ASF-01 | PI13175 | Verified | 1C-ASF-0046-P41 not installed. STG operating deck north side. | A | P | James Beech | McD | 2019-11-20 | James Beech | Const |  |  | 2019-11-25 | Kelvin Cook
ASF-01 | ASF-01 | PI13176 | Verified | 1C-ASF-0025-P41 not installed. STG operating deck north side. | A | P | James Beech | McD | 2019-11-20 | James Beech | Const |  |  | 2019-11-25 | Kelvin Cook
ASF-01 | ASF-01 | PI13177 | Verified | 1C-ASF-0045-P40 - support not installed. STG operating deck north side. | A | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-08 | James Beech | 2019-12-19 | Kelvin Cook
ASF-01 | ASF-01 | PI13178 | Verified | Tag all valves. | C | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2020-02-27 | James Beech | 2020-02-27 | Kelvin Cook
ASF-01 | ASF-01 | PI13201 | Verified | 1C-ASF-PV-0035 missing accummulator tank and tubing | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-11-25 | Gonzalo Pena | 2019-12-01 | Albert Burge
ASF-01 | ASF-01 | PI13202 | Verified | 1 1/2" condulet cover missing on AOV-0085 | B | E | Dustin Futrell | McD | 2019-11-20 | Dustin Futrell | Const |  |  | 2019-12-01 | Fred Michael
ASF-01 | ASF-01 | PI13203 | Verified | Tubing not connected need to weld the fitting to the instrument air line valve (PV-0035) | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-12-19 | Albert Burge | 2019-12-19 | Albert Burge
ASF-01 | ASF-01 | PI13204 | Verified | PV-0035 air pressure indicator is bent | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const |  |  | 2019-11-24 | Fred Michael
ASF-01 | ASF-01 | PI13205 | Verified | 1C-ASF-TV-0054 reinstate wiring after hydro | A | E | Mike Tabbert | McD | 2019-11-20 | Mike Tabbert | Const | 2019-11-23 | Dustin Futrell | 2019-12-10 | Mike Tabbert
ASF-01 | ASF-01 | PI13206 | Verified | 1C-ASF-AOV-0047 screw missing on the condulet cover | B | E | Dustin Futrell | McD | 2019-11-20 | Dustin Futrell | Const | 2019-11-23 | Dustin Futrell | 2019-12-01 | Fred Michael
ASF-01 | ASF-01 | PI13207 | Verified | 1C-ASF-AOV-0047 fittings loose at the condulet cover | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-11-23 | Dustin Futrell | 2019-12-01 | Fred Michael
ASF-01 | ASF-01 | PI13208 | Verified | 1C-ASF-TV-0053 Replace the broken positioner | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-12-06 | James Tanner | 2019-12-06 | James Tanner
ASF-01 | ASF-01 | PI13209 | Verified | 1C-ASF-FY-0050 wrong tag on valve. Replace LPS tag valve with ASF tag | C | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2020-01-27 | Bobby Williams | 2020-01-28 | Mike Tabbert
ASF-01 | ASF-01 | PI13210 | Verified | 1C-ASF-LEH-0075 and LEHH-0075 not installed | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-11-25 | Gonzalo Pena | 2019-12-01 | Albert Burge
ASF-01 | ASF-01 | PI13211 | Verified | LEH-0075 and LEHH-0075 need conduit and raceway | A | E | Chris Colvin | McD | 2019-11-20 | Chris Colvin | Const | 2019-11-23 | Dustin Futrell | 2019-12-05 | Mike Tabbert
ASF-01 | ASF-01 | PI13212 | Verified | Grouting on all conduit supports and raceways | C | C | Dustin Futrell | McD | 2019-11-20 | Dustin Futrell | Const |  |  | 2019-12-01 | Fred Michael
ASF-01 | ASF-01 | PI13213 | Verified | 1C-HTS-CAB-0206 flex fittings at terminal box is loose, on the stand | A | E | Dustin Futrell | McD | 2019-11-20 | Dustin Futrell | Const | 2019-11-23 | Dustin Futrell | 2019-12-01 | Fred Michael
ASF-01 | ASF-01 | PI13214 | Verified | 1C-HTS-CAB-0206 stand replace too short anchor bolt | B | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const |  |  | 2019-12-01 | Fred Michael
ASF-01 | ASF-01 | PI13215 | Verified | PIT-0018A and B to tighten the set screw | A | E | Dustin Futrell | McD | 2019-11-20 | Dustin Futrell | Const |  |  | 2019-11-24 | Fred Michael
ASF-01 | ASF-01 | PI13216 | Verified | PIT-0018A and B need tags | C | I | Dustin Futrell | McD | 2019-11-20 | Dustin Futrell | Const |  |  | 2019-12-01 | Fred Michael
ASF-01 | ASF-01 | PI13217 | Verified | PIT-0018A and B need to finish the heat shrink | A | E | Chris Colvin | McD | 2019-11-20 | Chris Colvin | Const | 2019-11-23 | Dustin Futrell | 2019-12-12 | Fred Michael
ASF-01 | ASF-01 | PI13218 | Verified | 1C-ASF-FY-0085 need tubing | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-11-25 | Gonzalo Pena | 2019-12-01 | Albert Burge
ASF-01 | ASF-01 | PI13833 | Verified | Tighten locknut and remove gags from spring can on support HGR-0046 on Isometric ASF-P41-0062-01 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const |  |  | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13834 | Verified | Bent stem on warm up valve : Piecemark # ASF-P40-0060-01-203-1 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13835 | Verified | Missing pipe support on Isometric ASF-PD-P40-0010-01 HGR-0030 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-08 | James Beech | 2019-12-16 | Ethan Byrd
ASF-01 | ASF-01 | PI13836 | Verified | Missing pipe support on Isometric ASF-PD-P40-0020-01 HGR-0028 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-08 | James Beech | 2019-12-16 | Ethan Byrd
ASF-01 | ASF-01 | PI13837 | Verified | Add 1'' grout on support HGR-0020 on Isometric P40-0060-01 | C | C | Alan Huntsman | McD | 2019-12-02 | Alan Huntsman | Const | 2020-02-03 | Michael Law | 2020-02-03 | Michael Law
ASF-01 | ASF-01 | PI13838 | Verified | Adjust strut so that pipe shoe is centered on base plate per ISO HGR-0021 on Isometric P40-0060-01 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-16 | Ethan Byrd
ASF-01 | ASF-01 | PI13839 | Verified | Tighten bolts on welded beam clips and remove gags from spring can HGR-0010 on Isometric P40-065-03 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13840 | Verified | Tighten locknut on adjustable strut and adjust per ISO on HGR-0014 on Isometric P40-0080-01 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13841 | Verified | Remove gag from spring can and tighten bolts HGR-0015 on Isometric P40-0080-01 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13842 | Verified | Missing lock nut on bottom of turnbuckle, bent all thread HGR-0001 on Isometric P40-0060-03 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13843 | Verified | Install pipe support HGR-0002 and remove cable lashing from piping on Isometric P40-0060-04 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-09 | Michael Law | 2019-12-16 | Ethan Byrd
ASF-01 | ASF-01 | PI13844 | Verified | Tighten all bolts and nuts, also add lock nut on the bottom of turnbuckle on HGR-003 on Isometric P40-0060-04 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-16 | Ethan Byrd
ASF-01 | ASF-01 | PI13845 | Verified | Adjust and tighten lock nut on adjustable strut per ISO on HGR-0004 on Isometric P40-0060-04 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13846 | Verified | Bent all thread, add lock nut to bottom of turnbuckle per ISO on HGR-0005 on Isometric P40-0060-04 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13847 | Verified | Missing lock nut on bottom of turnbuckle on HGR-0005 on Isometric P40-0060-04 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13848 | Verified | Missing lock nut on bottom of turnbuckle on HGR-0006 on Isometric P40-0060-04 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13849 | Verified | Remove gags from spring can and tighten bolts and nuts on HGR-0007 on Isometric P40-0060-06 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13850 | Verified | Remove zip ties and wire from pipe located near HGR-0007 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13851 | Verified | Tighten bolts on HGR-0019 per Isometric P40-0065-01 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13852 | Verified | Tighten bolts and remove gags on HGR-0035 on Isometric P41-0062-01 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13853 | Verified | Tighten lock nuts on adjustable strut on HGR-0047 on Isometric P41-0062-01 | A | P | James Beech | McD | 2019-12-02 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-05 | Ethan Byrd
ASF-01 | ASF-01 | PI13971 | Verified | 1C-IAS-PD-P41-0140-02: Complete tubing connection to 1C-ASF-PV-0035. | A | I | Gonzalo Pena | McD | 2019-12-05 | Gonzalo Pena | Const | 2019-12-06 | James Tanner | 2019-12-14 | Kelvin Cook
ASF-01 | ASF-01 | PI13972 | Verified | 1C-ASF-PD-P41-0210-02: Install 3/4" SW x 1/2" swage fitting to 1C-ASF-V-0141, install tubing and connecto to 1C-CRS-AOV-0090. | A | I | Gonzalo Pena | McD | 2019-12-05 | Gonzalo Pena | Const | 2019-12-06 | James Tanner | 2019-12-15 | Kelvin Cook
ASF-01 | ASF-01 | PI14360 | Verified | LEH-0075 and LEHH-0075 - conduit needs adjustment away from valve handwheel. | B | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-14 | Kelvin Cook
ASF-01 | ASF-01 | PI14361 | Verified | LEH-0075 and LEH-0075 - counduit needs adjustment away from vavle handwheel | B | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-20 | Fred Michael
ASF-01 | ASF-01 | PI14735 | Verified | 1C-ASF-PD-P40-0045-01: 1C-ASF-HGR-0032 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-13 | Bobby Williams | 2019-12-15 | Kelvin Cook
ASF-01 | ASF-01 | PI14736 | Verified | 1C-ASF-PD-P40-0025-01: 1C-ASF-HGR-0034 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-13 | Bobby Williams | 2019-12-15 | Kelvin Cook
ASF-01 | ASF-01 | PI16870 | Verified | Clean rust off magnetic switches at 1C-ASF-AOV-0085; Condenser Hotwell Sparging Steam Control Valve | C | I | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-27 | James Beech | 2020-06-08 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16871 | Verified | Repair bent regulator drain at 1C-ASF-AOV-0085; Condenser Hotwell Sparging Steam Control Valve | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-04-06 | James Beech | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16872 | Verified | Tag missing at 1C-ASF-MOV-8700; Steam Turbine Pre Warming Steam Motor Operated Valve | C | P | Kelvin Cook | McD | 2020-02-18 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16873 | Verified | Cables not terminated at 1C-ASF-TI-0074A; Cold Reheat Desuperheater Spray Temperature Indicator, Line No. 6-1C-ASF-0020, STG operating deck | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-09 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16874 | Verified | Cables not terminated at 1C-ASF-TI-0074B; Cold Reheat Desuperheater Spray Temperature Indicator, Line No. 6-1C-ASF-0020, STG operating deck | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-09 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16875 | Verified | Remove tie wrap from valve handle at 1C-ASF-SRV-0019; Aux Steam Safety Relief Valve, Line No. 6-1C-ASF-0020, STG operating deck | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16876 | Verified | 1C-ASF-SRV-0019; Aux Steam Safety Relief Valve needs tag, Line No. 6-1C-ASF-0020, STG operating deck | C | P | Kelvin Cook | McD | 2020-02-18 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16877 | Verified | 1C-ASF-V-0020; Equalization Valve missing tag, Line No. 6-1C-ASF-0020, STG operating deck | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-08 | James Beech | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16878 | Verified | 1C-ASF-V-0022; Equalization Valve missing tag, Line No. 6-1C-ASF-0020, STG operating deck | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-08 | James Beech | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16879 | Verified | Flex conduit ground cable disconnected to actuator at 1C-ASF-AOV-0047; Condensate Spray to Desuperheater Control Valve, Line No. 1-1C-ASF-0050, STG operating deck | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-06 | Chris Colvin | 2020-03-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16880 | Verified | Pressure Indicator is broken at 1C-ASF-AOV-0047; Condensate Spray to Desuperheater Control Valve, Line No. 1-1C-ASF-0050, STG operating deck | B | I | Gonzalo Pena | McD | 2020-02-18 | Gonzalo Pena | Comm |  |  | 2020-02-28 | John Watts
ASF-01 | ASF-01 | PI16881 | Verified | No ground cable on flex conduit from actuator to solenoid at 1C-ASF-AOV-0047; Condensate Spray to Desuperheater Control Valve, Line No. 1-1C-ASF-0050, STG operating deck | D | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-04-06 | Michael Law | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16882 | Verified | Regulator /solenoid mounting bracket is bent at 1C-ASF-AOV-0047; Condensate Spray to Desuperheater Control Valve, Line No. 1-1C-ASF-0050, STG operating deck | C | I | Gonzalo Pena | McD | 2020-02-18 | Gonzalo Pena | Comm | 2020-03-04 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16883 | Verified | Thread drain line and install cap at 1C-ASF-V-0078; Condensate Spray to Desuperheater Drain Valve; Line No. 1-1C-ASF-0050, STG operating deck | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-02-27 | James Beech | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16884 | Verified | Flex conduit from actuator to solenoid needs ground cable at 1C-ASF-AOV-0050; Condensate Spray to Desuperheater Control Valve, Line No. 1-1C-ASF-0051, STG operating deck | D | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-04-06 | Michael Law | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16885 | Verified | No tag at 1C-ASF-V-0048; Strainer 1C-ASF-STN-0045 Drain Valve, Line No. 1-1C-ASF-0051, STG operating deck | C | P | Kelvin Cook | McD | 2020-02-18 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16886 | Verified | No tag at 1C-ASF-V-0057; Condensate Spray to Desuperheater Isolation Valve, Line No. 1-1C-ASF-0051, STG operating deck | C | P | Kelvin Cook | McD | 2020-02-18 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16887 | Verified | No tag at 1C-ASF-CHK-0056; Condensate Spray to Desuperheater Check Valve, Line No. 1-1C-ASF-0051, STG operating deck | C | P | Kelvin Cook | McD | 2020-02-18 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16888 | Verified | No tag at 1C-ASF-V-0058; Condensate Spray to Desuperheater Vent Valve, Line No. 1-1C-ASF-0051, STG operating deck | C | P | Kelvin Cook | McD | 2020-02-18 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16889 | Verified | No tag at 1C-ASF-V-0059; Condensate Spray to Desuperheater Drain Valve, Line No. 1-1C-ASF-0051, STG operating deck | C | P | Kelvin Cook | McD | 2020-02-18 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI16890 | Verified | Complete insulation as required throughout system | C | Q | Sheri Fritz | PCI | 2020-02-18 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
ASF-01 | ASF-01 | PI17495 | Verified | Missing tag, 1C-ASF-V-0044, line 1C-ASF-P41-0051-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17496 | Verified | Missing tag, 1C-ASF-V-0057, line 1C-ASF-P41-0051-02 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17497 | Verified | 1C-ASF-CHK-0056; line 1C-ASF-P41-0051-02 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17498 | Verified | Missing tag, 1C-ASF-V-0058, line 1C-ASF-P41-0051-04 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17499 | Verified | Missing tag, 1C-ASF-V-0059, line 1C-ASF-P41-0051-05 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17500 | Verified | Missing/loose hardware, 1C-AOV-0050 conduit cover | C | E | Chris Colvin | McD | 2020-03-03 | Chris Colvin | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17501 | Verified | Missing tag, 1C-ASF-V-0041, line 1C-ASF-P41-0050-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17502 | Verified | Missing tag, 1C-ASF-V-0043, line 1C-ASF-P41-0050-03 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17503 | Verified | Loose cap; 1C-ASF-P41-0050-03 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-09 | Chris Colvin | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17504 | Verified | Broken/damaged, bent regulator and solenoid mounting plate, 1C-ASF-AOV-0047, line 1C-ASF-P41-0050-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-06 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17505 | Verified | Broken/damaged pressure gauge, 1C-ASF-AOV-0047, line 1C-ASF-P41-0050-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-06 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17506 | Verified | Broken/damaged, bent air supply tubing, 1C-ASF-AOV-0047, line 1C-ASF-P41-0050-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-06 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17507 | Verified | Installation not complete, control flex conduit ground not connected, 1C-AOV-0047, line 1C-ASF-P41-0050-01 | D | E | Michael Law | McD | 2020-03-03 | Michael Law | Comm | 2020-04-28 | Michael Law | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17508 | Verified | Missing hardware, conduit cover screw missing, 1C-ASF-AOV-0047, line 1C-ASF-P41-0050-01 | C | E | Chris Colvin | McD | 2020-03-03 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17509 | Verified | Broken/damaged, bent actuator limit adjustment bolt, 1C-ASF-TV-0054, line 1C-ASF-P41-0050-02 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-07 | Albert Burge | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17510 | Verified | Missing tag, 1C-ASF-V-0048, line 1C-ASF-P41-0050-02 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17511 | Verified | Missing tag, 1C-ASF-CHK-0049, line 1C-ASF-P41-0050-02 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17512 | Verified | Missing tag, 1C-ASF-V-0073, line 1C-ASF-P41-0050-04 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17513 | Verified | Missing tag, 1C-ASF-V-0078, line 1C-ASF-P41-0050-05 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17514 | Verified | Missing tag, 1C-ASF-V-0079, line 1C-ASF-P41-0050-08 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-27 | James Beech | 2020-06-08 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17515 | Verified | Missing tag, 1C-ASF-V-0011, line 1C-ASF-P40-0010-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17516 | Verified | Missing tag, 1C-ASF-V-0021, line 1C-ASF-P40-0010-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17517 | Verified | Missing hardware, valve handwheel roll pin, 1C-ASF-V-0010. line 1C-ASF-P40-0010-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-31 | James Beech | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17518 | Verified | See hanger drawing 1C-ASF-HGR-0030; incorrect/needs redline, item notation steel plate 1/2" x 0'-6" x 0'-6" points to W section, item notation steel W4x13 x 0'-6" points to steel plate | D | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-10 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17519 | Verified | Hanger not in per design, W section turned 90 deg from design drawing, 1C-ASF-HGR-0030, line 1C-ASF-P40-0010-01 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-10 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17520 | Verified | Material concern, plastic vent plug, may not conform to 30 yr, design life, 1C-ASF-PV-0015 controller, line 1C-ASF-P40-0010-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-20 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17521 | Verified | Loose hardware, controller cover screw loose, 1C-ASF-PV-0015, line 1C-ASF-P40-0010-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17522 | Verified | Not per design type, tubing support instrument air booster /regulator to accumulator, 1C-ASF-PV-0015, line 1C-ASF-P40-0010-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-07 | Albert Burge | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17523 | Verified | Missing/inaccessable tag, 1C-ASF-V-0017, line 1C-ASF-P40-0010-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17524 | Verified | Missing tag, 1C-ASF-V-0020, line 1C-ASF-P40-0010-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Keith Pollock
ASF-01 | ASF-01 | PI17525 | Verified | Missing tag, 1C-ASF-V-0022, line 1C-ASF-P40-0010-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-06 | Keith Pollock
ASF-01 | ASF-01 | PI17526 | Verified | Missing hardware, valve handwheel roll pin, 1C-ASF-V-0017, line 1C-ASF-P0010-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-31 | James Beech | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17527 | Verified | Hanger not per design alignment, GUHD-A-2 clips not on centerline, 1C-ASF-HGR-0029, line 1C-ASF-P40-0020-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-26 | James Beech | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17528 | Verified | Hanger installation not complete, hot adjustment and tack weld, HGR-0033, 1C-ASF-P40-0025-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-27 | James Beech | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17529 | Verified | Hanger not per design location, HGR-0906 not aligned to centerline SRV-0019 outlet vent pipe 1C-ASF-P40-0025-01 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-10 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17530 | Verified | Hanger not per design location, installed approximately one ft. west of design location, 1C-ASF-HGR-0028, line 1C-ASF-P40-0020-01 | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm | 2020-08-06 | Tim Green | 2020-08-14 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17531 | Verified | Missing tag, 1C-ASF-V-0018A, line 1C-ASF-P41-0060-05 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17532 | Verified | Missing tag, 1C-ASF-V-0018B, line 1C-ASF-P41-0060-06 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17533 | Verified | Loose hardware, handwheel roll pin, 1C-ASF-V-00030, line 1C-ASF-P40-0031-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-02 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17534 | Verified | Missing tag, 1C-ASF-V-0032, line 1C-ASF-P40-0031-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17535 | Verified | Missing tag, 1C-ASF-V-0023, line 1C-ASF-P40-0031-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-13 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17536 | Verified | Loose hardware, controller conduit cover screw, 1C-ASF-PV-0035, line 1C-ASF-P40-0031-01 | C | E | Chris Colvin | McD | 2020-03-03 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17537 | Verified | Support not per design type standard, control booster tubing, 1C-ASF-PV-0035, line 1C-ASF-P40-0031-01 | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm | 2020-06-01 | Tim Green | 2020-06-08 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17538 | Verified | Missing tag, 1C-ASF-V-0025, line 1C-ASF-P41-0040-02 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17539 | Verified | Missing tag, 1C-ASF-V-0014, line 1C-ASF-P40-0040-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17540 | Verified | Missing tag, 1C-ASF-V-0024, line 1C-ASF-P40-0040-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17541 | Verified | Missing hardware, hex nuts, 1C-ASF-HGR-0028, line 1C-ASF-P40-0020-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-27 | James Beech | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17542 | Verified | Loose hardware, nut on anchor bolt, 1C-ASF-HGR-901, line 1C-ASF-P40-0060-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-27 | James Beech | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17543 | Verified | Missing tag, 1C-ASF-V-0081, line 1C-ASF-P40-0080 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17544 | Verified | P&ID and ISO drawings incorrect/need redline, valve includes bonnet pressure equalizing valve not numbered, 1C-ASF-V-0081, line 1C-ASF-P40-0080-01 | C | P | Charles Worthington | McD | 2020-03-03 | Charles Worthington | Comm | 2020-04-28 | Charles Worthington | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17545 | Verified | Missing tag, bonnet pressure equalizing valve on 1C-ASF-V-0081, line 1C-ASF-P40-0080-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-27 | James Beech | 2020-06-08 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17546 | Verified | Missing hardware, hex nuts, 1C-ASF-HGR-0018, line 1C-ASF-P40-0065-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-27 | James Beech | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17547 | Verified | Drawing incorrect/need redline, drawing indicates two (2) hex nuts, one (1) as Item 1 in drawing 1C-ASF-HGR-0904, and one (1) as a component in drawing 1C-ASF-HGR-0033. Drawing 1C-ASF-HRG-0033 does not indicate two nuts stacked as part of assembly. Redline requested to clarify intent of design engineering. Line 1C-ASF-P40-0020-01 | D | P | Michael Law | McD | 2020-03-03 | Michael Law | Comm | 2020-06-08 | Nelson Eichelberger | 2020-06-08 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17548 | Verified | Hanger not per design orientation, post turned 90 degrees, 1C-ASF-HGR-0022, line 1C-ASF-P40-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-27 | James Beech | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17549 | Verified | Hanger not per design orientation, hanger turned 180 degrees from as drawn, 1C-ASF-HGR-0902, line 1C-ASF-P40-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-31 | James Beech | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17550 | Verified | Hanger not per design location, HGR-0023, HGR-0902, HGR-0031 and HGR-0905 not set to same centerline per drawings, 1C-ASF-HGR-XXXX, line 1C-ASF-P40-0040-01 and line 1C-ASF-P40-0045-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-02 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17551 | Verified | Hanger not per design location, hanger centerline offset, 1C-ASF-HGR-0031, line 1C-ASF-P40-0045-01 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-10 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17552 | Verified | Hanger not per design orientation, hanger turned 90 degrees, 1C-ASF-HGR-0025, line 1C-ASF-P40-0060-02 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-10 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17553 | Verified | Installation not complete, missing vent holes, 1C-ASF-HGR-0903, line 1C-ASF-P40-0060-02 | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm | 2020-05-29 | James Beech | 2020-07-10 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17554 | Verified | Not per design location, hanger item 1 and welded beam attachment not installed at drawing offset, hanger item 3 and welded beam attachment not installed at drawing offset, 1C-ASF-HGR-0059, line 1C-ASF-P41-0051-10 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-31 | James Beech | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17555 | Verified | Installation not complete, hanger adjustment not per drawing, 1C-ASF-HGR-0059, line 1C-ASF-P41-0051-10 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-02 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17556 | Verified | Loose hardware, hanger clamp bolts not tight, 1C-ASF-HGR-0059, line 1C-ASF-P41-0051-10 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-31 | James Beech | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17557 | Verified | Not per design orientation, installed on east side of pipe, 1C-ASF-HGR 0053, line 1C-ASF-P41-0050-06 | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm | 2020-06-02 | Tim Green | 2020-06-03 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17558 | Verified | Installation not complete, shear lugs not installed both sides of hanger item 4, 1C-ASF-HGR 0053, line 1C-ASF-P41-0050-06 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-27 | James Beech | 2020-06-08 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17559 | Verified | Hanger not per design orientation, item 1 mounted on east side of pipe, 1C-ASF-HGR-0052, line 1C-ASF-P41-0050-06 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-10 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17560 | Verified | Not per design, vent hole on side opposite as drawn, 1C-ASF-HGR-0051, line 1C-ASF-P41-0050-07 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-02 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17561 | Verified | Hanger not installed, 1C-ASF-HGR-0066, line 1C-ASF-P41-0051-07 | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm | 2020-08-06 | Tim Green | 2020-08-14 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17562 | Verified | Missing tag, 1C-ASF-V-0060, line 1C-ASF-P41-0051-08 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17563 | Verified | Hanger not per design orientation, hex nut installed above turnbuckle, 1C-ASF-HGR-0005, line 1C-ASF-P40-0060-04 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-09 | Chris Colvin | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17564 | Verified | Drawing incorrect/need redline, bill of materials item list does not match the components identified in the drawing, 1C-ASF-HGR-0007, line 1C-ASF-P40-0060-04 | D | P | Michael Law | McD | 2020-03-03 | Michael Law | Comm | 2020-07-16 | Eric Policarpio | 2020-07-16 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17565 | Verified | Pipe not per design location, 1C-ASF-P40-0080-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-02 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17566 | Verified | Hanger installation not complete, hanger pipe stress review and design revision, adjustment to length of item 4 for sufficient overlap for growth, potential reinforcement of item 4, adjustment to items 2 and 3 for revised position of pipe, 1C-ASF-HGR-0014, line 1C-ASF-P40-0080-01 | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm |  |  | 2020-06-03 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17567 | Verified | Hanger not per design location, hanger location offset relative to pipe, 1C-ASF-HGR-0015; line 1C-ASF-P40-0080-01 | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm | 2020-06-02 | Tim Green | 2020-06-03 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17568 | Verified | Hanger not installed per design type, location, and fit, 1C-ASF-HGR-0016, line 1C-ASF-P40-0080- | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-02 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17569 | Verified | Hanger not installed to design location, 1C-ASF-HGR-0017, line 1C-ASF-0080-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-02 | Tim Green | 2020-05-26 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17570 | Verified | Hanger not per design type, GULA-C-6 guides not installed, 1C-ASF-HGR-0013, line 1C-ASF-P40-0080-03 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-02 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17571 | Verified | Hanger installation not complete, not adjusted level, 1C-ASF-HGR-0019, line 1A-ASF-P40-0065-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-02 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17774 | Verified | DSC00003; ASF Line P41-0051-01, V-0044, missing tag | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17775 | Verified | DSC00010; ASF Line P41-0051-02, V-0057, missing tag | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17776 | Verified | DSC00012; ASF Line P41-0051-02, CHK-0056, missing tag | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17777 | Verified | DSC00014; ASF Line P41-0051-04, V-0058, missing tag | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17778 | Verified | DSC00016; ASF Line P41-0051-05, V-0059, drain line valve missing tag | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17780 | Verified | DSC00020; ASF Line P41-0051-01, AOV-0050 control conduit valve cover screws loose. | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17781 | Verified | DSC00020; ASF Line P41-0051-01, AOV-0050 control conduit supports bolted to grating. Not per instalation specification and drawings. | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17782 | Verified | DSC00028; ASF Line P41-0050-01, V-0041, missing tag | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17783 | Verified | DSC00028; ASF Line P41-0050-01, V-0041, pipe cap on valve installed as cap on drain nipple from V-0043, ASF Line P41-0050-03. Cap installed loose; cap not shown on isometric. | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17784 | Verified | DSC00030; ASF Line P41-0050-3, V-0043, missing tag | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17785 | Verified | DSC00032; ASF Line P41-0050-3, V-0043, cap installed loose on drain side nipple. | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-20 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17786 | Verified | DSC00034; ASF Line P41-0050-01, AOV -0047, actuator air supply regulator gauge damaged, tubing bent out of plane, bracket to attach controller and regulator is bent | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17787 | Verified | DSC00035; ASF Line P41-0050-01, AOV -0047, actuator air supply regulator gauge damaged. | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17788 | Verified | DSC00037; ASF Line P41-0050-01, AOV -0047, actuator air supply regulator gauge damaged. | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17789 | Verified | DSC00039; ASF Line P41-0050-01, AOV -0047, actuator air supply regulator gauge tubing and bracket to attach controller and regulator is bent /damaged | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-20 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17790 | Verified | DSC00041; ASF Line P41-0050-01, AOV -0047, actuator control conduit flex ground lead is disconnected | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17791 | Verified | DSC00043; ASF Line P41-0050-01, AOV -0047, actuator control conduit Tee cover plate screws missing | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17792 | Verified | DSC00045; ASF Line P41-0050-02, TV-0054, actuator stem stroke limit adjustment bolt bent | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17793 | Verified | DSC00047; ASF Line P41-0050-02, V-0048, missing tag | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17794 | Verified | DSC00049; ASF Line P41-0050-02, CHK-0049, missing tag | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17795 | Verified | DSC00051; ASF Line P41-0050-04, V-0073, missing tag | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17796 | Verified | DSC00053; ASF Line P41-0050-05, V-0078, missing tag | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17797 | Verified | DSC00057; ASF Line P41-0050-08, V-0079, missing tag | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17798 | Verified | DSC00058; Tubing tray supported off ASF Line P41-0050-07. Not per standard pipe installation or instrument installation specifications or drawings. | C | I | Tim Green | McD | 2020-03-12 | Tim Green | Const | 2020-06-01 | Tim Green | 2020-06-08 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17799 | Verified | DSC00060; CRS Line P40-0020 not insulated per piping specification | C | Q | Richard McSpadden | PCI | 2020-03-12 | Richard McSpadden | Const | 2020-08-14 | Eric Policarpio | 2020-08-14 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17800 | Verified | DSC00062; ASF Line P40-0010-01, V-0010, V-0011, V-0021, missing tags visible to personnel | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-20 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17801 | Verified | DSC00064; ASF Line P40-0010-01, V-0010, hand-wheel missing roll pin. | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-04-02 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17802 | Verified | DSC00066; ASF Line P40-0010-01, HGR-0030, alloy steel resistant pipe clamp, temperature 1000 deg. F, assembled with galvanized fasteners vs SS. | D | P | Gary Pickeral | McD | 2020-03-12 | Gary Pickeral | Const | 2020-05-26 | Gary Pickeral | 2020-07-10 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17803 | Verified | DSC00071; ASF Line P40-0010-01, PV-0015, controller covers screw loose | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17804 | Verified | DSC00072; ASF Line P40-0010-01, PV-0015, controller covers screw loose | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17805 | Verified | DCS00074; ASF Line P40-0010-01, PV-0015, instrument tubing missing adequate support. | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-20 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17806 | Verified | DSC00075; ASF Line P40-0010-01, PV-0015, instrument tubing missing adequate support. | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-20 | Tim Green | 2020-05-06 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17807 | Verified | DSC00077; ASF Line P40-0010-01, V-0017, V-0020, V-0022, missing tags visible to personnel | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17808 | Verified | DSC00079; ASF Line P40-0010-01, V-0017, hand-wheel missing roll pin | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-04-02 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17809 | Verified | DSC00081; ASF Line P40-0020-01, HGR 0029, below pipe Tee connecting SRV-0019 -- bare rusting piping needs painted | C | X | Johnny Campbell | McD | 2020-03-12 | Johnny Campbell | Const | 2020-04-23 | Johnny Campbell | 2020-04-24 | Mark Williamson
ASF-01 | ASF-01 | PI17810 | Verified | DSC00082; ASF Line P40-0020-01, HGR 0029, below pipe Tee connecting SRV-0019, GUHD-A-2 shoe guides not aligned with SRV. | C | P | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-05-26 | James Beech | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17811 | Verified | DSC00084; ASF Line P40-0020-01, HRG's 0904, 0033, & 0906, not aligned to SRV-0019 discharge pipe centerline | C | P | Gary Pickeral | McD | 2020-03-12 | Gary Pickeral | Const | 2020-05-21 | Gonzalo Pena | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17812 | Verified | DSC00087; ASF Line P40-0020-01, HGR 0028 not installed per drawing location | C | P | Gary Pickeral | McD | 2020-03-12 | Gary Pickeral | Const | 2020-05-21 | Gary Pickeral | 2020-07-10 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17813 | Verified | DSC00089; ASF Line P40-0060-06, HGR 0026 to be 4'-8 13/16" plant east if TW-0074A and 20' 0 3/16 west of FW centerline. Not able to verify -- inaccessible | D | P | Nelson Eichelberger | ENT | 2020-03-12 | Nelson Eichelberger | Const | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
ASF-01 | ASF-01 | PI17814 | Verified | DSC00091; ASF Line P41-0060-05, V-0018A, missing tag | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-05-28 | Nelson Eichelberger | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17815 | Verified | DSC00093; ASF Line P41-0060-06, V-0018B, missing tag | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-05-28 | Nelson Eichelberger | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17816 | Verified | DSC00095; ASF Line P40-0031-01, V-0030, hand-wheel missing roll pin | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17817 | Verified | DSC00097; ASF Line P40-0031-01, V-0032, missing tag | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17818 | Verified | DSC00099; ASF Line P40-0031-01, V-0023, missing tag | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17819 | Verified | DSC00101; ASF Line P40-0031-01, V-0035, control conduit cover plate screws loose. | C | I | Tim Green | McD | 2020-03-12 | Tim Green | Const | 2020-06-01 | Tim Green | 2020-06-08 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17820 | Verified | DSC00102; ASF Line P40-0031-01, V-0035, control air supply booster tubing inadequately supported. | C | I | Tim Green | McD | 2020-03-12 | Tim Green | Const | 2020-06-01 | Tim Green | 2020-06-08 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17821 | Verified | DSC0104; ASF Line P40-0031-01, V-0035, control air supply booster tubing inadequately supported. | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-05-28 | Nelson Eichelberger | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17822 | Verified | DSC00105; ASF Line P40-0031-01, V-0025, (ref. LK-1C-ASF-ME-PID-0001, R2, 4-23-19), missing tag | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17823 | Verified | DSC00108; ASF Line P40-0031-01, V-0014, missing tag | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-28 | Nelson Eichelberger
ASF-01 | ASF-01 | PI17824 | Verified | DSC00111; ASF Line P40-0031-01, V-0024, missing tag | C | I | James Beech | McD | 2020-03-12 | James Beech | Const | 2020-03-13 | Tim Green | 2020-05-28 | Nelson Eichelberger
BYS-01 | BYS-01 | PI00017 | Verified | Install 2 hour fire stop in cable penetration from battery room to swg room. | C | E | Mike Tabbert | McD | 2019-01-16 | Mike Tabbert | Const | 2019-09-05 | Dustin Futrell | 2019-09-05 | Randy Carpenter
BYS-01 | BYS-01 | PI00021 | Verified | Replace broken and stuck absorbant bags in battery containment. | B | E | Shannon Savoy | McD | 2019-01-16 | Shannon Savoy | Const | 2019-02-14 | Shannon Savoy | 2019-02-14 | Mike Tabbert
BYS-01 | BYS-01 | PI00130 | Verified | Missing battery link between batteries 59 & 60. | A | E | Phil Work | McD | 2019-01-28 | Phil Work | Const | 2019-01-29 | Phil Work | 2019-01-30 | Curtis Platzek
BYS-01 | BYS-01 | PI00131 | Verified | Battery link to 10-ESG-SWB-0001 link terminations disconnected until Gutor arrives. | B | E | Logan Holland | McD | 2019-01-28 | Logan Holland | Const | 2019-04-01 | Shannon Savoy | 2019-04-01 | Mike Tabbert
BYS-01 | BYS-01 | PI00132 | Verified | Install battery room PERMANENT label on door (signage). | C | E | Mike Tabbert | McD | 2019-01-28 | Mike Tabbert | Const | 2019-09-28 | Mike Tabbert | 2019-09-30 | Randy Carpenter
BYS-01 | BYS-01 | PI00133 | Verified | Provide temporary eyewash station in the battery room. | A | E | Phil Work | McD | 2019-01-28 | Phil Work | Const | 2019-01-29 | Phil Work | 2019-01-31 | Randy Carpenter
BYS-01 | BYS-01 | PI00134 | Verified | Missing breather caps on cells 45 & 59 in the battery room. | B | E | Shannon Savoy | McD | 2019-01-28 | Shannon Savoy | Const | 2019-02-21 | Shannon Savoy | 2019-03-04 | Shannon Scott
BYS-01 | BYS-01 | PI04784 | Verified | Current cable lists not matching.. GSN = 36, at Consturction handover to Commissioning = 24, in Co-Console = 24. To determine the correct number of cables for this subsystem - as of 06-Sep GSN cable no is matching with Co-Console and Turnover book | C | E | Randy Carpenter | McD | 2019-09-05 | Randy Carpenter | Comm | 2019-09-06 | Eric Policarpio | 2019-09-24 | Eric Policarpio
BYS-01 | BYS-01 | PI04785 | Verified | Provide access to fan filter of battery room. need to cut cable tray | C | E | Dustin Futrell | McD | 2019-09-05 | Dustin Futrell | Comm | 2019-09-10 | Mike Tabbert | 2019-09-24 | Randy Carpenter
CCW-01 | CCW-01 | PI01034 | Verified | Ground conduit on 10-CCW-M-0100A. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01035 | Verified | Ground conduit on 10-CCW-M-0100B. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01036 | Verified | Seal tite exterior ground incomplete on 10-CCW-M-0100A. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01037 | Verified | Seal tite exterior ground incomplete on 10-CCW-M-0100B. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01038 | Verified | Complete grid ground to 10-CCW-M-0100A. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01039 | Verified | Complete grid ground to 10-CCW-M-0100B. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01040 | Verified | Install motor connection boots on 10-CCW-M-0100A (after comm.). | B | E | Luis Cantu | McD | 2019-05-14 | Luis Cantu | Const | 2019-06-07 | Shannon Savoy | 2019-06-21 | Logan Holland
CCW-01 | CCW-01 | PI01041 | Verified | Install motor connection boots on 10-CCW-M-0100B (after comm.). | B | E | Luis Cantu | McD | 2019-05-14 | Luis Cantu | Const | 2019-06-07 | Shannon Savoy | 2019-06-21 | Logan Holland
CCW-01 | CCW-01 | PI01042 | Verified | Conduit ground wires are too small on heater connection box on 10-CCW-M-0100A. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-16 | Mike Tabbert
CCW-01 | CCW-01 | PI01043 | Verified | Conduit ground wires are too small on heater connection box on 10-CCW-M-0100B. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-16 | Mike Tabbert
CCW-01 | CCW-01 | PI01044 | Verified | Cables not labeled in motor term. box on 10-CCW-M-0100A. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01045 | Verified | Cables not labeled in motor term. box on 10-CCW-M-0100B. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01046 | Verified | Replace plastic plugs on term. boxes with steel plugs on 10-CCW-M-0100A. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01047 | Verified | Replace plastic plugs on term. boxes with steel plugs on 10-CCW-M-0100B. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01048 | Verified | Equipment tag neededs on 10-CCW-M-0100A & B. | C | E | Joshua Sturgeon | McD | 2019-05-14 | Joshua Sturgeon | Const | 2019-09-06 | Mike Tabbert | 2019-09-11 | Shannon Scott
CCW-01 | CCW-01 | PI01049 | Verified | Complete ground in 10-CCW-M-0100A motor term. box. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01050 | Verified | Complete ground in 10-CCW-M-0100B motor term. box. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01051 | Verified | Install all missing condulet covers at 10-CCW-M-0100A & B (ground level & overhead). | B | E | Luis Cantu | McD | 2019-05-14 | Luis Cantu | Const | 2019-06-18 | Luis Cantu | 2019-06-26 | Logan Holland
CCW-01 | CCW-01 | PI01052 | Verified | Need firestop in compartment 10-CCW-M-0100A in the main PDC (after comm.) | C | E | Luis Cantu | McD | 2019-05-14 | Luis Cantu | Const | 2019-07-19 | Ken Mundy | 2019-07-26 | Logan Holland
CCW-01 | CCW-01 | PI01053 | Verified | Need firestop in compartment 10-CCW-M-0100B in the main PDC (after comm.) | C | E | Luis Cantu | McD | 2019-05-14 | Luis Cantu | Const | 2019-07-19 | Ken Mundy | 2019-07-26 | Logan Holland
CCW-01 | CCW-01 | PI01054 | Verified | Clean inside compartment 10-CCW-M-0100A in the main PDC. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01055 | Verified | Clean inside compartment 10-CCW-M-0100B in the main PDC. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01056 | Verified | Cables / wires missing tags in compartment 10-CCW-M-0100A in the main PDC. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01057 | Verified | Cables / wires missing tags in compartment 10-CCW-M-0100B in the main PDC. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01058 | Verified | Add heat shrink to stress cones in compartment 10-CCW-M-0100A in the main PDC. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01059 | Verified | Add heat shrink to stress cones in compartment 10-CCW-M-0100B in the main PDC. | A | E | Shannon Savoy | McD | 2019-05-14 | Shannon Savoy | Const | 2019-05-16 | Dan Dula | 2019-05-17 | Phil Carter
CCW-01 | CCW-01 | PI01112 | Verified | Install 10-CCW-T-0350. | A | M | Shane Crowe | McD | 2019-05-20 | Shane Crowe | Const | 2019-06-14 | Joshua Sturgeon | 2019-06-17 | Kelvin Cook
CCW-01 | CCW-01 | PI01418 | Verified | Cold galvanize all supports where needed. | C | C | James Beech | McD | 2019-06-06 | James Beech | Const |  |  | 2019-12-01 | Fred Michael
CCW-01 | CCW-01 | PI01419 | Verified | A ground cable & bolt protruding from concrete at CCW pump skid A are a trip hazard. Remove if not needed. | B | E | Luis Cantu | McD | 2019-06-06 | Luis Cantu | Const | 2019-06-21 | Luis Cantu | 2019-06-21 | Shannon Scott
CCW-01 | CCW-01 | PI01420 | Verified | Tighten flex for 10-CCW-PIT-0110 (near CCW pump A). | B | E | Luis Cantu | McD | 2019-06-06 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-06-17 | Shannon Scott
CCW-01 | CCW-01 | PI01421 | Verified | Need a unistrut strap at 10-CCW-PIT-0110. | B | E | Luis Cantu | McD | 2019-06-06 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-11 | Shannon Scott
CCW-01 | CCW-01 | PI01422 | Verified | Clean mud / concrete from all tagging at the CCW pumps. | B | C | Johnny Campbell | McD | 2019-06-06 | Johnny Campbell | Const | 2019-07-22 | Johnny Campbell | 2019-07-24 | Shannon Scott
CCW-01 | CCW-01 | PI01423 | Verified | Complete grounding at CCW heat exchangers. | A | E | Luis Cantu | McD | 2019-06-06 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-06-17 | Shannon Scott
CCW-01 | CCW-01 | PI01424 | Verified | Install 1C-CCW-FDR-0100. | A | P | Damon Turner | McD | 2019-06-06 | Damon Turner | Const | 2019-06-19 | Damon Turner | 2019-06-20 | Kelvin Cook
CCW-01 | CCW-01 | PI01476 | Verified | Tag all valves. | C | P | Bobby Williams | McD | 2019-06-19 | Bobby Williams | Const | 2020-02-19 | Bobby Williams | 2020-03-03 | Michael Law
CCW-01 | CCW-01 | PI01477 | Verified | Install caps at 1C-CCW-FP-0214A & B @ stator cooler skid. | B | I | Gonzalo Pena | McD | 2019-06-19 | Gonzalo Pena | Const | 2019-06-21 | Gonzalo Pena | 2019-06-25 | Shannon Scott
CCW-01 | CCW-01 | PI01478 | Verified | Grout all supports. | C | C | Johnny Campbell | McD | 2019-06-19 | Johnny Campbell | Const | 2019-07-25 | Jack Fields | 2019-08-08 | Kelvin Cook
CCW-01 | CCW-01 | PI01479 | Verified | Need conduit strap on wall at 1C-CCV-TV-0247 (near stator cooler skid). | C | E | Dustin Futrell | McD | 2019-06-19 | Dustin Futrell | Const | 2019-07-30 | Luis Cantu | 2019-08-08 | Shannon Scott
CCW-01 | CCW-01 | PI01480 | Verified | 1C-CCW-TCV-0247 needs vent cap. | B | I | Gonzalo Pena | McD | 2019-06-19 | Gonzalo Pena | Const | 2019-06-28 | Gonzalo Pena | 2019-07-19 | Kelvin Cook
CCW-01 | CCW-01 | PI01481 | Verified | Tighten nuts on pipe support at 1C-CCW-TCV-0247 (near stator cooler skid). | B | P | Damon Turner | McD | 2019-06-19 | Damon Turner | Const | 2019-07-26 | Terry Deaton | 2019-07-31 | Shannon Scott
CCW-01 | CCW-01 | PI01482 | Verified | 10-CCW-PV-0131 needs vent cap (STG mezz.). | B | I | Gonzalo Pena | McD | 2019-06-19 | Gonzalo Pena | Const | 2019-06-28 | Gonzalo Pena | 2019-07-19 | Kelvin Cook
CCW-01 | CCW-01 | PI01483 | Verified | 10-CCW-LIT-0170 at the CCW exp. tank needs ground wire. | A | E | Luis Cantu | McD | 2019-06-19 | Luis Cantu | Const | 2019-06-25 | Luis Cantu | 2019-06-25 | Shannon Scott
CCW-01 | CCW-01 | PI01484 | Verified | 10-CCW-V-0160 at the CCW exp. tank has wrong tag number. | C | P | Bobby Williams | McD | 2019-06-19 | Bobby Williams | Const | 2020-02-19 | Bobby Williams | 2020-03-03 | Michael Law
CCW-01 | CCW-01 | PI01485 | Verified | CCW Exp. Tank 10-CCW-T-0300 needs ground. | A | E | Luis Cantu | McD | 2019-06-19 | Luis Cantu | Const | 2019-06-25 | Luis Cantu | 2019-06-25 | Shannon Scott
CCW-01 | CCW-01 | PI01486 | Verified | Valve 1A-CCW-V-0753 at the 1A Sample Panel missing handwheel plate & nut. | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton | Const | 2019-06-21 | Terry Deaton | 2019-06-21 | Kelvin Cook
CCW-01 | CCW-01 | PI01487 | Verified | 10CCWK0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-06-19 | Luis Cantu | Const | 2019-06-20 | Luis Cantu | 2019-06-24 | Mike Tabbert
CCW-01 | CCW-01 | PI01488 | Verified | 10CCWK0002, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-06-19 | Luis Cantu | Const | 2019-06-20 | Luis Cantu | 2019-06-24 | Mike Tabbert
CCW-01 | CCW-01 | PI01489 | Verified | 10CCWX0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-06-19 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
CCW-01 | CCW-01 | PI01490 | Verified | 10CCWX0006, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-06-19 | Luis Cantu | Const | 2019-06-20 | Luis Cantu | 2019-06-24 | Mike Tabbert
CCW-01 | CCW-01 | PI01491 | Verified | 1ACCWX0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-06-19 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-27 | Mike Tabbert
CCW-01 | CCW-01 | PI01492 | Verified | 1ACCWX0002, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-06-19 | Luis Cantu | Const | 2019-07-26 | Dustin Futrell | 2019-07-27 | Mike Tabbert
CCW-01 | CCW-01 | PI01493 | Verified | 1BCCWX0001, Pull and Terminate Cable | B | E | Dustin Futrell | McD | 2019-06-19 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-25 | Mike Tabbert
CCW-01 | CCW-01 | PI01494 | Verified | 1BCCWX0002, Pull and Terminate Cable | B | E | Dustin Futrell | McD | 2019-06-19 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-25 | Mike Tabbert
CCW-01 | CCW-01 | PI01495 | Verified | 1CCCWX0003, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-06-19 | Luis Cantu | Const | 2019-06-20 | Luis Cantu | 2019-06-24 | Mike Tabbert
CCW-01 | CCW-01 | PI01496 | Verified | 10-CCW-LIT-0170, Not Installed. | A | E | Luis Cantu | McD | 2019-06-19 | Luis Cantu | Const | 2019-06-20 | Gonzalo Pena | 2019-06-24 | Mike Tabbert
CCW-01 | CCW-01 | PI01497 | Verified | Complete conduit for all Instruments and Valves. | A | E | Luis Cantu | McD | 2019-06-19 | Luis Cantu | Const | 2019-06-21 | Luis Cantu | 2019-06-24 | Mike Tabbert
CCW-01 | CCW-01 | PI01498 | Verified | 10-CCW-PIT-0110, complete tubing installation | A | E | Luis Cantu | McD | 2019-06-19 | Luis Cantu | Const | 2019-06-20 | Gonzalo Pena | 2019-06-24 | Mike Tabbert
CCW-01 | CCW-01 | PI01499 | Verified | 10-CCW-PIT-0140, complete tubing installation | A | E | Luis Cantu | McD | 2019-06-19 | Luis Cantu | Const | 2019-06-20 | Gonzalo Pena | 2019-06-24 | Mike Tabbert
CCW-01 | CCW-01 | PI01500 | Verified | On ISO 1A-CCW-PD-P40-0465-01 Instrument 1A-CCW-FE-0445A needs to be remove & turned in to eng. To be installed by commissioning after flush. | C | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01501 | Verified | On ISO 1A-CCW-PD-P40-0475-02 Instrument 1A-CCW-FE-0445B needs to be remove & turned in to eng. To be installed by commissioning at flush. | C | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01502 | Verified | On ISO 1A-CCW-PD-P40-0595-01 flange missing bolt & wrong gasket | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01503 | Verified | On ISO 1A-CCW-PD-P40-0595-01 flange on the side of PS-1A-CCW-P40-0595-01-152-3 needs gasket to be removed | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01504 | Verified | On ISO 1A-CCW-PD-P40-0602-01 connection to 1A-FWS-P-0100A/R2 incomplete bolt up | A | P | Damon Turner | McD | 2019-06-19 | Damon Turner |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01505 | Verified | On ISO 1A-CCW-PD-P40-0605-01 connection to 1A-FWS-P-0100B/R2 incomplete bolt up | A | P | Damon Turner | McD | 2019-06-19 | Damon Turner |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01506 | Verified | ISO 1A-CCW-PD-P40-0612-01 is not installed | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01507 | Verified | ISO 1A-CCW-PD-P40-0612-02 is not installed | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01508 | Verified | ISO 1A-CCW-PD-P40-0612-03 is not installed | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01509 | Verified | On ISO 1A-CCW-PD-P41-0595-03 pipe support 1A-CCW-PD-HGR-0326 is not installed | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01510 | Verified | ISO 1A-CCW-PD-P41-0800-01 is not intalled | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01511 | Verified | ISO 1A-CCW-PD-P41-0800-02 is not intalled | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01512 | Verified | ISO 1A-CCW-PD-P41-0803-01 is not intalled | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01513 | Verified | ISO 1A-CCW-PD-P41-0803-02 is not intalled | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01514 | Verified | ISO 1A-CCW-PD-P41-0805-01 is not intalled | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01515 | Verified | ISO 1A-CCW-PD-P41-0806-01 is not intalled | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01516 | Verified | ISO 1A-CCW-PD-P41-0806-02 is not intalled | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01517 | Verified | ISO 1A-CCW-PD-P41-0808-01 is not intalled | A | P | Terry Deaton | McD | 2019-06-19 | Terry Deaton |  |  |  | 2019-06-19 | Ed Gober
CCW-01 | CCW-01 | PI01518 | Verified | On ISO 1B-CCW-PD-P40-0465-01 1B-CCW-TW-0444A - install cap. | B | I | Gonzalo Pena | McD | 2019-06-19 | Gonzalo Pena | Const | 2019-06-21 | Kelvin Cook | 2019-06-21 | Kelvin Cook
CCW-01 | CCW-01 | PI01519 | Verified | ISO 10-CCW-PD-P40-0100-01 valve 10-CCW-V-0106A needs a chain operator | C | P | Alex Isaac | McD | 2019-06-19 | Alex Isaac | Const | 2019-10-01 | Alex Isaac | 2019-10-01 | Alex Isaac
CCW-01 | CCW-01 | PI01520 | Verified | ISO 10-CCW-PD-P40-0120-01 valve 10-CCW-V-0106B needs a chain operator | C | P | Alex Isaac | McD | 2019-06-19 | Alex Isaac | Const | 2019-10-01 | Alex Isaac | 2019-10-01 | Alex Isaac
CCW-01 | CCW-01 | PI01521 | Verified | Pump 10-CCW-P-0100A Needs Coupling installed ( After Pipe Stress) | A | M | Shane Crowe | McD | 2019-06-19 | Shane Crowe | Const | 2019-06-25 | Joshua Sturgeon | 2019-06-25 | Joshua Sturgeon
CCW-01 | CCW-01 | PI01522 | Verified | Pump 10-CCW-P-0100B Needs Coupling installed ( After Pipe Stress) | A | M | Shane Crowe | McD | 2019-06-19 | Shane Crowe | Const | 2019-06-25 | Joshua Sturgeon | 2019-06-25 | Joshua Sturgeon
CCW-01 | CCW-01 | PI01523 | Verified | Pump 10-CCW-P-0100A needs Motor and Pump Alignment Adjustment Bolts tightned ( After Pipe Stress) | A | M | Shane Crowe | McD | 2019-06-19 | Shane Crowe | Const | 2019-06-25 | Joshua Sturgeon | 2019-06-25 | Joshua Sturgeon
CCW-01 | CCW-01 | PI01524 | Verified | Pump 10-CCW-P-0100B needs Motor and Pump Alignment Adjustment Bolts tightned ( After Pipe Stress) | A | M | Shane Crowe | McD | 2019-06-19 | Shane Crowe | Const | 2019-06-25 | Joshua Sturgeon | 2019-06-25 | Joshua Sturgeon
CCW-01 | CCW-01 | PI01525 | Verified | Heat Exchanger 10-CCW-HEX-0200A Needs Protective metal removed | C | M | Danny Pase | McD | 2019-06-19 | Danny Pase | Const | 2019-07-17 | Michael Law | 2019-07-19 | Joshua Sturgeon
CCW-01 | CCW-01 | PI01526 | Verified | Heat Exchanger 10-CCW-HEX-0200B Needs Protective Metal Removed. | C | M | Danny Pase | McD | 2019-06-19 | Danny Pase | Const | 2019-07-17 | Michael Law | 2019-07-19 | Joshua Sturgeon
CCW-01 | CCW-01 | PI01527 | Verified | On ISO 10-CCW-PD-P40-0595-01 pipe support 1C-CCW-PD-HGR-0253 need second set of nuts at ubolt | A | P | Damon Turner | McD | 2019-06-19 | Damon Turner | Const | 2019-06-20 | Damon Turner | 2019-06-20 | Kelvin Cook
CCW-01 | CCW-01 | PI01528 | Verified | On ISO 10-CCW-PD-P40-0595-04 instrument 10-CCW-FE-0158 to be installed at flush completion | B | P | William Mitchell | McD | 2019-06-19 | William Mitchell | Const |  |  | 2019-11-23 | Stuart Herring
CCW-01 | CCW-01 | PI01529 | Verified | On 1C-CCW-PD-P40-0200-02 Blind flange is not installed | A | P | Damon Turner | McD | 2019-06-19 | Damon Turner | Const | 2019-06-20 | Kelvin Cook | 2019-06-20 | Kelvin Cook
CCW-01 | CCW-01 | PI01530 | Verified | On ISO 1C-CCW-PD-P40-0255-01 flange connecting to the FE is missing bolts | A | P | Damon Turner | McD | 2019-06-19 | Damon Turner | Const | 2019-06-20 | Damon Turner | 2019-06-20 | Kelvin Cook
CCW-01 | CCW-01 | PI01531 | Verified | On ISO 1C-CCW-PD-P40-0260-02 flange connecting to the FE loose bolts and no gasket intalled | A | P | Damon Turner | McD | 2019-06-19 | Damon Turner | Const | 2019-06-20 | Damon Turner | 2019-06-20 | Kelvin Cook
CCW-01 | CCW-01 | PI01532 | Verified | On ISO 1C-CCW-PD-P40-0267-01 blind is not installed | A | P | Damon Turner | McD | 2019-06-19 | Damon Turner | Const | 2019-06-20 | Kelvin Cook | 2019-06-20 | Kelvin Cook
CCW-01 | CCW-01 | PI01533 | Verified | On ISO 1C-CCW-PD-P40-0300-01 still needs correct bolting, too short. | A | P | Damon Turner | McD | 2019-06-19 | Damon Turner | Const | 2019-06-20 | Kelvin Cook | 2019-06-20 | Kelvin Cook
CCW-01 | CCW-01 | PI01534 | Verified | On ISO 1C-CCW-PD-P40-0341-03 flange has incomplete bolting at underground connection | A | P | Damon Turner | McD | 2019-06-19 | Damon Turner | Const | 2019-06-20 | Kelvin Cook | 2019-06-20 | Kelvin Cook
CCW-01 | CCW-01 | PI02504 | Verified | LK-10-CCW-PD-P40-0115-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02505 | Verified | LK-1A-CCW-PD-P41-0605-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Tom Noble
CCW-01 | CCW-01 | PI02506 | Verified | LK-1A-CCW-PD-P41-0800-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02507 | Verified | LK-1A-CCW-PD-P41-0803-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02508 | Verified | LK-1A-CCW-PD-P41-0803-03 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02509 | Verified | LK-1A-CCW-PD-P41-0805-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Tom Noble
CCW-01 | CCW-01 | PI02510 | Verified | LK-1A-CCW-PD-P41-0806-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02511 | Verified | LK-1A-CCW-PD-P41-0808-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02512 | Verified | LK-1A-CCW-PD-P41-0809-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02513 | Verified | LK-1A-CCW-PD-P41-0814-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02514 | Verified | LK-1A-CCW-PD-P41-0815-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02515 | Verified | LK-1A-CCW-PD-P41-0815-03 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02516 | Verified | LK-1A-CCW-PD-P41-0818-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02517 | Verified | LK-1A-CCW-PD-P41-0820-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02518 | Verified | LK-1A-CCW-PD-P41-0821-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02519 | Verified | LK-1A-CCW-PD-P41-0821-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02520 | Verified | LK-1B-CCW-PD-P40-0612-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Tom Noble
CCW-01 | CCW-01 | PI02521 | Verified | LK-1B-CCW-PD-P40-0625-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02522 | Verified | LK-1B-CCW-PD-P41-0389-04 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02523 | Verified | LK-1B-CCW-PD-P41-0595-03 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02524 | Verified | LK-1B-CCW-PD-P41-0900-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02525 | Verified | LK-1B-CCW-PD-P41-0903-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02526 | Verified | LK-1B-CCW-PD-P41-0903-03 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02527 | Verified | LK-1B-CCW-PD-P41-0903-05 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02528 | Verified | LK-1B-CCW-PD-P41-0908-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02529 | Verified | LK-1B-CCW-PD-P41-0909-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Tom Noble
CCW-01 | CCW-01 | PI02530 | Verified | LK-1B-CCW-PD-P41-0912-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Tom Noble
CCW-01 | CCW-01 | PI02531 | Verified | LK-1B-CCW-PD-P41-0912-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
CCW-01 | CCW-01 | PI02532 | Verified | LK-1B-CCW-PD-P41-0915-05 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Tom Noble
CCW-01 | CCW-01 | PI02533 | Verified | LK-1B-CCW-PD-P41-0918-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Tom Noble
CCW-01 | CCW-01 | PI02534 | Verified | LK-1B-CCW-PD-P41-0920-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Tom Noble
CCW-01 | CCW-01 | PI02535 | Verified | LK-1B-CCW-PD-P41-0920-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Tom Noble
CCW-01 | CCW-01 | PI02536 | Verified | LK-1C-CCW-PD-P41-0389-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Tom Noble
CCW-01 | CCW-01 | PI02537 | Verified | LK-1C-CCW-PD-P41-0389-03 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Tom Noble
CCW-01 | CCW-01 | PI02566 | Verified | ON ISO 1A-CCW-PD-P41-0803-03 install instrument 1A-CCW-FE-0843 after commissioning flush is completed. | B | P | Stuart Herring | McD | 2019-07-23 | Stuart Herring | Const |  |  | 2019-11-23 | Stuart Herring
CCW-01 | CCW-01 | PI02567 | Verified | On ISO 1A-CCW-PD-P41-0808-02 handle missing plastic rubber on valve 1A-CCW-V-0802. | B | P | James Beech | McD | 2019-07-23 | James Beech | Const |  |  | 2019-12-01 | Stuart Herring
CCW-01 | CCW-01 | PI02568 | Verified | On ISO 1A-CCW-PD-P41-0809-01 missing threaded cap on valve 1A-CCW-V-0832. | B | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-08-01 | Kelvin Cook
CCW-01 | CCW-01 | PI02569 | Verified | ON ISO 1A-CCW-PD-P41-0812-01 install instrument 1A-CCW-FE-0849 after commissioning flush is completed. | B | P | Stuart Herring | McD | 2019-07-23 | Stuart Herring | Const |  |  | 2019-11-23 | Stuart Herring
CCW-01 | CCW-01 | PI02570 | Verified | On ISO 1A-CCW-PD-P41-0812-01 missing threaded cap on valve 1A-CCW-V-0833. | B | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-08-01 | Kelvin Cook
CCW-01 | CCW-01 | PI02571 | Verified | On ISO 1A-CCW-PD-P41-0812-02 instrument 1A-CCW-FP-0849 is not installed. | B | I | Gonzalo Pena | McD | 2019-07-23 | Gonzalo Pena | Const | 2019-07-25 | Gonzalo Pena | 2019-08-02 | Kelvin Cook
CCW-01 | CCW-01 | PI02572 | Verified | On ISO 1A-CCW-PD-P41-0812-03 instrument 1A-CCW-FP-0849 is not installed. | B | I | Gonzalo Pena | McD | 2019-07-23 | Gonzalo Pena | Const | 2019-07-25 | Gonzalo Pena | 2019-08-02 | Kelvin Cook
CCW-01 | CCW-01 | PI02754 | Verified | On ISO on 1B-CCW-PD-P41-0425-02 pipe support 1B-CCW-PD-HGR-0101,0102 is not installed | B | P | Bobby Williams | McD | 2019-07-24 | Bobby Williams | Const | 2020-01-30 | Charlie English | 2020-01-31 | Kelvin Cook
CCW-01 | CCW-01 | PI02755 | Verified | On ISO on 1B-CCW-PD-P41-0430-01 pipe support 1B-CCW-PD-HGR-0099,0100 is not installed | B | P | Bobby Williams | McD | 2019-07-24 | Bobby Williams | Const | 2020-01-30 | Charlie English | 2020-01-31 | Kelvin Cook
CCW-01 | CCW-01 | PI02756 | Verified | On ISO on 1B-CCW-PD-P41-0435-02 pipe support 1B-CCW-PD-HGR-0105 is not installed | B | P | Bobby Williams | McD | 2019-07-24 | Bobby Williams | Const | 2020-01-30 | Charlie English | 2020-01-31 | Kelvin Cook
CCW-01 | CCW-01 | PI02757 | Verified | On ISO on 1B-CCW-PD-P41-0440-01 pipe support 1B-CCW-PD-HGR-103,104 is not installed | B | P | Bobby Williams | McD | 2019-07-24 | Bobby Williams | Const | 2020-01-30 | Charlie English | 2020-01-31 | Kelvin Cook
CCW-01 | CCW-01 | PI04466 | Verified | BSI the CCW supply pipe to the LO cooler not included in the CCW flush. Torque and bend lock washers | B | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-13 | Damon Turner | 2019-11-24 | Brian Ballard
CCW-01 | CCW-01 | PI07786 | Verified | Re-drill U-Bolt holes and install U-Bolts on CCW supply and return skid piping at Unit 1A Boiler Feed Pump A, small bore piping painted bright green, located north side of FW Pump skid. | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-12-31 | Bobby Williams | 2020-01-27 | Michael Law
CCW-01 | CCW-01 | PI13550 | Verified | Remove tape from CCW-M-0100B; CCW B Motor | C | M | Bobby Williams | McD | 2019-11-27 | Bobby Williams | Comm | 2020-01-15 | Bobby Williams | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13551 | Verified | Clean up 10-CCW-P-0100B; CCW Pump B skid and equipment | C | C | Alan Huntsman | McD | 2019-11-27 | Alan Huntsman | Comm | 2020-03-11 | Alan Huntsman | 2020-04-02 | John Watts
CCW-01 | CCW-01 | PI13552 | Verified | Complete concrete finishing work at foundation of 10-CCW-P-0100B; CCW Pump B | C | C | Alan Huntsman | McD | 2019-11-27 | Alan Huntsman | Comm | 2020-03-19 | Johnny Campbell | 2020-04-02 | John Watts
CCW-01 | CCW-01 | PI13553 | Verified | Tighten vertical pipe support base plate hold down anchors at 10-CCW-P-0100B, CCW Pump B discharge, Line No. 24-10-CCW-0120 | C | M | Bobby Williams | McD | 2019-11-27 | Bobby Williams | Comm | 2020-01-15 | Bobby Williams | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13554 | Verified | 10-CCW-V-0106B; CCW Pump B discharge isolation valve corroded, needs to be cleaned and painted | C | X | Jerry Smith | McD | 2019-11-27 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-04-02 | John Watts
CCW-01 | CCW-01 | PI13555 | Verified | 10-CCW-V-0106A; CCW Pump A discharge isolation valve corroded, needs to be cleaned and painted | C | X | Jerry Smith | McD | 2019-11-27 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-04-02 | John Watts
CCW-01 | CCW-01 | PI13556 | Verified | 10-CCW-V-0145A; CCW Pump A suction valve is corroded, needs to be painted | C | X | Jerry Smith | McD | 2019-11-27 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-04-02 | John Watts
CCW-01 | CCW-01 | PI13557 | Verified | Clean all 24" CCW piping above CCW Heat Exchangers A and B | C | C | Alan Huntsman | McD | 2019-11-27 | Alan Huntsman | Comm | 2020-03-11 | Alan Huntsman | 2020-04-02 | John Watts
CCW-01 | CCW-01 | PI13558 | Verified | Clean up and remove tape at 10-CCW-HEX-0200A & B | C | C | Alan Huntsman | McD | 2019-11-27 | Alan Huntsman | Comm | 2020-03-11 | Alan Huntsman | 2020-04-02 | John Watts
CCW-01 | CCW-01 | PI13559 | Verified | Clean up system piping at 1C STG EHC Oil Cooler A & B, SE side STG Bldg, ground floor | C | C | Alan Huntsman | McD | 2019-11-27 | Alan Huntsman | Comm | 2020-03-11 | Alan Huntsman | 2020-04-02 | John Watts
CCW-01 | CCW-01 | PI13560 | Verified | Clean inlet piping and valves at 1C STG Main Oil Cooler A & B, S side STG Bldg, ground floor | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-25 | James Beech | 2020-02-02 | Shannon Scott
CCW-01 | CCW-01 | PI13561 | Verified | Grout vertical pipe support at inlet to 1A Generator Hydrogen Gas Cooler 1, Line No. 4-1A-CCW-0405 | C | C | Johnny Campbell | McD | 2019-11-27 | Johnny Campbell | Comm | 2019-12-12 | Jack Fields | 2019-12-18 | Shannon Scott
CCW-01 | CCW-01 | PI13562 | Verified | Grout vertical pipe support at inlet to 1A Generator Hydrogen Gas Cooler 2, Line No. 4-1A-CCW-0415X | C | C | Johnny Campbell | McD | 2019-11-27 | Johnny Campbell | Comm | 2019-12-12 | Jack Fields | 2019-12-18 | Shannon Scott
CCW-01 | CCW-01 | PI13563 | Verified | Seal Temperature Element 1ACCW-TE-0624A conduit penetration at 1A Boiler Feed Pump A enclosure | C | E | Tim Gallegos | McD | 2019-11-27 | Tim Gallegos | Comm | 2020-06-05 | Tim Gallegos | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13564 | Verified | Power cable conduit penetrations need to be sealed at 1A-CCW-TI-0642B; 1A Boiler Feed Pump B return line Temperature Indicator, both sides of enclosure need to be sealed | C | E | Tim Gallegos | McD | 2019-11-27 | Tim Gallegos | Comm | 2020-06-05 | Tim Gallegos | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13565 | Verified | Grout supply and return CCW piping at 1A Sample Panel Chiller | C | C | Johnny Campbell | McD | 2019-11-27 | Johnny Campbell | Comm | 2019-12-09 | Jack Fields | 2019-12-11 | Shannon Scott
CCW-01 | CCW-01 | PI13566 | Verified | Grout supply and return CCW piping at 1C Sample Panel Chiller | C | C | Johnny Campbell | McD | 2019-11-27 | Johnny Campbell | Comm | 2019-12-09 | Jack Fields | 2019-12-11 | Shannon Scott
CCW-01 | CCW-01 | PI13567 | Verified | Remove tape, wire, rope, tie wraps, and old tags from all subsystem piping and components | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-03-27 | James Beech | 2020-04-02 | John Watts
CCW-01 | CCW-01 | PI13568 | Verified | Clean and Paint subsystem piping and components | C | X | Jerry Smith | McD | 2019-11-27 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-04-02 | John Watts
CCW-01 | CCW-01 | PI13569 | Verified | Check/replace CCW-M-0100B; CCW Pump B Motor Termination Box cover gasket, upper side of cover appears to be tight with gap at lower side | C | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Comm | 2020-02-07 | Mike Tabbert | 2020-02-07 | Fred Michael
CCW-01 | CCW-01 | PI13570 | Verified | Check/replace both termination box gaskets at CCW-M-0100A; CCW Pump A Motor | C | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Comm | 2020-02-07 | Mike Tabbert | 2020-02-07 | Alan Huntsman
CCW-01 | CCW-01 | PI13571 | Verified | Power cable conduit Uni-strut strap is loose at 1A Boiler Feed Pump A CCW return Temperature Indicator 1A-CCW-TI-0624A, Line No. 3-1A-CCW-0603 | C | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Comm | 2020-04-28 | Matt Gilmore | 2020-05-26 | Randy Carpenter
CCW-01 | CCW-01 | PI13572 | Verified | No power cable run to 1B-CCW-TI-0624B; 1B Boiler Feed Pump B return line Temperature Indicator, Line No. 3-!B-CCW-0606 | C | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Comm | 2020-02-24 | Mike Tabbert | 2020-02-26 | Keith Pollock
CCW-01 | CCW-01 | PI13573 | Verified | Grind off and seal old ground penetration in concrete foundation at E side of 10-CCW-P-0100A; CCW Pump A | C | E | Johnny Campbell | McD | 2019-11-27 | Johnny Campbell | Comm | 2019-12-12 | Jack Fields | 2019-12-18 | Shannon Scott
CCW-01 | CCW-01 | PI13574 | Verified | Clean up CCW Recirc piping at NW side of STG Mezzanine | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-17 | Charlie English | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13575 | Verified | Power cable conduit missing condolets at 1A-CCW-TI-0642B; 1A Boiler Feed Pump B return line Temperature Indicator, both sides of enclosure | C | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Comm | 2020-02-24 | Mike Tabbert | 2020-02-26 | Keith Pollock
CCW-01 | CCW-01 | PI13576 | Verified | Straighten 10-CCW-PI-0149B; CCW Pump B suction pressure indicator tubing, PI crooked | C | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2019-12-30 | Gonzalo Pena | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13577 | Verified | 10-CCW-PI-0149B; CCW Pump B suction pressure indicator tubing needs to be reworked, tubing hard against pipe support | C | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2019-12-30 | Gonzalo Pena | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13578 | Verified | Adjust rubber seal inside 10-CCW-PIT-0110; CCW discharge header pressure indicating transmitter cabinet | B | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2019-12-30 | Gonzalo Pena | 2020-01-07 | Shannon Scott
CCW-01 | CCW-01 | PI13579 | Verified | 10-CCW-PI-0149A; 10-CCW-P-0100A pressure indicator needs to be turned to W | B | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2019-12-30 | Gonzalo Pena | 2020-01-07 | Shannon Scott
CCW-01 | CCW-01 | PI13580 | Verified | Instrument Air isolation valve to 10-CCW-PC-0131; CCW Recirc Pressure Control Valve is leaking, NW side of STG Mezzanine | B | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2020-02-10 | James Tanner | 2020-02-10 | Shannon Scott
CCW-01 | CCW-01 | PI13581 | Verified | Clean out inside of 10-CCW-PIT-0110; CCW discharge header pressure indicating transmitter cabinet, STG ground floor near CCW Heat Exchangers | C | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2019-12-30 | Gonzalo Pena | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13582 | Verified | Seal tubing penetration at 10-CCW-PIT-0331; CCW Supply Pressure Indicating Transmitter cabinet, NW side STG Bldg , ground floor | C | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2019-12-30 | Gonzalo Pena | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13583 | Verified | Need tie wrap at 90 of 10-CCW-PIT-0110; CCW discharge header pressure indicating transmitter tube bundle | C | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2019-12-30 | Gonzalo Pena | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13584 | Verified | Tighten tubing bundle locking nut at 10-CCW-PIT-0331; CCW Supply Presssure Indicating Transmitter cabinet, NW side STG bldg, ground floor | C | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2019-12-30 | Gonzalo Pena | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13585 | Verified | Tighten loose flex connection to 10-CCW-PIT-0331; CCW Supply Pressure Indicating Transmitter cabinet, NW side STG, ground floor | C | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CCW-01 | CCW-01 | PI13586 | Verified | 1B-CCW-TI-0624A; 1B Boiler Feed Pump A return line Temperature Indicator support is loose, Line No. 3-1B-CCW-0603 | C | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2019-12-30 | Gonzalo Pena | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13587 | Verified | Open conduit condolet at control power to 10-CCW-PC-0131; CCW Recirc Pressure Control Valve | C | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Comm | 2020-04-28 | Matt Gilmore | 2020-05-26 | Randy Carpenter
CCW-01 | CCW-01 | PI13588 | Verified | Clean out 10-CCW-PIT-0131; CCW Suppply Pressure Indicating Transmitter cabinet, NW side STG Bldg, ground floor | C | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2019-12-30 | Gonzalo Pena | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13589 | Verified | Remove choker from tubing bundle above 10-CCW-PIT-0331; CCW Supply Pressure Indicating Transmitter cabinet, NW side STG bldg , ground floor | C | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2020-01-20 | Gonzalo Pena | 2020-02-02 | Shannon Scott
CCW-01 | CCW-01 | PI13590 | Verified | Need tie wrap at 90 of 10-CCW-PIT-0331; CCW Supply Pressure Indicating Transmitter bundle, above cabinet, NW side STG, ground floor | C | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2019-12-30 | Gonzalo Pena | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13591 | Verified | Rework Instrument Air tubing to 1CCW-TV-0313; 1C STG Main Oil Cooler A & B Temperature Control Valve, Line No. 10-1C-CCW-0300X, S side STG Bldg, ground floor | C | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Comm | 2019-12-30 | Gonzalo Pena | 2020-01-06 | Shannon Savoy
CCW-01 | CCW-01 | PI13592 | Verified | 10-CCW-M-0100A; CCW Pump A Motor is missing jacking bolt | C | M | Shane Crowe | McD | 2019-11-27 | Shane Crowe | Comm | 2020-01-15 | Shane Crowe | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13593 | Verified | Tag all CCW-01 Subsystem components | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-04-30 | James Beech | 2021-01-22 | Eric Policarpio
CCW-01 | CCW-01 | PI13594 | Verified | Remove tape from CCW-P-0100B; CCW Pump B suction flange bolts | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-07 | Shannon Scott
CCW-01 | CCW-01 | PI13595 | Verified | Tighten 3" cover plate at 10-CCW-V-045B; CCW Pump B suction valve | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-07 | Shannon Scott
CCW-01 | CCW-01 | PI13596 | Verified | 10-CCW-V-0103B; CCW Pump B discharge drain valve needs cap | C | P | Reggie Brown | McD | 2019-11-27 | Reggie Brown | Comm | 2020-01-31 | Charlie English | 2020-02-05 | Shannon Scott
CCW-01 | CCW-01 | PI13597 | Verified | 10-CCW-V-0103A; CCW Pump A discharge drain valve needs cap | C | P | Reggie Brown | McD | 2019-11-27 | Reggie Brown | Comm | 2020-01-31 | Charlie English | 2020-02-05 | Shannon Scott
CCW-01 | CCW-01 | PI13598 | Verified | Install chain operator at 10-CCW-V-0145B; CCW Pump B suction valve | D | P | Tim Green | McD | 2019-11-27 | Tim Green | Comm | 2020-08-12 | Tim Green | 2020-08-12 | Nelson Eichelberger
CCW-01 | CCW-01 | PI13599 | Verified | Install chain operator at 10-CCW-V-0142; CCW Pump B suction initial fill connection | D | P | Michael Law | McD | 2019-11-27 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-07-28 | Keith Pollock
CCW-01 | CCW-01 | PI13600 | Verified | Verify location of all saddle supports at CCW 24" supply and return piping, saddle supports installed across I-Beam supports at some areas and not others | C | P | Kelvin Cook | McD | 2019-11-27 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-02 | John Watts
CCW-01 | CCW-01 | PI13601 | Verified | 10-CCW-V-0145A; CCW Pump A suction valve needs chain operator | C | P | Kelvin Cook | McD | 2019-11-27 | Kelvin Cook | Comm | 2020-02-11 | Kelvin Cook | 2020-02-15 | Shannon Scott
CCW-01 | CCW-01 | PI13602 | Verified | 10-CCW-V-0115A; CCW Heat Exchanger A inlet isolation valve needs chain operator | C | P | Kelvin Cook | McD | 2019-11-27 | Kelvin Cook | Comm | 2020-02-11 | Kelvin Cook | 2020-02-15 | Shannon Scott
CCW-01 | CCW-01 | PI13603 | Verified | CCW piping rod hanger is bent at CCW Expansion Tank Overflow Tote, Line No. 4-10-CCW-0186, NE side of STG Bldg, ground floor | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-17 | Charlie English | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13604 | Verified | Tighten loose U-Bolt at 1C-GCH-HEX-9000C; 1C STG Generator Hydrogen Cooler C return line, Line No. 6-1C-CCW-0245, N side STG Bldg Mezzanine | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-20 | Bobby Williams | 2019-12-23 | Shannon Scott
CCW-01 | CCW-01 | PI13605 | Verified | Reposition 1CCW-SRV-0239A; 1C STG Generator Hydrogen Cooler A Return Safety Relief Valve exhast to point down, N side STG Bldg Mezzanine | C | P | Kelvin Cook | McD | 2019-11-27 | Kelvin Cook | Comm | 2020-01-31 | Charlie English | 2020-02-10 | Shannon Scott
CCW-01 | CCW-01 | PI13606 | Verified | Reposition 1CCW-SRV-0239D; 1C STG Generator Hydrogen Cooler D Return Safety Relief Valve exhast to point down, N side STG Bldg Mezzanine | C | P | Kelvin Cook | McD | 2019-11-27 | Kelvin Cook | Comm | 2020-01-31 | Charlie English | 2020-02-10 | Shannon Scott
CCW-01 | CCW-01 | PI13607 | Verified | Reposition 1CCW-SRV-0239C; 1C STG Generator Hydrogen Cooler C Return Safety Relief Valve exhast to point down, N side STG Bldg Mezzanine | C | P | Kelvin Cook | McD | 2019-11-27 | Kelvin Cook | Comm | 2020-01-31 | Charlie English | 2020-02-10 | Shannon Scott
CCW-01 | CCW-01 | PI13608 | Verified | Install missing U-Bolt at 1C-GCH-HEX-9000C; 1C Generator Hydrogen Cooler C inlet line, Line No. 6-1C-CCW-0220, N side STG Bldg Mezzanine | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-20 | Bobby Williams | 2019-12-23 | Shannon Scott
CCW-01 | CCW-01 | PI13609 | Verified | Install cap at 1C-CCW-V-0211A; 1C STG Generator Stator Cooling Water Cooler A return line vent valve, Line No. 6-1C-CCW-0255, SE side STG Bldg ground floor, E of CCW Pumps | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-07 | Shannon Scott
CCW-01 | CCW-01 | PI13610 | Verified | Install cap at 1C-CCW-V-0211B; 1C STG Generator Stator Cooling Water Cooler B return line vent valve, Line No. 6-1C-CCW-0260, STG Bldg ground floor, E of CCW Pumps | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-07 | Shannon Scott
CCW-01 | CCW-01 | PI13611 | Verified | 1C-CCW-V-0325B; 1C STG EHC Oil Cooler B return line vent valve needs cap, Line No. 2-1C-CCW-0335, SE side STG Bldg, ground floor | C | P | Reggie Brown | McD | 2019-11-27 | Reggie Brown | Comm | 2020-01-31 | Charlie English | 2020-02-10 | Shannon Scott
CCW-01 | CCW-01 | PI13612 | Verified | Rod hanger and clamp support needs to be straightened at inlet to 1C STG Main Oil Cooler A, Line No. 10-1C-CCW-0300X, S side STG Bldg, ground floor | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-20 | Bobby Williams | 2019-12-23 | Shannon Scott
CCW-01 | CCW-01 | PI13613 | Verified | 1C-CCW-V-0323A; 1C STG Main Oil Cooler A return vent valve needs cap, Line No. 10- 1C-CCW-0340, S side STG Bldg, ground floor | C | P | Reggie Brown | McD | 2019-11-27 | Reggie Brown | Comm | 2020-01-31 | Charlie English | 2020-02-10 | Shannon Scott
CCW-01 | CCW-01 | PI13614 | Verified | 10-CCW-V-0115B; CCW Heat Exchanger B inlet isolation valve needs chain operator | C | P | Kelvin Cook | McD | 2019-11-27 | Kelvin Cook | Comm | 2020-02-11 | Kelvin Cook | 2020-02-15 | Shannon Scott
CCW-01 | CCW-01 | PI13615 | Verified | 1C-CCW-V-0323B; 1C STG Main Oil Cooler B return vent valve needs cap, Line No. 10-1C-CCW-0345, S side STG Bldg, ground floor | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-04-02 | Tim Green | 2020-04-07 | Bernard Stasse
CCW-01 | CCW-01 | PI13616 | Verified | 10-CCW-V-0124A; CCW Heat Exchanger A discharge isolation valve needs chain operator | C | P | Kelvin Cook | McD | 2019-11-27 | Kelvin Cook | Comm | 2020-02-11 | Kelvin Cook | 2020-02-15 | Shannon Scott
CCW-01 | CCW-01 | PI13617 | Verified | Remove chain fall and rope from 1C STG Main Oil Cooler B return line, Line No. 10-1C-CCW-0345, S side STG Bldg, ground floor | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-20 | Bobby Williams | 2019-12-23 | Shannon Scott
CCW-01 | CCW-01 | PI13618 | Verified | 10-CCW-V-0124B; CCW Heat Exchanger B discharge isolation valve needs chain operator | C | P | Kelvin Cook | McD | 2019-11-27 | Kelvin Cook | Comm | 2020-02-11 | Kelvin Cook | 2020-02-15 | Shannon Scott
CCW-01 | CCW-01 | PI13619 | Verified | 1ACCW-SRV-0409A; 1A Generator Hydrogen Gas Cooler 1 Return Safety Relief Valve is missing discharge vent fitting | C | P | James Beech | McD | 2019-11-27 | James Beech | Const | 2020-04-16 | James Beech | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13620 | Verified | Remove tape from flange bolts at 1A Generator Hydrogen Gas Cooler supply line, Line No. 8-1A-CCW-0400, W side of GT A Lube Oil Enclosure, ground floor | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13621 | Verified | Remove tape from flange bolts at 1A Generator Hydrogen Gas Cooler return line, Line No. 8-1A-CCW-0445, W side of GT A Lube Oil Enclosure, ground floor | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13622 | Verified | 1A-CCW-V-0401A; 1A Generator Hydrogen Gas Cooler 1 inlet drain valve needs cap, Line No. 4-1A-CCW-0405 | C | P | Reggie Brown | McD | 2019-11-27 | Reggie Brown | Comm | 2020-01-10 | Charlie English | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13623 | Verified | 1A-CCW-V-0401B; 1A Generator Hydrogen Gas Cooler 2 inlet drain valve needs cap, Line No. 4-1A-CCW-0415X | C | P | Reggie Brown | McD | 2019-11-27 | Reggie Brown | Comm | 2020-01-10 | Charlie English | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13624 | Verified | 1A-CCW-V-0408A; 1A Generator Hydrogen Gas Cooler 1 return drain valve needs cap, Line No. 4-1A-CCW-151X | C | P | Reggie Brown | McD | 2019-11-27 | Reggie Brown | Comm | 2020-01-10 | Charlie English | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13625 | Verified | 1A-CCW-V-0408A; 1A Generator Hydrogen Gas Cooler 2 return drain valve needs cap, Line No. 4-1A-CCW-0420 | C | P | Reggie Brown | McD | 2019-11-27 | Reggie Brown | Comm | 2020-01-10 | Charlie English | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13626 | Verified | 1C-CCW-V-0337A; 1C STG Main Oil Cooler A return isolation valve needs chain operator, Line No. 10-1C-CCW-0340, S side STG Bldg, ground floor | C | P | Kelvin Cook | McD | 2019-11-27 | Kelvin Cook | Comm | 2020-02-11 | Kelvin Cook | 2020-02-15 | Shannon Scott
CCW-01 | CCW-01 | PI13627 | Verified | U-bolt at end of 1B Generator Hydrogen Gas Cooler CCW supply header is missing nut, upstream of flange, Line No. 8-1B-CCW-0400 | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-21 | Charlie English | 2020-02-02 | Shannon Scott
CCW-01 | CCW-01 | PI13628 | Verified | 1B-CCW-V-0459A; 1B Generator Hydrogen Gas Cooler 1 CCW supply line vent valve needs cap, Line No. 4-1B-CCW-0405 | C | P | Reggie Brown | McD | 2019-11-27 | Reggie Brown | Comm | 2020-01-10 | Charlie English | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13629 | Verified | 1B-CCW-V-0459B; 1B Generator Hydrogen Gas Cooler 2 CCW supply line vent valve needs cap, Line No. 4-1B-CCW-0415 | C | P | Reggie Brown | McD | 2019-11-27 | Reggie Brown | Comm | 2020-01-10 | Charlie English | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13630 | Verified | 1B-CCW-V-0459C; 1B Generator Hydrogen Gas Cooler 3 CCW supply line vent valve needs cap, Line No. 4-1B-CCW-0425 | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-10 | Charlie English | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13631 | Verified | 1B-CCW-V-0459D; 1B Generator Hydrogen Gas Cooler 4 CCW supply line vent valve needs cap, Line No. 4-1B-CCW-0435 | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-10 | Charlie English | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13632 | Verified | 1B-CCW-V-0460A; 1B Generator Hydrogen Gas Cooler 1 CCW return line vent valve needs cap, Line No. 4-1B-CCW-0430 | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-10 | Charlie English | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13633 | Verified | 1B-CCW-V-0460B; 1B Generator Hydrogen Gas Cooler 2 CCW return line vent valve needs cap, Line No. 4-1B-CCW-0420 | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-10 | Charlie English | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13634 | Verified | 1B-CCW-V-0408C; 1B Generator Hydrogen Gas Cooler 3 CCW return line drain valve needs cap, Line No. 4-1B-CCW-0430 | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-10 | Charlie English | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13635 | Verified | 1B-CCW-V-0408D; 1B Generator Hydrogen Gas Cooler 4 CCW return line drain valve needs cap, Line No. 4-1B-CCW-0440 | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-10 | Charlie English | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13636 | Verified | 1B Generator Hydrogen Gas Cooler's 1 & 2 supply and return drain valve's; 1B-CCW-V-0401A, 1B-CCW-V-0401B, 1B-CCW-V-0408A, 1B-CCW-V-0408A need to be rotated so valve handles point to the West, current configuration causes pinch points, E side of 1B Generator, ground floor | C | P | Bobby Williams | McD | 2019-11-27 | Bobby Williams | Comm | 2020-02-02 | Charlie English | 2020-02-26 | Keith Pollock
CCW-01 | CCW-01 | PI13637 | Verified | 1C-CCW-V-0337B; 1C STG Main Oil Cooler B return isolation valve needs chain operator, Line No. 10-1C-CCW-0345, S side STG Bldg, ground floor | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13638 | Verified | U-Bolt nuts loose at CCW supply to 1A Boiler Feed Pump A, upstream of 1A-CCW-V-0602A; supply isolation valve | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13639 | Verified | 1A-CCW-SRV-0609A; 1A Boiler Feed Pump A return line safety relief valve bronze discharge not installed, part is hanging on valve in plastic bag | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13640 | Verified | 1A-CCW-SRV-0609B; 1A Boiler Feed Pump B return line safety relief valve bronze discharge not installed, part is hanging on valve in plastic bag | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-15 | Bobby Williams | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13641 | Verified | 1B-CCW-SRV-0609A; 1B Boiler Feed Pump A return line safety relief valve bronze discharge not installed, part is hanging on valve in plastic bag, Line No. 3-1B-CCW-0603 | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-06 | Shannon Scott
CCW-01 | CCW-01 | PI13642 | Verified | 1C-CCW-V-0331B; 1C STG Main Oil Cooler B inlet isolation valve needs chain operator, Line No. 10-1C-CCW-0310 | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13643 | Verified | 1A GT Lube Oil Cooler B return safety relief valve tag number incorrect, currently tagged as 1ACCW-SRV-0409B, should be 1ACCW-SRV-0449B | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13644 | Verified | Rotate 1A-CCW-V-0475A; 1A Boiler Feed Pump A Supply Vent Valve so the handle points to E side of enclosure, current configuration creates pinch point, Line no. 3-1A-CCW-0500 | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-15 | Tim Green | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13645 | Verified | Rotate 1A-CCW-V-0475B; 1A Boiler Feed Pump B Supply Vent Valve so the handle points to E side of enclosure, current configuration creates pinch point, Line No. 3-1A-CCW-0601 | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-15 | Tim Green | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13646 | Verified | Rotate 1B-CCW-V-0761B; 1B Sample Panel Chiller CCW Inlet Drain Valve handle to the W, currently valve is hard against pipe support angle iron, cannot close 100% | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-02-06 | James Beech | 2020-02-26 | Keith Pollock
CCW-01 | CCW-01 | PI13647 | Verified | Ensure all Safety Relief Valve discharge vents face down | C | P | Reggie Brown | McD | 2019-11-27 | Reggie Brown | Comm | 2020-02-11 | Kelvin Cook | 2020-02-15 | Shannon Scott
CCW-01 | CCW-01 | PI13648 | Verified | CCW supply and return lines at 1A-SSS-SCL-0500 to fix grating penetration. Install kick plate where required | C | S | Tim Gallegos | McD | 2019-11-27 | Tim Gallegos | Comm | 2020-06-05 | Tim Gallegos | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13649 | Verified | CCW return line at 1A-SSS-SCL-0500 tighten up U-bolt support | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13650 | Verified | CCW return lines at 1A-SSS-SCL-0500 need additional support | D | P | Bobby Williams | McD | 2019-11-27 | Bobby Williams | Comm | 2020-02-24 | Bobby Williams | 2020-04-02 | John Watts
CCW-01 | CCW-01 | PI13651 | Verified | CCW supply and return lines at 1A-SSS-SCL-0600 to fix grating penetration. Install kick plate where required | C | S | Tim Gallegos | McD | 2019-11-27 | Tim Gallegos | Comm | 2020-06-05 | Tim Gallegos | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13652 | Verified | CCW return line at 1A-SSS-SCL-0600 tighten up U-bolt support | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13653 | Verified | CCW supply and return lines at 1A-SSS-SCL-0300 to fix grating penetration. Install kick plate where required | C | S | Tim Gallegos | McD | 2019-11-27 | Tim Gallegos | Comm | 2020-06-05 | Tim Gallegos | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13654 | Verified | CCW supply line at 1A-SSS-SCL-0300 reposition the valve handle to eliminate pinch point with the return line alve handle | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13655 | Verified | CCW supply line at 1A-SSS-SCL-0300 remove the temporary weld of the pipe to the grating | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13656 | Verified | CCW supply and return lines at 1A-SSS-SCL-0100 to fix grating penetration. Install kick plate where required | C | S | Tim Gallegos | McD | 2019-11-27 | Tim Gallegos | Comm | 2020-06-05 | Tim Gallegos | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13657 | Verified | CCW supply line drain line at 1A-SSS-SCL-0100 correct the obstruction to valve handle | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-02-10 | James Beech | 2020-02-17 | Shannon Scott
CCW-01 | CCW-01 | PI13658 | Verified | CCW supply and return lines at 1A-SSS-SCL-0200 to fix grating penetration. Install kick plate where required | C | S | Tim Gallegos | McD | 2019-11-27 | Tim Gallegos | Comm | 2020-06-05 | Tim Gallegos | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13659 | Verified | CCW return line at 1A-SSS-SCL-0200 to correct valve handle orientation pinch point | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-02-10 | James Beech | 2020-02-17 | Shannon Scott
CCW-01 | CCW-01 | PI13660 | Verified | CCW supply and return lines at 1B-SSS-SCL-0400 to fix grating penetration. Install kick plate where required | C | S | Bobby Williams | McD | 2019-11-27 | Bobby Williams | Comm |  |  | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13661 | Verified | CCW supply and return lines at 1B-SSS-SCL-0400 to tighten u-bolt support | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13662 | Verified | CCW supply and return lines at 1B-SSS-SCL-0500 to fix grating penetration. Install kick plate where required | C | S | Tim Gallegos | McD | 2019-11-27 | Tim Gallegos | Comm | 2020-05-08 | Tim Gallegos | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13663 | Verified | CCW supply line at 1B-SSS-SCL-0500 need additional support | D | P | Michael Law | McD | 2019-11-27 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13664 | Verified | CCW supply line at 1B-SSS-SCL-0500 drain valve handle to rotate | D | P | Michael Law | McD | 2019-11-27 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13665 | Verified | CCW return line at 1B-SSS-SCL-0500 tighten up u bolt. Line not supported properly | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13666 | Verified | CCW supply and return lines at 1B-SSS-SCL-0100 to fix grating penetration. Install kick plate where required | C | S | Tim Gallegos | McD | 2019-11-27 | Tim Gallegos | Comm | 2020-05-08 | Tim Gallegos | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13667 | Verified | CCW supply and return lines at 1B-SSS-SCL-0100 u-bolt support to tighten | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-20 | Shannon Scott
CCW-01 | CCW-01 | PI13668 | Verified | CCW supply and return lines at 1B-SSS-SCL-0600 u-bolt support to tighten | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI13669 | Verified | CCW supply and return lines at 1B-SSS-SCL-0600 to fix grating penetration. Install kick plate where required | C | S | Tim Gallegos | McD | 2019-11-27 | Tim Gallegos | Comm | 2020-05-08 | Tim Gallegos | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13670 | Verified | CCW supply line at 1B-SSS-SCL-0600 drain valve handle to reposition | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-01-25 | James Beech | 2020-02-17 | Shannon Scott
CCW-01 | CCW-01 | PI13671 | Verified | CCW supply and return lines at 1B-SSS-SCL-0200 to fix grating penetration. Install kick plate where required | C | S | Tim Gallegos | McD | 2019-11-27 | Tim Gallegos | Comm | 2020-05-08 | Tim Gallegos | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13672 | Verified | CCW supply and return lines at 1B-SSS-SCL-0200 to correct pinch point on both lines | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-02-10 | James Beech | 2020-02-17 | Shannon Scott
CCW-01 | CCW-01 | PI13673 | Verified | CCW return line at 1B-SSS-SCL-0200 loose nut on u-bolt | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2020-04-14 | James Beech | 2020-07-29 | John Watts
CCW-01 | CCW-01 | PI13674 | Verified | 1A GT Lube Oil Cooler A and B CCW supply and return piping support has loose nut at NW baseplate, E side of 1A GT | C | P | James Beech | McD | 2019-11-27 | James Beech | Comm | 2019-12-31 | Bobby Williams | 2020-01-13 | Shannon Scott
CCW-01 | CCW-01 | PI14525 | Verified | 10-CCW-LIT-0170 - Level gauge on expansion tank will not put out a proper tank level. The line was drained several times, but that did not fix it. When using a magnet to reset the gauge, we were able to get a level, but all the strips were not working properly. And, when we drained the line to test the strips, they wouldn't move to show the level going down. | B | I | Albert Burge | McD | 2019-12-07 | Albert Burge | Comm | 2020-02-05 | Albert Burge | 2020-02-11 | Shannon Scott
CCW-01 | CCW-01 | PI14526 | Verified | 10-CCW-PIT-0110 - The pressure transmitter for CCW header needs a weather proof enclosure | C | I | James Tanner | McD | 2019-12-07 | James Tanner | Comm | 2019-12-08 | Shannon Scott | 2019-12-11 | Shannon Scott
CCW-01 | CCW-01 | PI14527 | Verified | 10-CCW-PIT-0140 - The pressure transmitter for CCW header needs a weather proof enclosure | C | I | James Tanner | McD | 2019-12-07 | James Tanner | Comm | 2019-12-08 | Shannon Scott | 2019-12-11 | Shannon Scott
CCW-01 | CCW-01 | PI14687 | Verified | 10-CCW-PIT-0131-LOOSE FLEX CONNECTOR. | C | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const |  |  | 2019-12-13 | John Sullivan
CCW-01 | CCW-01 | PI14856 | Verified | Missing pipe support hanger 10-CCW-PD-HGR-0190 - Engineering to check missing/not installed support | A | P | Bobby Williams | McD | 2019-12-20 | Bobby Williams | Comm | 2020-01-08 | Bobby Williams | 2020-01-23 | Blake Boudreaux
CCW-01 | CCW-01 | PI14857 | Verified | Missing pipe support hanger 10-CCW-PD-HGR-0183 - Engineering to check missing/not installed support | A | P | Bobby Williams | McD | 2019-12-20 | Bobby Williams | Comm | 2020-01-08 | Bobby Williams | 2020-01-23 | Blake Boudreaux
CCW-01 | CCW-01 | PI14858 | Verified | Missing pipe support hanger 10-CCW-PD-HGR-0233 - Engineering to check missing/not installed support | A | P | Bobby Williams | McD | 2019-12-20 | Bobby Williams | Comm | 2020-01-08 | Bobby Williams | 2020-01-23 | Blake Boudreaux
CCW-01 | CCW-01 | PI14865 | Verified | 1C-CCW-SRV-0336B (1C STG Main Oil Cooler B) - Safety Relief valve in cable tray needs to be relocated | B | P | Bobby Williams | McD | 2019-12-23 | Bobby Williams | Comm | 2020-02-06 | Charlie English | 2020-02-10 | Shannon Scott
CCW-01 | CCW-01 | PI15889 | Verified | 10-CCW-STN-0148A - Operators cannot remove strainer on CCW A pump due to low-hanging conduit | C | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Comm | 2020-01-15 | Shannon Scott | 2020-01-15 | Shannon Scott
CCW-01 | CCW-01 | PI15890 | Verified | 10-CCW-V-0116A, 10-CCW-V-0116B,10-CCW-SRV-0123A, 10-CCW-SRV-0123B- Cannot access valves | D | P | Michael Law | McD | 2020-01-13 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
CCW-01 | CCW-01 | PI18108 | Verified | 10-CCW-LIT-0170 - The local indication is stuck on 23, which does not match the true value being sent to DCS. | C | I | Albert Burge | McD | 2020-03-20 | Albert Burge | Comm | 2020-03-30 | Albert Burge | 2021-01-05 | Keith Pollock
CCW-01 | CCW-01 | PI18189 | Verified | Ensure the suction strainers have been pulled on CCW Pumps | C | P | William Mitchell | McD | 2020-03-26 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2020-04-17 | John Watts
CEM-01 | CEM-01 | PI09694 | Verified | Missing teflon washers in CB10 and CB7 hose fittings to Calibration Gas Bottles | B | I | Albert Burge | McD | 2019-10-16 | Albert Burge | Comm | 2020-01-16 | Albert Burge | 2020-01-16 | Albert Burge
CEM-01 | CEM-01 | PI09695 | Verified | 1B LAN CAB not shown on Units 1A & 1B CEMS Typical Shelter Floor Plan; Drawing No. 00573.03.01 | D | E | Michael Law | McD | 2019-10-16 | Michael Law | Comm |  |  | 2019-12-18 | Randy Carpenter
CEM-01 | CEM-01 | PI09696 | Verified | Remove tie wraps from CEM Bldg A interior lighting | C | E | Chris Colvin | McD | 2019-10-16 | Chris Colvin | Comm | 2019-12-01 | Fred Michael | 2019-12-16 | Randy Carpenter
CEM-01 | CEM-01 | PI09697 | Verified | Update ESF-PNL-0006 Panel Schedule | C | E | Mike Tabbert | McD | 2019-10-16 | Mike Tabbert | Comm | 2019-12-01 | Fred Michael | 2019-12-18 | Randy Carpenter
CEM-01 | CEM-01 | PI09698 | Verified | Need support for Ethernet to Fiber Cable inside 1A-CEM-CAB-0001 | C | E | Mike Tabbert | McD | 2019-10-16 | Mike Tabbert | Comm | 2020-02-12 | Mike Tabbert | 2020-04-02 | John Watts
CEM-01 | CEM-01 | PI09699 | Verified | Clean off rust on CEM Bldg B roof | C | C | Alan Huntsman | McD | 2019-10-16 | Alan Huntsman | Comm | 2019-12-01 | Albert Burge | 2019-12-16 | Randy Carpenter
CEM-01 | CEM-01 | PI09700 | Verified | Secure umbilical to top of stack with metal hose clamps every 3 ft | D | I | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-07-16 | Nelson Eichelberger
CEM-01 | CEM-01 | PI09701 | Verified | Cable 1ACEMX0003-PR-15 not terminated inside 1A-CEM-CAB-0001 Cabinet | C | E | Logan Holland | McD | 2019-10-16 | Logan Holland | Comm | 2019-10-18 | Mike Tabbert | 2019-10-28 | Shannon Scott
CEM-01 | CEM-01 | PI09702 | Verified | Cable 1ACEMX0003-PR-16 not terminated inside 1A-CEM-CAB-0001 Cabinet | C | E | Logan Holland | McD | 2019-10-16 | Logan Holland | Comm | 2019-10-18 | Mike Tabbert | 2019-10-28 | Shannon Scott
CEM-02 | CEM-02 | PI02238 | Verified | 1BCEMK0001, Pull Cable. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
CEM-02 | CEM-02 | PI02239 | Verified | 1BCEMK0001, Terminate Cable. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
CEM-02 | CEM-02 | PI02240 | Verified | Install lean-to on outside of CEMS building. | B | M | Shane Crowe | McD | 2019-07-09 | Shane Crowe | Const | 2019-07-18 | Joshua Sturgeon | 2019-07-23 | Mike Tabbert
CEM-02 | CEM-02 | PI02241 | Verified | Install stack probe. | B | I | Gonzalo Pena | McD | 2019-07-09 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-05 | Mike Tabbert
CEM-02 | CEM-02 | PI02242 | Verified | Install bottle racks. | B | I | Gonzalo Pena | McD | 2019-07-09 | Gonzalo Pena | Const | 2019-08-08 | Gonzalo Pena | 2019-08-14 | Mike Tabbert
CEM-02 | CEM-02 | PI02237 | Verified | Tighten CEMS Building anchor bolts to foundation. | B | M | Shane Crowe | McD | 2019-07-09 | Shane Crowe | Const | 2019-07-17 | Tim Gallegos | 2019-07-23 | Mike Tabbert
CEM-02 | CEM-02 | PI09703 | Verified | Route ITS cables in conduit, West side of CEM Bldg B | B | E | Sheri Fritz | ITS | 2019-10-16 | Sheri Fritz | Comm | 2020-01-09 | Sheri Fritz | 2020-01-13 | Fred Michael
CEM-02 | CEM-02 | PI09704 | Verified | Heat shrink Umbilical at West side of CEM Bldg B | C | I | Gonzalo Pena | McD | 2019-10-16 | Gonzalo Pena | Comm | 2019-11-09 | James Tanner | 2019-11-13 | Shannon Scott
CEM-02 | CEM-02 | PI09705 | Verified | Remove plastic cover from SS Bottle Rack overhead cover at West side of CEM Bldg B | C | I | Gonzalo Pena | McD | 2019-10-16 | Gonzalo Pena | Comm | 2019-11-09 | James Tanner | 2019-11-13 | Shannon Scott
CEM-02 | CEM-02 | PI09706 | Verified | Install additional ground cable at NW corner of CEM Bldg B | C | E | Dustin Futrell | McD | 2019-10-16 | Dustin Futrell | Comm | 2019-10-18 | Mike Tabbert | 2019-10-24 | Shannon Scott
CEM-02 | CEM-02 | PI09707 | Verified | Missing teflon washers in CB10 and CB7 hose fittings to Calibration Gas Bottles | B | I | Albert Burge | McD | 2019-10-16 | Albert Burge | Comm | 2020-01-16 | Albert Burge | 2020-01-16 | Albert Burge
CEM-02 | CEM-02 | PI09708 | Verified | 1B LAN CAB not shown on Units !A & 1B CEMS Typical Shelter Floor Plan; Drawing No. 00573.03.01 | D | E | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2019-12-01 | Fred Michael | 2019-12-18 | Randy Carpenter
CEM-02 | CEM-02 | PI09709 | Verified | Remove tie wraps from CEM Bldg B interior lighting | C | E | Chris Colvin | McD | 2019-10-16 | Chris Colvin | Comm |  |  | 2020-01-13 | Fred Michael
CEM-02 | CEM-02 | PI09710 | Verified | Update ESF-PNL-0006 Panel Schedule | C | E | Mike Tabbert | McD | 2019-10-16 | Mike Tabbert | Comm | 2019-12-01 | Fred Michael | 2019-12-11 | Shannon Scott
CEM-02 | CEM-02 | PI09711 | Verified | Need support for Ethernet to Fiber Cable inside 1B-CEM-CAB-0001 | C | E | Sheri Fritz | ITS | 2019-10-16 | Sheri Fritz | Comm | 2019-12-01 | Fred Michael | 2019-12-18 | Randy Carpenter
CEM-02 | CEM-02 | PI09712 | Verified | Remove nail stuck in CEM Bldg B roof | C | C | Johnny Campbell | McD | 2019-10-16 | Johnny Campbell | Comm | 2019-11-05 | Johnny Campbell | 2019-11-07 | Shannon Scott
CEM-02 | CEM-02 | PI09713 | Verified | Clean off rust on CEM Bldg B roof | C | C | Alan Huntsman | McD | 2019-10-16 | Alan Huntsman | Comm | 2019-12-01 | Fred Michael | 2019-12-16 | Randy Carpenter
CEM-02 | CEM-02 | PI09714 | Verified | Secure umbilical to top of stack with metal hose clamps every 3 ft | D | I | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2019-12-23 | Michael Law | 2020-01-13 | Fred Michael
CEM-02 | CEM-02 | PI02230 | Verified | Repair seal tite at the CEMs building disconnect switch. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
CEM-02 | CEM-02 | PI02229 | Verified | Move CEMS building ground. It runs where the bottle rack will be. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
CEM-02 | CEM-02 | PI02227 | Verified | Component tags that are installed do not have the tag numbers, only description. | C | E | Chris Colvin | McD | 2019-07-09 | Chris Colvin | Const | 2021-01-22 | Eric Policarpio | 2021-01-22 | Eric Policarpio
CEM-02 | CEM-02 | PI02225 | Verified | Terminate transformer 1B-CEM-XFM-0001 factory cables. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
CEM-02 | CEM-02 | PI02223 | Verified | Install CEMs building drain pipe. | B | P | Terry Deaton | McD | 2019-07-09 | Terry Deaton | Const | 2019-08-02 | Terry Deaton | 2019-08-03 | Justin Houdeshell
CEM-02 | CEM-02 | PI02221 | Verified | Pull umbilical slack to top. | B | I | Gonzalo Pena | McD | 2019-07-09 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-07 | Albert Burge
CEM-01 | CEM-01 | PI02236 | Verified | Tighten CEMS Building anchor bolts to foundation. | B | M | Shane Crowe | McD | 2019-07-09 | Shane Crowe | Const | 2019-07-17 | Tim Gallegos | 2019-07-23 | Mike Tabbert
CEM-01 | CEM-01 | PI02235 | Verified | Install bottle racks. | B | I | Gonzalo Pena | McD | 2019-07-09 | Gonzalo Pena | Const | 2019-08-08 | Gonzalo Pena | 2019-08-14 | Mike Tabbert
CEM-01 | CEM-01 | PI02234 | Verified | Install stack probe. | B | I | Gonzalo Pena | McD | 2019-07-09 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-28 | Mike Tabbert
CEM-01 | CEM-01 | PI02233 | Verified | Install lean-to on outside of CEMS building. | B | M | Shane Crowe | McD | 2019-07-09 | Shane Crowe | Const | 2019-07-18 | Joshua Sturgeon | 2019-07-23 | Mike Tabbert
CEM-01 | CEM-01 | PI02232 | Verified | 1ACEMK0001, Terminate Cable. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
CEM-01 | CEM-01 | PI02231 | Verified | Repair seal tite at the CEMs building transformer. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
CEM-01 | CEM-01 | PI02228 | Verified | Move CEMS building ground. It runs where the bottle rack will be. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
CEM-01 | CEM-01 | PI02226 | Verified | Component tags that are installed do not have the tag numbers, only description. | C | E | Mike Tabbert | McD | 2019-07-09 | Mike Tabbert | Const | 2020-02-06 | Mike Tabbert | 2020-02-10 | Fred Michael
CEM-01 | CEM-01 | PI02224 | Verified | Terminate transformer 1a-CEM-XFM-0001 factory cables. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
CEM-01 | CEM-01 | PI02222 | Verified | Install CEMs building drain pipe. | B | P | Terry Deaton | McD | 2019-07-09 | Terry Deaton | Const | 2019-08-02 | Terry Deaton | 2019-08-03 | Justin Houdeshell
CEM-01 | CEM-01 | PI02220 | Verified | Pull umbilical slack to top. | B | I | Gonzalo Pena | McD | 2019-07-09 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-07 | Albert Burge
CEM-02 | CEM-02 | PI02788 | Verified | Submit CCFs for 1B-CEM-CAB-0002, 1B-CEM-AT-0002, 0006 & 0007 - Only need CCF for AT-0002 | B | I | Gonzalo Pena | McD | 2019-07-25 | Gonzalo Pena | Const |  |  | 2019-10-16 | Eric Policarpio
CEM-02 | CEM-02 | PI16543 | Verified | 1B-CEM-AT-0002 - The HMI screen on the 1B NOX/O2 analyzer (1B-CEM-AT-0001) has failed and does not allow operation. | B | I | Albert Burge | McD | 2020-02-06 | Albert Burge | Comm | 2020-02-19 | Albert Burge | 2020-02-24 | Keith Pollock
CEM-02 | CEM-02 | PI16544 | Verified | 1B-CEMS-UMBILICAL - LCPS Unit 1B NH3 (converted sample) analyzer is not seeing any sample gases. When the direct calibration toggle switch is on, the analyzer sees calibration gases. The sample lines in the umbilical coming into the CEMS shelter were swapped in troubleshooting and the problem followed. This proves the issue is in the umbilical up to and including the probe box. | B | I | Albert Burge | McD | 2020-02-06 | Albert Burge | Comm | 2020-02-19 | Albert Burge | 2020-02-28 | John Watts
CEM-02 | CEM-02 | PI16545 | Verified | 1B-CEM-AT-0007 - 1B Converter - The converter is burnt and not operational. The converter inlet stainless tubing and the top of the converter separated from the body of the converter. The extreme heat caused the insulation to break loose and travel to the filter (CCSF1) causing the filter to need replacement also. | B | I | Albert Burge | McD | 2020-02-06 | Albert Burge | Comm | 2020-03-06 | Albert Burge | 2020-03-06 | Nelson Eichelberger
CEM-01 | CEM-01 | PI18023 | Verified | The HVAC system is not working. It is currently 80-85 degrees in the CEMS shelter. The operator tried turning the HVAC on and off several times, but that had no effect. It seems like the fan on the outside of the shelter is not working properly. | C | E | Mike Tabbert | McD | 2020-03-17 | Mike Tabbert | Comm | 2020-04-06 | Mike Tabbert | 2020-04-16 | Keith Pollock
CEM-01 | CEM-01 | PI09693 | Verified | Install additional ground cable at NW corner of CEM Bldg A | C | E | Dustin Futrell | McD | 2019-10-16 | Dustin Futrell | Comm | 2019-10-18 | Mike Tabbert | 2019-10-24 | Shannon Scott
CEM-01 | CEM-01 | PI09692 | Verified | Remove plastic cover from SS Bottle Rack overhead cover at West side of CEM Bldg A | C | I | Gonzalo Pena | McD | 2019-10-16 | Gonzalo Pena | Comm | 2019-11-09 | James Tanner | 2019-11-13 | Shannon Scott
CEM-01 | CEM-01 | PI09691 | Verified | Heat shrink Umbilical at West side of CEM Bldg A | C | I | Gonzalo Pena | McD | 2019-10-16 | Gonzalo Pena | Comm | 2019-11-09 | James Tanner | 2019-11-13 | Shannon Scott
CEM-01 | CEM-01 | PI09690 | Verified | Route ITS cables in conduit, West side of CEM Bldg A | B | E | Sheri Fritz | ITS | 2019-10-16 | Sheri Fritz | Comm | 2020-01-09 | Sheri Fritz | 2020-03-04 | Nelson Eichelberger
CEM-01 | CEM-01 | PI02787 | Verified | Submit CCFs for 1A-CEM-CAB-0002, 1A-CEM-AT-0002, 0006 & 0007 - Only need CCF for AT-0002 | B | I | Gonzalo Pena | McD | 2019-07-25 | Gonzalo Pena | Const |  |  | 2019-10-16 | Eric Policarpio
CIV-01 | CIV-01 | PI16222 | Verified | Flocculant tank containment drain valve needs tag. | C | P | Tim Green | McD | 2020-01-21 | Tim Green | Comm | 2020-07-24 | Tim Green | 2020-08-14 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16233 | Cleared | Raw water building east side door does not have panic hardware. | C | S | Tim Gallegos | McD | 2020-01-21 | Tim Gallegos | Comm | 2020-04-22 | Tim Gallegos
CIV-01 | CIV-01 | PI16234 | Verified | Seal conduit penetrations in the flocculant skid room. | C | E | Tim Gallegos | McD | 2020-01-21 | Tim Gallegos | Comm | 2020-04-30 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-01 | CIV-01 | PI16235 | Verified | Flocculant room - south interior wall missing screws. | C | S | Bobby Williams | McD | 2020-01-21 | Bobby Williams | Comm | 2020-02-21 | Tim Gallegos | 2020-02-26 | John Watts
CIV-01 | CIV-01 | PI16236 | Verified | Flocculant room - remove nails & point & patch floc. Skid. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-02-10 | Jerry Smith | 2020-03-03 | Michael Law
CIV-01 | CIV-01 | PI16237 | Verified | Flocculant / compressor room interior door threshhold missing screw. | C | S | Bobby Williams | McD | 2020-01-21 | Bobby Williams | Comm | 2020-02-21 | Tim Gallegos | 2020-02-26 | John Watts
CIV-01 | CIV-01 | PI16238 | Verified | Flocculant room exterior door - top latch does not engage. | C | S | Bobby Williams | McD | 2020-01-21 | Bobby Williams | Comm | 2020-03-06 | Tim Gallegos | 2020-03-12 | John Watts
CIV-01 | CIV-01 | PI16239 | Verified | Seal / shroud pipe penetrations on south side of water treatment building. | C | S | Bobby Williams | McD | 2020-01-21 | Bobby Williams | Comm | 2020-02-05 | Tim Gallegos | 2020-06-08 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16240 | Verified | Flocculant tank roof structure - double nut all anchor bolts (all 4 corners). | C | S | Bobby Williams | McD | 2020-01-21 | Bobby Williams | Comm | 2020-01-27 | Tim Gallegos | 2020-02-05 | Shannon Scott
CIV-01 | CIV-01 | PI16241 | Verified | Point & patch on the exterior of the flocculant tank containment walls. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-02-14 | Alan Huntsman | 2020-02-26 | John Watts
CIV-01 | CIV-01 | PI16242 | Verified | Grind down the cut unused anchor bolts on foundation west of floc. Tank containment. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-02-14 | Alan Huntsman | 2020-02-26 | John Watts
CIV-01 | CIV-01 | PI16243 | Verified | Clean out the flocculant tank containment when all work is done (insulation). | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-02-19 | Alan Huntsman | 2020-05-27 | Dave Goldak
CIV-01 | CIV-01 | PI16244 | Verified | Raw water priming pump skids need mortar rub on the bush hammered surfaces. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-02-10 | Jerry Smith | 2020-02-20 | John Watts
CIV-01 | CIV-01 | PI16245 | Verified | Flocculant tank containment ladder top rail extensions are bent. | C | S | Bobby Williams | McD | 2020-01-21 | Bobby Williams | Comm | 2020-01-25 | Tim Gallegos | 2020-02-05 | Shannon Scott
CIV-01 | CIV-01 | PI16246 | Verified | Flocculant tank containment ladder needs concrete landing pad. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-02-10 | Jerry Smith | 2020-02-20 | John Watts
CIV-01 | CIV-01 | PI16247 | Verified | Cut / remove unused screw on inside of beam on the southeast corner of flocculant tank containment. | C | S | Bobby Williams | McD | 2020-01-21 | Bobby Williams | Comm | 2020-01-25 | Tim Gallegos | 2020-02-05 | Shannon Scott
CIV-01 | CIV-01 | PI16248 | Verified | Complete gutter & downspout on the flocculant tank roof. | C | S | Sheri Fritz | MOO | 2020-01-21 | Sheri Fritz | Comm | 2020-04-30 | Tim Mills | 2020-05-27 | Dave Goldak
CIV-01 | CIV-01 | PI16250 | Cleared | Raw water building west double doors do not have auto door closers. | C | S | Tim Gallegos | McD | 2020-01-21 | Tim Gallegos | Comm | 2020-04-22 | Tim Gallegos
CIV-01 | CIV-01 | PI16251 | Verified | Raw water building does not have "Exit Lights". | C | E | Mike Tabbert | McD | 2020-01-21 | Mike Tabbert | Comm | 2020-04-21 | Mike Tabbert | 2020-07-10 | Dave Goldak
CIV-01 | CIV-01 | PI16252 | Verified | Raw water pump area - foundation - remove nails in concrete on east side. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-02-19 | Alan Huntsman | 2020-02-26 | John Watts
CIV-01 | CIV-01 | PI16253 | Verified | Raw water pump area - foundation - point & patch gouges / unused anchor bolts. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-02-14 | Alan Huntsman | 2020-02-26 | John Watts
CIV-01 | CIV-01 | PI16254 | Verified | Raw water pump area - re-install handrails around syphon line so that the toe boards are on the grating side. | C | S | Bobby Williams | McD | 2020-01-21 | Bobby Williams | Comm | 2020-02-10 | Tim Gallegos | 2020-02-21 | John Watts
CIV-01 | CIV-01 | PI16255 | Verified | Raw water pump area - grating clips missing. | C | S | Bobby Williams | McD | 2020-01-21 | Bobby Williams | Comm | 2020-02-05 | Tim Gallegos | 2020-02-12 | Dave Goldak
CIV-01 | CIV-01 | PI16256 | Verified | Raw water pump area - grout pipe supports for vent line on top of retaining wall. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-03-05 | Alan Huntsman | 2020-03-05 | Dave Goldak
CIV-01 | CIV-01 | PI16257 | Verified | Raw water pump area - mortar rub, point & patch retaining wall (all sides). | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-03-05 | Alan Huntsman | 2020-03-05 | Dave Goldak
CIV-01 | CIV-01 | PI16258 | Verified | Raw water pump area - pipe supports at the southwest corner - repair or replace grout. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-02-10 | Jerry Smith | 2020-02-20 | John Watts
CIV-01 | CIV-01 | PI16260 | Verified | Raw water pump area - concrete sleepers (4) for the syphon line - pull nails, point & patch and mortar rub. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-03-05 | Alan Huntsman | 2020-03-05 | Dave Goldak
CIV-01 | CIV-01 | PI16261 | Verified | Complete all stone surfacing required in the Raw Water Area. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-03-19 | Johnny Campbell | 2020-05-27 | Dave Goldak
CIV-01 | CIV-01 | PI16262 | Verified | Raw water pump area - the two concrete sllepers outside of the fence need backfill. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-03-05 | Alan Huntsman | 2020-03-05 | Dave Goldak
CIV-01 | CIV-01 | PI16263 | Verified | Raw water pump area - complete rip rap at the box culvert on the upstream side - on north/south road to raw water area. | C | C | Brooks Baker | McD | 2020-01-21 | Brooks Baker | Comm | 2020-04-03 | Johnny Campbell | 2020-07-07 | Dave Goldak
CIV-01 | CIV-01 | PI16264 | Verified | Raw water pump area - install jersey barriers at roadway at the box culvert - on north/south road to raw water area. | D | C | Michael Law | McD | 2020-01-21 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-07-07 | Dave Goldak
CIV-01 | CIV-01 | PI16265 | Verified | Raw water pump area - backfill area on west side of the raw water area near the southwest fence gate. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-05-27 | Dave Goldak
CIV-01 | CIV-01 | PI16224 | Verified | Raw water foundation - patch northeast corner. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-02-19 | Alan Huntsman | 2020-03-05 | Dave Goldak
CIV-01 | CIV-01 | PI16225 | Verified | Raw water foundation - cut unused anchor bolts flush to concrete - at conduit support for 10-DCS-CAB-0204. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-02-10 | Jerry Smith | 2020-02-20 | John Watts
CIV-01 | CIV-01 | PI16226 | Verified | Seal conduit penetrations on north and south side of raw building & unused screw holes on the north side. | C | E | Chris Colvin | McD | 2020-01-21 | Chris Colvin | Comm | 2020-01-23 | Jared Stimpson | 2020-01-30 | Fred Michael
CIV-01 | CIV-01 | PI15429 | Verified | Filter press enclosure - Anchor bolt washer plate weld is not complete | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-05 | Tim Gallegos | 2020-02-07 | Michael Law
CIV-01 | CIV-01 | PI15430 | Verified | Filter press - Install roof beams to support roofing | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-01 | CIV-01 | PI15431 | Verified | Filter Press - Inside enclosure equipment platform - nosing at platform landing, toe plate at equipment opening | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-05 | Tim Gallegos | 2020-02-07 | Michael Law
CIV-01 | CIV-01 | PI16227 | Verified | Seal discharge pipe penetrations on the north side of the raw water building. | C | P | Johnny Campbell | McD | 2020-01-21 | Johnny Campbell | Comm | 2020-03-18 | Johnny Campbell | 2020-06-08 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16228 | Verified | Raw water foundation - point & patch concrete on west side of the unit substation transformer. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-02-10 | Jerry Smith | 2020-02-20 | John Watts
CIV-01 | CIV-01 | PI16229 | Verified | Label on/off switch on west side of raw water building. | C | E | Chris Colvin | McD | 2020-01-21 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-07-10 | Dave Goldak
CIV-01 | CIV-01 | PI16230 | Verified | Adjust raw water building west side double door hardware - top bolt not lining up to engage. | C | S | Bobby Williams | McD | 2020-01-21 | Bobby Williams | Comm | 2020-02-21 | Tim Gallegos | 2020-02-26 | John Watts
CIV-01 | CIV-01 | PI16231 | Verified | Both compressor skids in the raw water building need mortar rub on bush hammered surface. | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-02-10 | Jerry Smith | 2020-02-20 | John Watts
CIV-01 | CIV-01 | PI16232 | Verified | Louver on southeast corner in the raw water building does not close properly. | C | M | Shane Crowe | McD | 2020-01-21 | Shane Crowe | Comm | 2020-01-24 | Shane Crowe | 2020-02-05 | Shannon Scott
CIV-01 | CIV-01 | PI16219 | Verified | Manhole MH-03 - grade surrounding area for drainage (at road to raw water area). | C | C | Alan Huntsman | McD | 2020-01-21 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-05-27 | Dave Goldak
CIV-01 | CIV-01 | PI16220 | Verified | Red line dwg. LK-10-000-PL-CE-CVL-0135. | D | C | Michael Law | McD | 2020-01-21 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-06-16 | Dave Goldak
CIV-01 | CIV-01 | PI16221 | Verified | Install fencing at Raw Water area with 20' double swing gate. | C | C | Sheri Fritz | BEA | 2020-01-21 | Sheri Fritz | Comm | 2020-05-21 | Jason Ezell | 2020-05-27 | Dave Goldak
CIV-01 | CIV-01 | PI15482 | Verified | Clarifier sodium hydrocloride tank building enclosure pad off | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-17 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-01 | CIV-01 | PI15483 | Verified | Makeup water Chemical storage - extend grating for inside ladder | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-17 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-01 | CIV-01 | PI15484 | Verified | Makeup water Chemical storage - add toe plate for equipment opening | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-17 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-01 | CIV-01 | PI16857 | Verified | Clean and close - entire storm collection network. | C | C | Brooks Baker | McD | 2020-02-17 | Brooks Baker | Const | 2020-06-16 | Dave Goldak | 2020-06-16 | Dave Goldak
CIV-01 | CIV-01 | PI17655 | Verified | Outfall 002 at the corner of the retention pond needs safer access for operators to take this sample. Suggestion: Stairs, Handrail, Platform | C | S | Bobby Williams | McD | 2020-03-04 | Bobby Williams | Comm | 2020-03-26 | Tim Gallegos | 2020-03-31 | John Watts
CIV-02 | CIV-02 | PI02450 | Verified | Ladder landing dislodged. Put back in position. | C | C | Johnny Campbell | McD | 2019-07-22 | Johnny Campbell | Const | 2019-07-25 | Johnny Campbell | 2019-08-08 | Dave Goldak
CIV-02 | CIV-02 | PI02451 | Verified | Install ladder rail bolts to concrete pad. | C | S | Tim Gallegos | McD | 2019-07-22 | Tim Gallegos | Const | 2019-07-25 | Tim Gallegos | 2019-08-08 | Dave Goldak
CIV-02 | CIV-02 | PI15452 | Verified | STG Mezz Floor - Provide toe plates around opening | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
CIV-02 | CIV-02 | PI15453 | Verified | STG Mezz Floor - Provide banding where grating is cut for opening | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
CIV-02 | CIV-02 | PI15454 | Verified | STG Mezz floor - handrail cut for opening or equipment access need finish | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
CIV-02 | CIV-02 | PI15459 | Verified | Removable HR above lube oil tank not secured properly (2014-502-HR1) | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-04-02 | Michael Law
CIV-02 | CIV-02 | PI15460 | Verified | Complete Valve Access platform Installation (Seq 201-0) - Ground level STG | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-04 | Michael Law | 2020-05-04 | Michael Law
CIV-02 | CIV-02 | PI15465 | Verified | STG Operating deck - correct handrail near stair tower cut for steam blow pipe 2031-506HR2 | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-04-02 | Michael Law
CIV-02 | CIV-02 | PI15474 | Verified | Install removable hatch at South opening | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-08 | Tim Gallegos | 2020-04-09 | Michael Law
CIV-02 | CIV-02 | PI15475 | Verified | STG operating deck - near pipe rack - fix handrail at pipe 2031-516HR1 | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-04-02 | Michael Law
CIV-02 | CIV-02 | PI15476 | Verified | STG Operating deck - near pipe rack - fix grating opening in floor | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-04-02 | Michael Law
CIV-02 | CIV-02 | PI15477 | Verified | STG Operating deck - near pipe rack - fix handrail cut for pipe or valves | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-04-02 | Michael Law
CIV-02 | CIV-02 | PI15478 | Verified | STG thyristor cubical - Reverse bracing at the ladder - 2013-300V3 | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-26 | Tim Gallegos | 2020-02-27 | Michael Law
CIV-02 | CIV-02 | PI15479 | Verified | STG thyristor cubical - Extend grating at the ladder | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-26 | Tim Gallegos | 2020-02-27 | Michael Law
CIV-02 | CIV-02 | PI15480 | Verified | Pipe support between condenser vaccum pump requires grout | C | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-02-18 | Michael Law
CIV-02 | CIV-02 | PI15481 | Verified | Support 1C-CNM-PD-HGR-0073 anchor bolt not tighten | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-02 | CIV-02 | PI15519 | Verified | Stator Tank - Rungs slick, 30" landing issue, 7" behind rungs and top rung not flush - fabricate new ladder to eliminate OSHA non-compliances | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-24 | Tim Gallegos | 2020-02-24 | Michael Law
CIV-02 | CIV-02 | PI14880 | Verified | Need toe plate in grating around YCFF 1/2" and YCFD 1/2" SS drain lines, STG Bldg mezzanine under Generator | C | S | Tim Gallegos | McD | 2019-12-24 | Tim Gallegos | Comm | 2020-05-12 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-02 | CIV-02 | PI16732 | Verified | Remove angle iron stuck in ground at Condenser Overflow Line No. 6-1C-CNM-0243 above ground flange, West side of Demin Water Tank | C | C | Alan Huntsman | McD | 2020-02-13 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-07-14 | Nelson Eichelberger
CIV-02 | CIV-02 | PI16783 | Verified | 3 inch piping penetration through grating at North side of 1C Gland Seal Steam Condenser needs toe plate | C | S | Tim Gallegos | McD | 2020-02-13 | Tim Gallegos | Comm | 2020-05-04 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-02 | CIV-02 | PI16904 | Verified | Need toe plate around EHC tubing penetrationat 1C-STS-MSV-900A; Main Stop Valve A, STG Bldg. mezzanine | C | C | Tim Gallegos | McD | 2020-02-18 | Tim Gallegos | Comm | 2020-05-12 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-02 | CIV-02 | PI16905 | Verified | Need toe plate around EHC tubing penetrationat 1C-STS-MSV-900B; Main Stop Valve, STG Bldg. mezzanine | C | C | Tim Gallegos | McD | 2020-02-18 | Tim Gallegos | Comm | 2020-05-12 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-01 | CIV-01 | PI15485 | Verified | Control room roof downspouts are not connected to ground drain | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-07-16 | Nelson Eichelberger
CIV-01 | CIV-01 | PI15510 | Verified | Fire Water Tank Lower - Did not Climb - ladder is OSHA compliant - equiped with SAF-T-CLIMB system and compatible harness equipment | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const |  |  | 2020-01-30 | Michael Law
CIV-01 | CIV-01 | PI15511 | Verified | Fire Water Tank Uper - Did not Climb - ladder is OSHA compliant - equiped with SAF-T-CLIMB system and compatible harness equipment | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const |  |  | 2020-01-30 | Michael Law
CIV-01 | CIV-01 | PI15516 | Verified | Raw Water Flocculent Containment - 7' behind 2nd step - move ladder out to create 7” clear requirement to conduit (add’l concrete) | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-15 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-01 | CIV-01 | PI15517 | Verified | Raw Water Flocculent Tank - ladder is OSHA compliant, Client safety requires permanent tie-off to access to top of tank | D | S | Michael Law | McD | 2020-01-08 | Michael Law | Const | 2020-01-29 | Michael Law | 2020-01-29 | Michael Law
CIV-01 | CIV-01 | PI15582 | Verified | Need fencing and placarding around McDermott side of the gas yard, fence needs grounding | C | C | Sheri Fritz | BEA | 2020-01-08 | Sheri Fritz | Comm | 2020-07-16 | Chris Colvin | 2020-07-27 | Dave Goldak
CIV-01 | CIV-01 | PI16404 | Verified | Complete final grading. | C | C | Brooks Baker | McD | 2020-01-28 | Brooks Baker | Const | 2020-07-16 | Brooks Baker | 2020-11-11 | Dave Goldak
CIV-01 | CIV-01 | PI16405 | Verified | Cut off all storm drain lifting lugs flush and seal. | C | C | Alan Huntsman | McD | 2020-01-28 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-07-10 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16406 | Verified | Point & patch concrete storm drain cover A-16. | C | C | Alan Huntsman | McD | 2020-01-28 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-06-08 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16407 | Verified | Attach fencing to pole (southwest corner). | C | C | Sheri Fritz | BEA | 2020-01-28 | Sheri Fritz | Const | 2020-05-21 | Jason Ezell | 2020-07-16 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16408 | Verified | Complete final grading. | C | C | Brooks Baker | McD | 2020-01-28 | Brooks Baker | Const | 2020-04-09 | Michael Law | 2020-04-09 | Michael Law
CIV-01 | CIV-01 | PI16409 | Verified | Clean off all storm drain covers after final grade. | C | C | Brooks Baker | McD | 2020-01-28 | Brooks Baker | Const | 2020-07-16 | Brooks Baker | 2020-11-11 | Dave Goldak
CIV-01 | CIV-01 | PI16410 | Verified | Install silt fencing at all storm drains. | C | C | Alan Huntsman | McD | 2020-01-28 | Alan Huntsman | Const | 2020-03-19 | Johnny Campbell | 2020-07-10 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16420 | Verified | Complete final grading. | C | C | Brooks Baker | McD | 2020-01-28 | Brooks Baker | Const | 2020-04-09 | Michael Law | 2020-04-09 | Michael Law
CIV-01 | CIV-01 | PI16411 | Verified | Remove excess rock from storm drain A-30. | C | C | Brooks Baker | McD | 2020-01-28 | Brooks Baker | Const | 2020-04-01 | Brooks Baker | 2020-07-10 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16412 | Verified | Remove excess rock from storm drain B-10. | C | C | Brooks Baker | McD | 2020-01-28 | Brooks Baker | Const | 2020-04-01 | Brooks Baker | 2020-07-10 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16413 | Verified | Repair hole in perimeter north of filter press / west of gate to fuel gas area gate. | C | C | Tim Gallegos | McD | 2020-01-28 | Tim Gallegos | Const | 2020-05-12 | Tim Gallegos | 2020-07-16 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16414 | Verified | Address silt washing erosion on soil piles on the north hillside (outside fence line). | C | C | Brooks Baker | McD | 2020-01-28 | Brooks Baker | Const | 2020-05-11 | Brooks Baker | 2020-07-14 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16415 | Verified | Remove 16" HDPE pipe northwest area (outside fence line). | C | C | Brooks Baker | McD | 2020-01-28 | Brooks Baker | Const | 2020-04-14 | Brooks Baker | 2020-07-14 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16416 | Verified | Address perimeter berm erosion at the west fence line. | C | C | Brooks Baker | McD | 2020-01-28 | Brooks Baker | Const | 2020-05-01 | Brooks Baker | 2020-07-14 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16730 | Verified | Dig / find DIV-02 - west of OWS at sentiment basin. | C | C | Brooks Baker | McD | 2020-02-13 | Brooks Baker | Const | 2020-06-09 | Brooks Baker | 2020-06-10 | Dave Goldak
CIV-01 | CIV-01 | PI16417 | Verified | Complete fencing at the craft turnstile area. | C | C | Sheri Fritz | BEA | 2020-01-28 | Sheri Fritz | Const | 2020-05-21 | Jason Ezell | 2020-07-16 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16418 | Verified | Address perimeter berm erosion at the north fence line. | C | C | Brooks Baker | McD | 2020-01-28 | Brooks Baker | Const | 2020-05-01 | Brooks Baker | 2020-07-14 | Nelson Eichelberger
CIV-01 | CIV-01 | PI16419 | Verified | Address erosion at fence line east of craft lunch tent. | C | C | Brooks Baker | McD | 2020-01-28 | Brooks Baker | Const | 2020-06-23 | Brooks Baker | 2020-07-14 | Nelson Eichelberger
CIV-02 | CIV-02 | PI17208 | Verified | Point & patch the northeast column on the exterior of the extcitation transformer blast wall. | C | C | Johnny Campbell | McD | 2020-02-25 | Johnny Campbell | Const | 2020-05-21 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17227 | Verified | Condenser chemical feed skid (ammonia) - cold galv underside of east roof beam. | C | C | Alan Huntsman | McD | 2020-02-25 | Alan Huntsman | Const | 2020-03-11 | Alan Huntsman | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17228 | Verified | Condensate pumps - remove unused bolts in side of foundation. | C | C | Alan Huntsman | McD | 2020-02-25 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17209 | Verified | Thyristor building -grout cable tray support. | C | C | Alan Huntsman | McD | 2020-02-25 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-04-15 | Keith Pollock
CIV-02 | CIV-02 | PI17210 | Verified | Thryristor building - point & patch columns and foundation (including ISO phase foundation & remove 4 unused bolts on south column. | C | C | Alan Huntsman | McD | 2020-02-25 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17211 | Verified | Thryristor building - touch up paint needed on the south side. | C | C | Alan Huntsman | McD | 2020-02-25 | Alan Huntsman | Const | 2020-03-16 | Alan Huntsman | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17212 | Verified | Thryristor building - seal cable tray penetration to excitation transformer area for 2 hour fire rating. | C | E | Chris Colvin | McD | 2020-02-25 | Chris Colvin | Const | 2020-03-31 | Matt Gilmore | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17213 | Verified | Thryristor building - stair tread nosing screws are loose / broken. | C | S | Bobby Williams | McD | 2020-02-25 | Bobby Williams | Const |  |  | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17214 | Verified | Thryristor building - west door - repair / replace hardware. Remove wire ties from door push bar when complete. | C | S | Bobby Williams | McD | 2020-02-25 | Bobby Williams | Const | 2020-03-26 | Tim Gallegos | 2021-04-21 | John Watts
CIV-02 | CIV-02 | PI17215 | Verified | Thryristor building - east door - repair / replace hardware. | C | S | Bobby Williams | McD | 2020-02-25 | Bobby Williams | Const | 2020-03-26 | Tim Gallegos | 2021-04-21 | John Watts
CIV-02 | CIV-02 | PI17216 | Verified | Condenser vacuum skid foundation - point & patch holes, etc. | C | C | Alan Huntsman | McD | 2020-02-25 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17217 | Verified | Unplug weep holes on the condenser vacuum pump B skid. | C | C | Alan Huntsman | McD | 2020-02-25 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17218 | Verified | Point & patch STG foundation including stair landings where needed. | C | C | Johnny Campbell | McD | 2020-02-25 | Johnny Campbell | Const | 2020-03-31 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17219 | Verified | Grout conduit support west & north sides of STG building. | C | C | Alan Huntsman | McD | 2020-02-25 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17221 | Verified | Cold galv vertical brace at north side of STG stair landing (ground floor). | C | C | Alan Huntsman | McD | 2020-02-25 | Alan Huntsman | Const | 2020-03-11 | Alan Huntsman | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17222 | Verified | Remove unused ground wire protruding from STG foundation - north side of condenser. | C | E | Chris Colvin | McD | 2020-02-25 | Chris Colvin | Const | 2020-03-31 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17223 | Verified | STG building - north valve access platform ladder J5 does not have 7" clearance from vertical brace. | C | S | Tim Gallegos | McD | 2020-02-25 | Tim Gallegos | Const | 2020-04-16 | Tim Gallegos | 2020-06-10 | Dave Goldak
CIV-02 | CIV-02 | PI17026 | Verified | Need toe plate around grating at Gland Steam Condenser 3" drain line penetration, STG Bldg. mezzanine, adjacent to Gland Steam Condenser | C | C | Tim Gallegos | McD | 2020-02-18 | Tim Gallegos | Comm | 2020-05-04 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-02 | CIV-02 | PI17202 | Verified | Complete site grading. | C | C | Brooks Baker | McD | 2020-02-25 | Brooks Baker | Const | 2020-05-01 | Brooks Baker | 2020-10-06 | Dave Goldak
CIV-02 | CIV-02 | PI17203 | Verified | Point & patch 1C excitation tranformer pedestals. | C | C | Johnny Campbell | McD | 2020-02-25 | Johnny Campbell | Const | 2020-05-21 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17204 | Verified | Red line dwg LK-1C-321-SD-CE-CON-0011-01. | D | C | Michael Law | McD | 2020-02-25 | Michael Law | Const | 2020-05-11 | Michael Law | 2020-06-22 | Dave Goldak
CIV-02 | CIV-02 | PI17205 | Verified | Patch gouge in north side interior of blast wall inside the excitation transformer area. | C | C | Johnny Campbell | McD | 2020-02-25 | Johnny Campbell | Const | 2020-05-21 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17206 | Verified | Patch north side exterior of blast wall of the excitation transformer area at column/pad. | C | C | Johnny Campbell | McD | 2020-02-25 | Johnny Campbell | Const | 2020-03-31 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17207 | Verified | Clean out control joint on the north side exterior of excitation transformer blast wall near the cable tray penetration. | C | C | Brooks Baker | McD | 2020-02-25 | Brooks Baker | Const | 2020-04-01 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17224 | Verified | STG building - north valve access platform missing small section of grating. | C | S | Tim Gallegos | McD | 2020-02-25 | Tim Gallegos | Const | 2020-04-22 | Tim Gallegos | 2020-06-10 | Dave Goldak
CIV-02 | CIV-02 | PI17225 | Verified | Condenser chemical feed skid (ammonia) - extend downspouts to 6" above final grade. | C | C | Tim Gallegos | McD | 2020-02-25 | Tim Gallegos | Const |  |  | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17226 | Verified | Condenser chemical feed skid (ammonia) - point & patch. | C | C | Alan Huntsman | McD | 2020-02-25 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17315 | Verified | Condensate Pump area, remove exposed metal, point & patch around all pipe supports. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17347 | Verified | Steps to Mezz deck rusted at 1st step & bent - Remove -replace tread. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-04-22 | Tim Gallegos | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17348 | Verified | 3rd step @ Column B/6 bent, Top deck nose plate bent also. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-21 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17349 | Verified | Remove all bolts from embed plates on concrete columns @ STG. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-13 | Johnny Campbell | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17350 | Verified | Toe plate @ column C/6 mezz deck needs filler. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17351 | Verified | SE concrete column @ column line C/6 point and patch and remove wood. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-18 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17352 | Verified | Eastside of condenser Mezz deck multiple openings in the grating, needing toe plate and handrail damage. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-21 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17353 | Verified | NE corner of Mezz deck handrail damage between Column L/6-7, and missing toe plate at pipe penetrations. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-21 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17354 | Verified | No toe plate at stairs between columns H/5-6. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-04-09 | Tim Gallegos | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17355 | Verified | Bent toe plate on crossover bridge at the Condenser nothside (Mezz deck). | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-13 | Tim Gallegos | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17356 | Verified | Staighten/ close all toe plate on column line H, repair all hand rail damage (Mezz deck). | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-04-09 | Tim Gallegos | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17357 | Verified | Mezz deck elevation remove all bolts from concrete columns at the embed plates. | C | C | Johnny Campbell | McD | 2020-02-28 | Johnny Campbell | Const | 2020-04-29 | Johnny Campbell | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17364 | Verified | STG Enclosure: Complete caulking on wall, roof, and flashings. | C | S | Bobby Williams | McD | 2020-03-02 | Bobby Williams | Const | 2020-03-17 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17365 | Verified | STG Enclosure: Install EPDM and base sealant around perimeter. | C | C | Johnny Campbell | McD | 2020-03-02 | Johnny Campbell | Const | 2020-04-09 | Michael Law | 2020-04-28 | Mark Williamson
CIV-02 | CIV-02 | PI17366 | Verified | STG Enclosure: Gap between toe plate and concrete is too large, east end of STG. | C | C | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-07-22 | Eric Policarpio | 2020-07-22 | Dave Goldak
CIV-02 | CIV-02 | PI17367 | Verified | STG Enclosure: Anchor bolt schedule indicates double nut on anchor bolts. Toshiba drawings indicate single. Engineering provide disposition. | C | S | Bobby Williams | McD | 2020-03-02 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17368 | Verified | STG Enclosure: Weld square washers at wall panel base plates 3/16" fillet, 3-sides per anchor bolt schedule | C | S | Bobby Williams | McD | 2020-03-02 | Bobby Williams | Const | 2020-03-13 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17369 | Verified | STG Enclosure: Missing bolts at top of wall to roof panel connections (numerous locations) | C | S | Bobby Williams | McD | 2020-03-02 | Bobby Williams | Const | 2020-03-13 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17370 | Verified | STG Enclosure: Missing bolts at top of wall to beam connections (numerous locations) | C | S | Bobby Williams | McD | 2020-03-02 | Bobby Williams | Const | 2020-03-16 | Tim Gallegos | 2020-06-24 | Dave Goldak
CIV-02 | CIV-02 | PI17371 | Verified | STG Enclosure: Install electrical switch plate covers (four locations) | C | E | Chris Colvin | McD | 2020-03-02 | Chris Colvin | Const | 2020-05-20 | Chris Colvin | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17372 | Verified | STG Enclosure: Install EXIT signage per detail (four doors) | C | E | Chris Colvin | McD | 2020-03-02 | Chris Colvin | Const | 2020-03-31 | Chris Colvin | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17373 | Verified | STG Enclosure: Install door closers (Item DCB, four doors) | C | S | Bobby Williams | McD | 2020-03-02 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-06-24 | Dave Goldak
CIV-02 | CIV-02 | PI17374 | Verified | STG Enclosure: Install Wind speed limitation (Item WSS, four locations) | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-06-30 | Tim Gallegos | 2020-07-07 | Dave Goldak
CIV-02 | CIV-02 | PI17375 | Verified | STG Enclosure: Install gutters and downspouts | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-02 | CIV-02 | PI17376 | Verified | STG Enclosure: North east door can't be opened from exterior. Adjust hardware. | C | S | Bobby Williams | McD | 2020-03-02 | Bobby Williams | Const | 2020-03-13 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17377 | Verified | STG Enclosure: South east door will not latch. Cannot check exit device | C | S | Bobby Williams | McD | 2020-03-02 | Bobby Williams | Const | 2020-03-13 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17378 | Verified | STG Enclosure: Northwest door exit device is functional, but it sticks. Minor adjustment necessary. | C | S | Bobby Williams | McD | 2020-03-02 | Bobby Williams | Const | 2020-03-26 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17379 | Verified | STG Enclosure: Remove 2x4s fastened to concrete deck, north side of Generator | C | C | Alan Huntsman | McD | 2020-03-02 | Alan Huntsman | Const | 2020-03-18 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17380 | Verified | STG Enclosure: Turbine deck table top not steel trowel finished per design. | C | C | Johnny Campbell | McD | 2020-03-02 | Johnny Campbell | Const | 2020-03-31 | Johnny Campbell | 2020-04-28 | Mark Williamson
CIV-02 | CIV-02 | PI17381 | Verified | Elevation 544: Extensive point/patch. Interior and exterior. | C | C | Johnny Campbell | McD | 2020-03-02 | Johnny Campbell | Const | 2020-03-31 | Johnny Campbell | 2020-04-28 | Mark Williamson
CIV-02 | CIV-02 | PI17382 | Verified | Elevation 544: Grout Weld receptacle base plate east end | C | C | Alan Huntsman | McD | 2020-03-02 | Alan Huntsman | Const | 2020-03-19 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17383 | Verified | Elevation 544: Grout Weld receptacle base plate west end | C | C | Alan Huntsman | McD | 2020-03-02 | Alan Huntsman | Const | 2020-03-19 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17384 | Verified | Elevation 544: Damaged and incomplete grout, vent pipe support, northwest corner. | C | C | Alan Huntsman | McD | 2020-03-02 | Alan Huntsman | Const | 2020-03-19 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17316 | Verified | NE corner ground floor STG stair missing nose cap on stair- Column L/7. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17317 | Verified | NE corner ground floor STG patch ruff suface on all pipe supports and Drain Tank Area. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17318 | Verified | Air Compressor house pad patch bushed area, and move pipe support (Column E/8). | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-19 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17320 | Verified | Remove all nails, Point and patch at grounding cable NW of Air Compressor. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-19 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17321 | Verified | Point and patch entire NE ground floor area where needed, removing all metal @ Col F/7. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-19 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17322 | Verified | Incomplete Platform East of Condenser-DWG LK-1C-201-PL-CE-STL-0060-01. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17323 | Verified | Lube Oil Containment wall Northside needs patch and point and all interior areas. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-18 | Johnny Campbell | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17326 | Verified | Grating needs adjustment and cut handrail 2 places DWG LK-1C-201-PL-CE-STL-0060-02. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-12 | Tim Gallegos | 2020-07-07 | Dave Goldak
CIV-02 | CIV-02 | PI17328 | Verified | Remove & repair bolt at Air receiver, Point and Patch all instrument supports. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-18 | Johnny Campbell | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17330 | Verified | Curb damage repair & nail removal SE of Condenser | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-18 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17331 | Verified | Point and Patch all required spot on the interior and exterior of Lube Oil containment walls. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-18 | Johnny Campbell | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17332 | Verified | Point & Patch Seal Oil House Pad. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-18 | Johnny Campbell | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17333 | Verified | Incomplete Platform West of Condenser-DWG LK-1C-201-PL-CE-STL-0060-01. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const |  |  | 2020-06-10 | Dave Goldak
CIV-02 | CIV-02 | PI17334 | Verified | Fire Valve House missing hole in threshold plate for door lock. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-21 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17335 | Verified | Fire valve house door handle inoperable. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-15 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-02 | CIV-02 | PI17337 | Verified | Remove isolation barrier at Fire valve house 16" line inside. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-18 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17338 | Verified | Lube Oil Stair south side missing srews & nose plate. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17339 | Verified | Lube Oil stair south side needs grating extended at the swing gate, 1st landing. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17341 | Verified | Lube Oil Pad, Heat Exchanger, Duplex Filter point and patch where needed. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17342 | Verified | Structural Steel in Lube Oil Containment area loose between Column line A/6-7. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17343 | Verified | Clean and Close Lube Oil Containment Area. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-05-19 | Alan Huntsman | 2020-10-06 | Dave Goldak
CIV-02 | CIV-02 | PI17344 | Verified | Lube Oil pump pad bushed area need finishing. | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Const | 2020-03-18 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17345 | Verified | Loose handrail top level of Lube Oil Containment- all around | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-21 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17346 | Verified | Stair nose plate at second landing south stairs STG missing- Elv 521'-10". | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17385 | Verified | Elevation 544: Bent handrail and toe plate along north end (Row H) | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-08 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17386 | Verified | Elevation 544: Cold galv paint weld connections from handrail to bent deck plate, exterior perimeter (northwest). | C | C | Alan Huntsman | McD | 2020-03-02 | Alan Huntsman | Const | 2020-03-11 | Alan Huntsman | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17387 | Verified | Elevation 544: Weld patch piece of galvanized plate at cut-out section of bent plate. Southwest corner of platform. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-21 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17388 | Verified | Elevation 544: Handrail not welded to exterior of deck bent plate, Line 6, Rows L thru H. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-09 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17389 | Verified | Elevation 544: Handrail not welded to exterior of deck bent plate, Row H, Line 5-6. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-09 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17390 | Verified | Elevation 544: Complete pipe penetration through concrete modifications and install toe plate around enlarged openings, northeast corner. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17391 | Verified | Elevation 544: Complete handrail replacement welds (steam blow removals). Cold galv joints. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-06 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17392 | Verified | Elevation 544: Caulk missing from sections of deck control joints. Clean opening and caulk joint. Southwest corner of deck | C | S | Johnny Campbell | McD | 2020-03-02 | Johnny Campbell | Const | 2020-04-08 | Johnny Campbell | 2020-04-28 | Mark Williamson
CIV-02 | CIV-02 | PI17393 | Verified | Elevation 544: Caulk missing from sections of deck control joints. Clean opening and caulk joint. Northeast corner of deck at Hot reheat pipe penetration | C | C | Alan Huntsman | McD | 2020-03-02 | Alan Huntsman | Const | 2020-03-18 | Johnny Campbell | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17394 | Verified | Elevation 544: Two broken fasteners at one checkerplate cover (northeast corner, south of Row J). | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-21 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17395 | Verified | Elevation 544: Checkerplate missing hold-down fasteners at (northeast corner, between Rows J-L). | C | S | Bobby Williams | McD | 2020-03-02 | Bobby Williams | Const | 2020-05-28 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17396 | Verified | Elevation 544: Paint Checkerplate cover edges safety yellow and Live Load stencil. All locations | C | C | Johnny Campbell | McD | 2020-03-02 | Johnny Campbell | Const | 2020-04-01 | Johnny Campbell | 2020-04-24 | Mark Williamson
CIV-02 | CIV-02 | PI17397 | Verified | Elevation 544: Broken weld at HR post/toeplate (near column G-9) | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17398 | Verified | Elevation 544: Cut PVC Pipe sleeves through concrete to grade and remove trip hazard. Multiple locations | C | S | Johnny Campbell | McD | 2020-03-02 | Johnny Campbell | Const | 2020-04-02 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17399 | Verified | Elevation 544: Remove cribbing, trash and broom clean deck, interior and exterior when all craft labor is complete. | C | C | Alan Huntsman | McD | 2020-03-02 | Alan Huntsman | Const | 2020-03-19 | Johnny Campbell | 2020-06-22 | Dave Goldak
CIV-02 | CIV-02 | PI17400 | Verified | Elevation 562-7: Rotate horizontal brace into position, bolt and torque. Approx J/8 | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-08 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17401 | Verified | South Stair Elev 500 thru 510-10: 2nd and 8th stair nosing missing fasteners. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-09 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17402 | Verified | South Stair Elev 532-10 thru 544: 12th stair nosing missing fastener. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-06 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17403 | Verified | South Stair Landing at 521-10 through 523 (Mezz Deck): Replace first damaged/bent stair tread. Ensure riser height is equal for all steps to mezz deck. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-06 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17404 | Verified | South Stair Landing at 532-10: Add toe plate under handrail, both sides | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-21 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17405 | Verified | North Stair: Loose jamb nut at Col G.2 / 3. Northwest column. Tighten and torque. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-09 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-02 | CIV-02 | PI17406 | Verified | North Stair Elev 500 thru 510-10: 9th, 10th, 11th and 13th stair nosing missing fasteners. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-23 | Tim Gallegos | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17407 | Verified | North Stair Elev 510-10 thru 521-10: 6th and 13th stair nosing missing fasteners. Replace protruding fastener on 1st step. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-23 | Tim Gallegos | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17408 | Verified | North Stair Elev 521-10 thru 532-10: 4th stair nosing missing fastener. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-23 | Tim Gallegos | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17409 | Verified | North Stair Elev 532-10 thru 544: 9th stair nosing missing fastener. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-23 | Tim Gallegos | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17410 | Verified | North Stair Platform Elev 521-10: Bent toeplate, northeast corner (J.1/3.9) | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-23 | Tim Gallegos | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17411 | Verified | North Stair Platform Elev 521-10: Missing/add toeplate under stair rail | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17412 | Verified | North Stair Platform Elev 544: Bent toeplate, northeast corner (J.1/3.9) | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-08 | Tim Gallegos | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17413 | Verified | North Stair Platform Elev 544: Cold galv handrail/midrail welds | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17414 | Verified | Stair Elev 544 through 552-10: 13th stair nosing and top landing missing fasteners. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17415 | Verified | Stair Elev 544 through 552-10: Replace cracked stair nosing, 12th step. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17416 | Verified | Elevation 552-10: Install small filler pieces of toe plate, both sides of stairs. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17417 | Verified | Elevation 552-10: Remove #9 wire from Column F8 | C | E | Chris Colvin | McD | 2020-03-02 | Chris Colvin | Const |  |  | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17418 | Verified | Elevation 552-10: Install filler piece of toe plate, Line 8, 10ft south of Row L. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17419 | Verified | Elevation 552-10: Install filler piece of handrail and midrail, Line 8, 10ft south of Row L. Gap between adjoining sections is too large. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17420 | Verified | Elevation 552-10: Missing (QTY=4) L6x4 sections SDS Silencer Support Trunion restraints. Refer to LK-1C-203-PL-CE-STL-0100-02, Detail A | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-29 | Tim Gallegos | 2020-06-02 | Dave Goldak
CIV-02 | CIV-02 | PI17421 | Verified | Elevation 552-10: Patch cut-out sections of Midrail and toeplate behind 1A-HRS-AOV-0086. Use GN-CE-STL-0001-13 Case 4. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-08 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17422 | Verified | Elevation 552-10: Patch/restore handrail return at pipe penetration. Northwest corner of platform north of J/7. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-08 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17423 | Verified | Elevation 552-10: Cold galv handrail and toeplate welds. Northwest corner of platform north of J/7. | C | C | Alan Huntsman | McD | 2020-03-02 | Alan Huntsman | Const | 2020-03-11 | Alan Huntsman | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17424 | Verified | Elevation 552-10: Modify handrail at hot reheat cut-out, west side, Line 7. Use GN-CE-STL-0001-13 Case 5. Add posts either side. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-06 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17425 | Verified | Elevation 552-10: Install banding or additional toeplate as required, several locations on platform. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-08 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17426 | Verified | Elevation 523-10 Mezz Deck: Install supplemental support steel under grating cut-outs for conduit penetrations. Approx Row 8, under panels 1C-NJS-PNL-001 and -002. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-05 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17427 | Verified | Elevation 523-10 Mezz Deck: Install toe plate banding around cut-outs for conduit penetrations. Approx Row 8, under panels 1C-NJS-PNL-001 and -002. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-05 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17428 | Verified | Elevation 523-10 Mezz Deck: Extensive toe plate/banding necessary at penetrations through grating, entire mezz deck | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-21 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-02 | CIV-02 | PI17429 | Verified | Elevation 523-10 Mezz Deck: Install toeplate around gaps on column Line 8, Columns B, C, D, E, and F. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-05 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17430 | Verified | Elevation 523-10 Mezz Deck: Install toeplate around gaps on column Row B, Columns 3 through 8. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-05 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17431 | Verified | Elevation 523-10 Mezz Deck: Missing toe plate under stairs, Line 5, Rows B-C. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-08 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17432 | Verified | Elevation 523-10 Mezz Deck: Install toe plate gap Line 5 at concrete pedestal. Approx 6". West side of condenser | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-08 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17433 | Verified | Elevation 523-10 Mezz Deck: Install toe plate gap between flanges of Col C/5 | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-08 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17434 | Verified | Elevation 523-10 Mezz Deck: Install toe plate gap at approx Line E-5 at concrete pedestal. West side of condenser | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-08 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17435 | Verified | Elevation 523-10 Mezz Deck: Install supplemental support steel under grating cut-outs for pipe penetrations. Approx grid E-5 at concrete pedestal. West of condenser. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-08 | Tim Gallegos | 2020-05-20 | Dave Goldak
CIV-02 | CIV-02 | PI17436 | Verified | Elevation 523-10 Mezz Deck: Install toe plate banding and replacement grating around cut-outs for pipe penetrations. Approx grid E-5 at concrete pedestal. West of condenser. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-05-08 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17437 | Verified | Elev 500: Columns on A-row in lube oil containment: loose jamb nuts at column baseplates (QTY=8). Tighten and torque as necessary. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-23 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17438 | Verified | Elev 500: Cable tray support steel between STG and PDC: Loose jamb nuts at column baseplates (Five columns). Tighten and torque as necessary. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-23 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17439 | Verified | Elev 501-6 Condenser Chemical Feed Shed: Weld square plate washers per Anchor bolt schedule. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-23 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17440 | Verified | Elev 500: Two columns north of condenser between Lines 5 and 6 on row F missing second jamb nut on base plate anchor bolts. 8 missing | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-23 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17441 | Verified | Elev 500: Two columns north of condenser between Lines 5 and 6 on row H missing second jamb nut on base plate anchor bolts. 8 missing | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-23 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17442 | Verified | Elev 500 Column J9: Missing (Q=2) jamb nuts at column anchor bolts. All are loose. Tighten and torque as necessary. | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-23 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17443 | Verified | Elev 500 Column L9: Missing (Q=4) jamb nuts at column anchor bolts | C | S | Tim Gallegos | McD | 2020-03-02 | Tim Gallegos | Const | 2020-04-30 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI17444 | Verified | Condensate Pump Foundation: All 48 jamb nuts missing or loose. Install, tighten/torque as necessary. | C | S | Shane Crowe | McD | 2020-03-02 | Shane Crowe | Const | 2020-04-30 | Tim Gallegos | 2020-05-19 | John Watts
CIV-02 | CIV-02 | PI18520 | Verified | STG Enclosure: Install EPDM and base sealant around perimeter. Toshiba Drawing 185259-101, Section C-C. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-07-07 | Dave Goldak | 2021-04-21 | John Watts
CIV-02 | CIV-02 | PI18521 | Verified | Elevation 544: Paint Checkerplate cover edges safety yellow and Live Load stencil. (northeast corner,between Rows -). LK-1C-203-PL-CE-STL-0100-02. Section 3-3. Notes 3 and 4 | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-15 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-02 | CIV-02 | PI18522 | Verified | Elevation 544: Paint Checkerplate cover edges safety yellow and Live Load stencil. (northeast corner,between Rows H-J). LK-1C-203-PL-CE-STL-0100-02. Section 3-3. Notes 3 and 4 | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-15 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-03 | CIV-03 | PI15380 | Verified | AAF Filter house - Monorail not installed over lube oil module | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-03 | CIV-03 | PI15381 | Verified | AAF Filter House platforms, gate springs not working correctly - Review all the gates | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-29 | Mike Tabbert
CIV-03 | CIV-03 | PI15382 | Verified | AAF Filter House - Remove temporary bracing and install permenant bracing ( MHI Approved temp bracing to stay then no action required) | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-03 | CIV-03 | PI15383 | Verified | AAF Filter House - Install Toe Plate below filter house | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-03 | CIV-03 | PI15384 | Verified | GCB Platform - Install Toe Plate at first landing | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-17 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-03 | CIV-03 | PI15385 | Verified | GCB Platform access - bent toe plate | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-17 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-03 | CIV-03 | PI15386 | Verified | GCB Platform - Install toe plate at 2nd landing | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-17 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-03 | CIV-03 | PI15387 | Verified | GCB Platform - nosing loose at 8th step - tripping hazard | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-17 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-03 | CIV-03 | PI15388 | Verified | GCB Platform - Install toe plate for conduite opening below equipment | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-17 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-03 | CIV-03 | PI15389 | Verified | GCB Platform - Gap at handrail - correct | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-17 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-03 | CIV-03 | PI15390 | Verified | GCB Platform - IPB Crossover platform - install gates | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-03 | CIV-03 | PI15391 | Verified | GCB Platform - IPB Crossover platform - Ladder does not meet 15" clearance criteria | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-17 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-03 | CIV-03 | PI15392 | Verified | GCB Platform - IPB Crossover platform - South Ladder needs cage or provide handrail protection | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-24 | Tim Gallegos | 2020-02-24 | Michael Law
CIV-03 | CIV-03 | PI15393 | Verified | Control package - nosing @ landing | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-03 | CIV-03 | PI15394 | Verified | Control package - Gap at handrail at HVAC unit - extend handrail and add toe Plate | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-19 | Tim Gallegos | 2020-07-16 | Nelson Eichelberger
CIV-03 | CIV-03 | PI15395 | Verified | Control package - four grating clips are required at each panel | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-03 | CIV-03 | PI15396 | Verified | MHI Platform - east - fix grating clips | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-03 | CIV-03 | PI15397 | Verified | MHI Platform - east - Install toe plate at opening below panels | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-03 | CIV-03 | PI15398 | Verified | GCB platform anchor bolt washer plate weld is not complete | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-17 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-03 | CIV-03 | PI15399 | Verified | IPB Support steel - Anchor bolt washer plate weld is not complete | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-17 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-03 | CIV-03 | PI15497 | Verified | GT Gas Module - Stair width OTQ for SCPS acceptance | D | S | Michael Law | McD | 2020-01-08 | Michael Law | Const | 2020-01-29 | Michael Law | 2020-01-29 | Michael Law
CIV-03 | CIV-03 | PI15499 | Verified | GT Gas Module - South End - Toe Plate required | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2020-07-21 | Satyam Gajjar
CIV-03 | CIV-03 | PI15502 | Verified | Inlet Air - correct bent handrail | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-05 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-03 | CIV-03 | PI15538 | Verified | Gas Package E-2nd step is 14, 2nd is 13 1/2 to the platform-revise rungs to align top rung with platform and subsequent evenly spaced rungs | C | S | James Strange | MHI | 2020-01-08 | James Strange | Const | 2020-07-16 | Eric Policarpio | 2020-07-16 | Nelson Eichelberger
CIV-03 | CIV-03 | PI15547 | Verified | W Aux Fan Lower-Gate spring not installed - required inspection | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-03 | CIV-03 | PI15548 | Verified | W Aux Fan Lower-Gate spring not installed - required inspection | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-03 | CIV-03 | PI15549 | Verified | NE Lube Oil-Ladder rung 24" from floor and 7" behind rung-modify brackets to move ladder out, extend to grating & positively attach | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-03-09 | Tim Gallegos | 2020-03-11 | Michael Law
CIV-03 | CIV-03 | PI15550 | Verified | SE Lube Oil-Ladder rung 24" from floor and 7" behind rung-modify brackets to move ladder out, extend to grating & positively attach | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-03-09 | Tim Gallegos | 2020-03-11 | Michael Law
CIV-03 | CIV-03 | PI15551 | Verified | W Lube Oil-Ladder rung 24" from floor and 7" behind rung-modify brackets to move ladder out, extend to grating & positively attach | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-03-09 | Tim Gallegos | 2020-03-11 | Michael Law
CIV-03 | CIV-03 | PI17681 | Verified | Install kick plates around conduit penetrations through grating. | C | S | Tim Gallegos | McD | 2020-03-04 | Tim Gallegos | Comm | 2020-07-14 | Tim Gallegos | 2020-07-14 | Nelson Eichelberger
CIV-03 | CIV-03 | PI17682 | Verified | Install kick plates around instrument tubing penetrations through grating | C | S | Tim Gallegos | McD | 2020-03-04 | Tim Gallegos | Comm | 2020-05-29 | Tim Gallegos | 2020-07-14 | Nelson Eichelberger
CIV-03 | CIV-03 | PI17683 | Verified | Loose grating at NE side of GT A Inlet Air Filter House grating platform, between Anti-Icing piping and Filter House | C | S | Tim Gallegos | McD | 2020-03-04 | Tim Gallegos | Comm | 2020-05-26 | Tim Gallegos | 2020-06-03 | Nelson Eichelberger
CIV-03 | CIV-03 | PI04325 | Verified | 1A SFC/Excitation package north access missing grating | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-09-16 | Tim Gallegos | 2019-12-12 | Michael Law
CIV-03 | CIV-03 | PI04314 | Verified | GT1A East side turbine Mid level external access platform Toe plate pushed out from grating on south end | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-09-10 | Tim Gallegos | 2019-10-04 | Joshua Sturgeon
CIV-03 | CIV-03 | PI04313 | Verified | GT1A Internal turbine access ladders not installed | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-09-04 | Tim Gallegos | 2019-10-04 | Joshua Sturgeon
CIV-03 | CIV-03 | PI04312 | Verified | GT1A East side turbine upper level external access platform grating clips ( span to large between clips) on south end of platform | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-09-04 | Tim Gallegos | 2019-12-12 | Michael Law
CIV-03 | CIV-03 | PI04311 | Verified | GT1A Vent Fan Access West Side access Ladders, grating, and handrails between Fuel Gas platform and vent fan platform not installed | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-10-17 | Tim Gallegos | 2019-12-12 | Joshua Sturgeon
CIV-03 | CIV-03 | PI04310 | Verified | GT1A AIFH Access Support Structure North West side small drop down platform missing grating and handrails | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-12-11 | Tim Gallegos | 2019-12-12 | Joshua Sturgeon
CIV-03 | CIV-03 | PI04309 | Verified | GT1A AIFH Access Support Structure North East side small drop down platform missing grating and handrails | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-12-11 | Tim Gallegos | 2019-12-12 | Joshua Sturgeon
CIV-03 | CIV-03 | PI00664 | Verified | Repair ground wire in the northeast corner of the 1A switchyard. | B | E | Shannon Savoy | McD | 2019-04-23 | Shannon Savoy | Const | 2019-04-30 | Richard Cruz | 2019-05-01 | Neil Simon
CIV-03 | CIV-03 | PI00661 | Verified | Missing all gate hardware at the A switchyard. | B | C | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-17 | Michael Law | 2019-07-17 | Michael Law
CIV-03 | CIV-03 | PI00659 | Verified | Attach grounds to braids not the gates in the switchyards. | B | E | Shannon Savoy | McD | 2019-04-23 | Shannon Savoy | Const | 2019-04-30 | Richard Cruz | 2019-05-01 | Neil Simon
CIV-03 | CIV-03 | PI00656 | Verified | Install all 1A switchyard fence pole caps. | B | C | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-17 | Michael Law | 2019-05-17 | Neil Simon
CIV-03 | CIV-03 | PI17699 | Verified | CTG 1A - Install concrete stair landing at bottom of south stair. | C | C | Alan Huntsman | McD | 2020-03-04 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-03 | CIV-03 | PI17848 | Verified | Unit 1A GT Enclosure Stairs - One of the steps going to the GT Enclosure (Plant East) is damaged. | C | S | Tim Gallegos | McD | 2020-03-16 | Tim Gallegos | Const | 2020-05-11 | Tim Gallegos | 2020-06-04 | Cintrel Spears
CIV-03 | CIV-03 | PI18029 | Verified | Unit 1A BFP Mezz Deck - Grating needs support on Unit 1A Mezz Deck over the boiler feedwater pumps. | C | S | Tim Gallegos | McD | 2020-03-17 | Tim Gallegos | Comm | 2020-05-26 | Tim Gallegos | 2020-07-16 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18074 | Verified | Unit 1A GT Package East Ladder - The distance from the first rung to the ground is 14 inches, and the second rung is 13.5 inches to the platform. Refer to OSHA Regulation: 1910.23 (b)(2) and OSHA 1910.23 Figure D-2 | C | S | James Strange | MHI | 2020-03-18 | James Strange | Comm | 2020-07-16 | Eric Policarpio | 2020-07-16 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18078 | Verified | 1A Inlet Filter House Stairs - The edge of the steps are slick and needs to be non-slip. Refer to OSHA Regulation: 1910.24 | C | C | James Strange | MHI | 2020-03-18 | James Strange | Comm | 2020-06-04 | Ron McMurtry | 2020-07-16 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18080 | Verified | Unit 1A Gas Control Valve Building - There is a narrow staircase to gas control valve building. Refer to OSHA Regulation: 1910.25(c)(4) | C | C | James Strange | MHI | 2020-03-18 | James Strange | Comm | 2021-05-27 | Eric Policarpio | 2021-05-27 | John Watts
CIV-03 | CIV-03 | PI18082 | Verified | Unit 1A Inlet Filter House Handrails - The railing in front of the hoods is severely bent in towards the hoods. | C | C | Tim Gallegos | McD | 2020-03-18 | Tim Gallegos | Comm | 2020-05-11 | Tim Gallegos | 2020-06-04 | Tanner Hillman
CIV-03 | CIV-03 | PI18085 | Verified | 1A GT Auxiliary Package - Water is leaking when it rains into the containment area, where the base of the building meets the floor on the east side, about 2' north and 3-4' south of where the conduit comes into the building. | C | C | Tim Gallegos | McD | 2020-03-18 | Tim Gallegos | Comm | 2020-05-18 | Tim Gallegos | 2020-07-29 | John Watts
CIV-03 | CIV-03 | PI18088 | Verified | 1A GT Control Package Handrails - These handrails are made differently than all of the rest of the handrails in the plant. Instead of the handrail supports being offset so your hands can run freely down the handrails, the supports are mounted directly to the side of the handrails cause your hands to be stopped at each support. Refer to OSHA Regulation: 1910.29(f)(2) | D | S | James Strange | MHI | 2020-03-18 | James Strange | Comm | 2021-07-06 | Eric Policarpio | 2021-07-06 | John Watts
CIV-03 | CIV-03 | PI18091 | Verified | 1A GT Control Package has a leak in the battery room coming from the ceiling that is dripping on top of one of the batteries. | C | E | James Strange | MHI | 2020-03-18 | James Strange | Comm | 2020-04-28 | Michael Law | 2020-04-29 | Keith Pollock
CIV-03 | CIV-03 | PI18215 | Verified | CTG 1A GSU Transformer South End area: Housekeeping, Debris, & Scaffolding | C | C | Johnny Campbell | McD | 2020-04-17 | Johnny Campbell | Const | 2020-04-29 | Johnny Campbell | 2020-07-28 | Keith Pollock
CIV-03 | CIV-03 | PI18216 | Verified | CTG 1A GSU Transformer Bleed Air Temp Return area: Incomplete Support Installation -- not grouted | C | E | Johnny Campbell | McD | 2020-04-17 | Johnny Campbell | Const | 2020-04-29 | Johnny Campbell | 2021-02-24 | John Watts
CIV-03 | CIV-03 | PI18241 | Verified | Clean and touch-up paint -- Unit 1A-FXC/SFC package (west outside wall) | C | C | Tim Gallegos | McD | 2020-04-30 | Tim Gallegos | Const | 2020-08-06 | Tim Gallegos | 2020-08-14 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18242 | Verified | Replace multiple missing wall panel screws -- Unit 1A-FXC/SFC package (west outside wall) | C | C | Tim Gallegos | McD | 2020-04-30 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-06-03 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18243 | Verified | Clean carbon contamination from HVAC case, U1-A HVAC unit - west wall, EXC-SFC package | C | C | Tim Gallegos | McD | 2020-04-30 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-08-14 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18244 | Verified | Clean up floor - remove duct seal (U1A-EXC-SFC package) | C | C | Johnny Campbell | McD | 2020-04-30 | Johnny Campbell | Const | 2020-05-07 | Johnny Campbell | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18245 | Verified | Clean up top of HVAC Case U1A-EXC/SFC Package (West wall HVAC unit) | C | C | Johnny Campbell | McD | 2020-04-30 | Johnny Campbell | Const | 2020-05-07 | Johnny Campbell | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18246 | Verified | Fall Hazard; Extend barrier around and behind ladder for crossover platform (U1A-GCB) | C | C | Tim Gallegos | McD | 2020-04-30 | Tim Gallegos | Const | 2020-06-30 | Mike Tabbert | 2020-07-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18247 | Verified | Need chain safety bottle rack installed.(UIA-GCB SF6 bottle storage area) | C | C | Tim Gallegos | McD | 2020-04-30 | Tim Gallegos | Const |  |  | 2020-06-03 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18248 | Verified | Remove trash, debris, wire, rope, & unused material from U1A-GCB East side access platform | C | C | Johnny Campbell | McD | 2020-04-30 | Johnny Campbell | Const | 2020-05-05 | Johnny Campbell | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18249 | Verified | Clean up rust, touch-up paint 1A-GCB enclosure | C | C | Johnny Campbell | McD | 2020-04-30 | Johnny Campbell | Const | 2020-05-14 | Johnny Campbell | 2020-07-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18250 | Verified | Clean off roof of UIA-CTG Turning Gear enclosure | C | C | Johnny Campbell | McD | 2020-04-30 | Johnny Campbell | Const | 2020-07-16 | Eric Policarpio | 2020-07-16 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18251 | Verified | Complete cleanout and cover installation on U1A cable tray at GCB | C | E | Chris Colvin | McD | 2020-04-30 | Chris Colvin | Const | 2020-08-06 | Chris Colvin | 2020-08-14 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18252 | Verified | 1A-CTG-Gen platform access to CT enclosure, missing nose-ing. East side of generator | C | C | James Strange | MHI | 2020-04-30 | James Strange | Const |  |  | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18253 | Verified | 1A-CTG-Gen platform access to CT enclosure, missing nose-ing on platform Wast side of generator | C | C | James Strange | MHI | 2020-04-30 | James Strange | Const | 2020-06-08 | Nelson Eichelberger | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18254 | Verified | 1A-CTG-GEN West side maintenance hoist. Replace rusted & corroded raise /lower (secondary) chain. Provide draining chain box for load chain. | C | C | Tim Gallegos | McD | 2020-04-30 | Tim Gallegos | Const | 2020-06-30 | Tim Gallegos | 2020-07-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18255 | Verified | Install stair tower anchor bolts at clips on bottom of stair (group basis) 1A-CTG-AIR inlet filter | C | C | Tim Gallegos | McD | 2020-04-30 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18256 | Verified | 1A-CTG-AIR inlet filter Stair Tower. Missing anti-slip stair and landing nose-ing | C | C | James Strange | MHI | 2020-04-30 | James Strange | Const | 2020-05-04 | Tim Gallegos | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18257 | Verified | U1A-CTG Air Inlet Filter House deck -- need trash & debris removed (tie wraps, tape, nails, wire, broken, sheet metal pieces | C | C | Johnny Campbell | McD | 2020-04-30 | Johnny Campbell | Const | 2020-07-16 | Brooks Baker | 2020-07-16 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18258 | Verified | U1A-CTG Air Inlet Filter House deck -- remove choker from under grating at West side on north end of main platform under grating under duct. | C | C | Tim Gallegos | McD | 2020-04-30 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2020-07-28 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18265 | Verified | Loose grating panels U1A Air Inlet Filter House deck, various places, east side - Many grating panels found loose, grating clips/clamps need to be tightened or additional clamps added. Location on east side of platform | C | S | Tim Gallegos | McD | 2020-05-13 | Tim Gallegos | Const | 2020-05-27 | Tim Gallegos | 2020-06-03 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18266 | Verified | Loose grating panels U1A Air Inlet Filter House deck, various places, west side - Many grating panels found loose, grating clips/clamps need to be tightened or additional clamps added. Location on west side of platform | C | S | Tim Gallegos | McD | 2020-05-13 | Tim Gallegos | Const | 2020-05-27 | Tim Gallegos | 2020-06-03 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18267 | Verified | Clean beam pocket, U1A Air Inlet Filter House in front of level 1 north door - Dirt, trash, and debris accumulated in pocket below level 1 north door. Location west side stair tower level 1 | C | C | Johnny Campbell | McD | 2020-05-13 | Johnny Campbell | Const | 2020-05-18 | Johnny Campbell | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18268 | Verified | Loose grating, U1A Air Inlet Filter House, doorway access level 1 platform - Loose grating doorway access level 1 platform and stair tower landing | C | S | Tim Gallegos | McD | 2020-05-13 | Tim Gallegos | Const | 2020-05-27 | Tim Gallegos | 2020-06-03 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18269 | Verified | Clean beam pocket, U1A Air Inlet Filter House in front of level 2 north door - Trash, debris and water accumulated in pocket below level 2 north door. Location west side stair tower level 2 | C | C | Johnny Campbell | McD | 2020-05-13 | Johnny Campbell | Const | 2020-05-18 | Johnny Campbell | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18270 | Verified | Uneven grating U1A Air Inlet Filter House stair tower level 3 - Grating uneven, loose, missing slip resistant nose-ing. Potential trip hazard at level 3 landing | C | S | James Strange | MHI | 2020-05-13 | James Strange | Const | 2020-06-04 | Ron McMurtry | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18271 | Verified | Clean out beam pocket U1A Air Inlet Filter House in front of north door level 3 platform - Dirt, trash, and debris accumulated in pocket in front of level 3 north door. Location west side stair tower level 3 | C | C | Johnny Campbell | McD | 2020-05-13 | Johnny Campbell | Const | 2020-05-18 | Johnny Campbell | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18272 | Verified | Clean out beam pocket U1A Air Inlet Filter House in front of north door level 4 platform - Dirt, trash, debris, and water accumulated in beam pocket in front of level 4 north door. Location west side stair tower level 4 | C | C | Johnny Campbell | McD | 2020-05-13 | Johnny Campbell | Const | 2020-05-18 | Johnny Campbell | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18273 | Verified | Uneven grating U1A Fuel Gas/Purge Air access platform west side of skid, top of first flight of stairs - Uneven, loose grating U1A Fuel Gas/Purge Air unit access platform on west side. | C | S | Tim Gallegos | McD | 2020-05-13 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18274 | Verified | Loose grating clips U1A Fuel Gas/Purge Air access platform west side of skid - Loose grating on U1A Fuel Gas/Purge Air unit access west side platform. Grating clamps loose. | C | S | Tim Gallegos | McD | 2020-05-13 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18275 | Verified | Damage stair tread U1A Fuel Gas/Purge Air unit west side access to GT Enclosure - Bent, damaged stair tread Fuel Gas/Purge Air Unit access to GT west side upper doors. Potential trip hazard, uneven step | C | S | Tim Gallegos | McD | 2020-05-13 | Tim Gallegos | Const | 2020-06-17 | Tim Gallegos | 2020-07-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18276 | Verified | Loose grating, grating clips, U1A Fuel Gas/Purge Air and GT west side doors access upper platform - Loose grating, loose grating clips on U1A GT upper access platform in multiple places | C | S | Tim Gallegos | McD | 2020-05-13 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-07-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18277 | Verified | Missing handrail gate return spring U1A Fuel Gas/Purge Air Unit, GT upper access platform - Handrail gate missing return spring, Fuel Gas/Purge Air unit access platform. Fall hazard. | C | S | James Strange | MHI | 2020-05-13 | James Strange | Const | 2020-07-28 | Eric Policarpio | 2020-07-28 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18278 | Verified | Broken bolt head U1A Fuel Gas/Purge Air unit roof access cover - Broken bolt head on Fuel Gas/Purge Air unit access cover. Potential leak hazard, potential fire hazard | C | S | Tim Gallegos | McD | 2020-05-13 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-07-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18279 | Verified | Loose grating, grating clamps, U1A Fuel Gas /Purge Air unit east side middle access platform - Loose grating and grating clamps. Potential trip hazard, unstable footing on grating. | C | S | Tim Gallegos | McD | 2020-05-13 | Tim Gallegos | Const | 2020-05-29 | Tim Gallegos | 2020-07-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18280 | Verified | Missing handrail gate return spring, U1A lower GT Casing Cooling Air control valve access platform - Missing handrail gate return spring, U1A lower ladder platform above Fuel Gas/ Purge Air unit to access ladder platforms to GT Casing Cooling Air control valves. Fall hazard. | C | S | James Strange | MHI | 2020-05-13 | James Strange | Const | 2020-06-08 | Ron McMurtry | 2020-07-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18281 | Verified | Missing handrail gate return spring, U1A middle GT Casing Cooling Air control valve access platform - Missing handrail gate return spring, U1A middle ladder platform above Fuel Gas/ Purge Air unit to access ladder platform for GT Casing Cooling Air control valves. Fall hazard. | C | S | James Strange | MHI | 2020-05-13 | James Strange | Const | 2020-06-08 | Ron McMurtry | 2020-07-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18282 | Verified | Missing handrail gate return spring, U1A upper GT Casing Cooling Air control valve access platform - Missing handrail gate return spring, U1A upper ladder platform above Fuel Gas/ Purge Air unit at GT Casing Cooling Air control valves. Fall hazard. | C | S | James Strange | MHI | 2020-05-13 | James Strange | Const | 2020-06-08 | Ron McMurtry | 2020-07-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18283 | Verified | Bent grating U1A platform at GT Casing Cooling Air control valves - Damaged, bent grating bars. Locally weakened platform. Potential trip hazard. | C | S | Tim Gallegos | McD | 2020-05-13 | Tim Gallegos | Const | 2020-06-18 | Tim Gallegos | 2020-07-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18284 | Verified | Loose grating clamps, U1A GT Enclosure Ventilation Fan platform - Loose grating clamps. Potential trip hazard. | C | S | Tim Gallegos | McD | 2020-05-13 | Tim Gallegos | Const | 2020-05-29 | Tim Gallegos | 2020-06-03 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18285 | Verified | Multiple loose bolts U1A GT Enclosure Ventilation Fan inlet duct at expansion joint flange - Fan B - Flange joint bolts tightened to limit of bolt threads, incorrect bolt length (or lack of combination flat washer and lock washer) leaves bolt loose and can be turned by hand | C | S | Shane Crowe | McD | 2020-05-13 | Shane Crowe | Const | 2020-05-26 | Shane Crowe | 2020-06-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18286 | Verified | Instrument tubing support obstructs walkway U1A GT Enclosure Ventilation Fan Access platform - Tubing tray support post set in walkway. Post needs relocated out of walk path, and tray support bracing re-arranged. | C | I | Tim Green | McD | 2020-05-13 | Tim Green | Const | 2020-08-06 | Tim Green | 2020-08-14 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18287 | Verified | Missing handrail gate return spring U1A GT Enclosure Gas Analyzer access platform east side of enclosure - Missing handrail gate return spring, U1A ladder platform for GT Enclosure gas analyzers, east side of enclosure. Fall hazard. | C | S | James Strange | MHI | 2020-05-13 | James Strange | Const | 2020-06-08 | Ron McMurtry | 2020-07-08 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18288 | Verified | Broken door latch U1A GT Enclosure Gas Analyzer cabinet, east side of GT enclosure - Instrument cabinet door latch broken, assembly screw may have been broken off internal to knob. Potential for instrument damage. | C | E | Mike Tabbert | McD | 2020-05-13 | Mike Tabbert | Const | 2020-07-20 | Mike Tabbert | 2020-07-28 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18289 | Verified | Missing handrail gate return spring U1A GT Enclosure east side ladder platform access to Gas Analyzers and Ventilation Fans - Missing handrail gate return spring, U1A GT Enclosure east side middle ladder platform for GT Enclosure Gas Analyzers and Ventilation Fans. Fall hazard. | C | S | James Strange | MHI | 2020-05-13 | James Strange | Const | 2020-06-08 | Ron McMurtry | 2020-07-14 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18290 | Verified | Loose grating clamps, U1A GT Enclosure east side doorway access platform | C | S | Tim Gallegos | McD | 2020-05-13 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2020-07-28 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18291 | Verified | Carbon contamination U1A GT Instrumentation junction boxes, east side GT Enclosure access platform - Carbon contamination on stainless steel junction boxes - top, sides and front. U1A GT Enclosure access platform. | C | C | Johnny Campbell | McD | 2020-05-13 | Johnny Campbell | Const | 2020-05-19 | Johnny Campbell | 2020-07-28 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18305 | Verified | GT west, elev 509-6: Install toe plate under fire extinguisher at top of stairs. | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-03-19 | Eric Policarpio | 2021-03-19 | John Watts
CIV-03 | CIV-03 | PI18306 | Verified | GT west, elev 509-6: Adjust grating panel at top of stairs from ground level. Uneven nosing at top of steps. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-02 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-03 | CIV-03 | PI18307 | Verified | GT west, elev 509-6: Install toe plate under ladder at Fuel Gas supply piping | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-03-19 | Eric Policarpio | 2021-03-19 | John Watts
CIV-03 | CIV-03 | PI18308 | Verified | GT west, elev 509-6: Install toe plate under electrical term box 1AMBY92GH031 | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-03-19 | Eric Policarpio | 2021-03-19 | John Watts
CIV-03 | CIV-03 | PI18309 | Verified | Install safety Gate closing springs at platforms leading to exhaust fans (3 locations east side, 3 locations west side) | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2020-06-08 | Ron McMurtry | 2020-06-16 | Dave Goldak
CIV-03 | CIV-03 | PI18310 | Verified | GT east, elev 507-10: Three loose grating clips at first stair platform landing. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-02 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-03 | CIV-03 | PI18311 | Verified | GT filter house, west Jacking point platform: Extend toe plate, two locations on east side of platform, one location under ladder on south end of platform. | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-03-19 | Eric Policarpio | 2021-03-19 | John Watts
CIV-03 | CIV-03 | PI18312 | Verified | GT filter house, east Jacking point platform: Extend toe plate, two locations on west side of platform, one location under ladder on south end of platform. | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-03-19 | Eric Policarpio | 2021-03-19 | John Watts
CIV-03 | CIV-03 | PI18313 | Verified | GT filter house: Extend toe plate under ladder to DP instrument control panel platform (west side). | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-03-19 | Eric Policarpio | 2021-03-19 | John Watts
CIV-03 | CIV-03 | PI18314 | Verified | GT filter house: Install safety gate closing spring on ladder to DP instrument control panel platform (west side). | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2020-06-08 | Ron McMurtry | 2020-06-16 | Dave Goldak
CIV-03 | CIV-03 | PI18315 | Verified | GT filter house: Numerous loose/missing grating clips throughout platform | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-11 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-03 | CIV-03 | PI18316 | Verified | GT filter house: Extend toe plate around perimeter of open hole in grating underneath air inlet/filters (3 sides) | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-03-19 | Eric Policarpio | 2021-03-19 | John Watts
CIV-03 | CIV-03 | PI18317 | Verified | GT filter house: Install safety gate closing spring on ladder to east jacking platform | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2020-06-08 | Ron McMurtry | 2020-06-16 | Dave Goldak
CIV-03 | CIV-03 | PI18318 | Verified | GT filter house: Install safety gate closing spring on ladder to east duct manway access. | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2020-06-08 | Ron McMurtry | 2020-06-16 | Dave Goldak
CIV-03 | CIV-03 | PI18319 | Verified | GT filter house: Extend handrail to duct plate on north end of east manway access platform. | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-03-19 | Eric Policarpio | 2021-03-19 | John Watts
CIV-03 | CIV-03 | PI18320 | Verified | GT filter house: Complete handrail/midrail repair at cutout for pipe conflict - northeast side of platform. Detail Case 6, LK-10-000-GN-STL-0001-13 | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-23 | Tim Gallegos | 2020-06-24 | Dave Goldak
CIV-03 | CIV-03 | PI18321 | Verified | GT South stair to tabletop: Missing hillside washers on stringer channel, east and west handrail attachments from Elev 500 ground to table top (Four handrails). | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-16 | Tim Gallegos | 2020-06-24 | Dave Goldak
CIV-03 | CIV-03 | PI18322 | Verified | GT South stair to tabletop elev 506-8: Extend grating to edge of landing platform support steel , west side at A/C access platform. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-17 | Tim Gallegos | 2020-06-24 | Dave Goldak
CIV-03 | CIV-03 | PI18323 | Verified | GT South stair to tabletop elev 506-8: Install toe plate on east edge of platform | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-18 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-03 | CIV-03 | PI18324 | Verified | GT South access platform (elev 512-11): Reinstall two loose grating clips on south end of table top. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-18 | Tim Gallegos | 2020-07-16 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18325 | Verified | SFC HVAC Access platform : Install abrasive nosing on edge of grating at entrance from stairway. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-18 | Tim Gallegos | 2020-06-24 | Dave Goldak
CIV-03 | CIV-03 | PI18326 | Verified | North Excitation access platform: Adjust springs to allo safety gate to close automatically at top of ladder. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-11 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-03 | CIV-03 | PI18327 | Verified | North Excitation access platform: Extend grating at top of ladder to edge of support channel. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-16 | Tim Gallegos | 2020-06-24 | Dave Goldak
CIV-03 | CIV-03 | PI18328 | Verified | West Excitation access platform: Extend midrail and close gap on northwest corner of platform. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-23 | Tim Gallegos | 2020-07-16 | Nelson Eichelberger
CIV-03 | CIV-03 | PI18329 | Verified | Circuit Breaker Platform: Install toeplate around open hole in floor under GCB (3-sides). | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-30 | Mike Tabbert | 2020-07-07 | Dave Goldak
CIV-03 | CIV-03 | PI18330 | Verified | Elev 500: Grout electrical unistrut support base, west of 1A-CTS-XFM-001 | C | C | Johnny Campbell | McD | 2020-05-26 | Johnny Campbell | Comm | 2020-05-28 | Brooks Baker | 2020-06-03 | Dave Goldak
CIV-03 | CIV-03 | PI18331 | Verified | Elev 500: Install lid or grating on open/unused drain hubs. One northwest of CTG, one at column XB/X2 | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-11 | Jason Ezell | 2020-07-16 | Nelson Eichelberger
CIV-04 | CIV-04 | PI00655 | Verified | Ground clamps on the west gate of the 1B switchyard are too big. | B | E | Luis Cantu | McD | 2019-04-23 | Luis Cantu | Const | 2019-07-17 | Michael Law | 2019-07-26 | Blake Boudreaux
CIV-04 | CIV-04 | PI00657 | Verified | Install all 1B switchyard fence pole caps. | B | C | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-17 | Michael Law | 2019-05-17 | Neil Simon
CIV-04 | CIV-04 | PI00658 | Verified | Ground wire on the 1B switchyard man gate needs to be buried (trip hazard). | B | E | Shannon Savoy | McD | 2019-04-23 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-01 | Neil Simon
CIV-04 | CIV-04 | PI00660 | Verified | Attach grounds to braids not the gates in the switchyards. | B | E | Shannon Savoy | McD | 2019-04-23 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-01 | Neil Simon
CIV-04 | CIV-04 | PI00662 | Verified | Missing all gate hardware at the 1B switchyard. | B | C | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-01 | Neil Simon | 2019-05-01 | Neil Simon
CIV-04 | CIV-04 | PI00663 | Verified | Need clamp on top row of barbed wire on the west gate of the 1B switchyard. | B | C | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-17 | Michael Law | 2019-05-17 | Neil Simon
CIV-04 | CIV-04 | PI00507 | Verified | Secure Excitation Transformer to embeds. | A | E | Dustin Futrell | McD | 2019-04-05 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-11-19 | Michael Law
CIV-04 | CIV-04 | PI04315 | Verified | GT1B AIFH Access Support Structure North East side small drop down platform missing grating and handrails | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-12-11 | Tim Gallegos | 2019-12-12 | Joshua Sturgeon
CIV-04 | CIV-04 | PI04316 | Verified | GT1B AIFH Access Support Structure North West side small drop down platform missing handrails | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-12-11 | Tim Gallegos | 2019-12-12 | Joshua Sturgeon
CIV-04 | CIV-04 | PI04317 | Verified | GT1B AIFH Stair tower all landings grating and toe plate not installed | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-12-11 | Tim Gallegos | 2019-12-12 | Joshua Sturgeon
CIV-04 | CIV-04 | PI04318 | Verified | GT1B AIFH Access Tower upper two landings grating and toe plate missing | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-09-16 | Tim Gallegos | 2019-10-04 | Joshua Sturgeon
CIV-04 | CIV-04 | PI04319 | Verified | GT1B East side turbine Mid level external access platform Toe plate pushed out from grating on south end | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-09-10 | Tim Gallegos | 2019-10-04 | Joshua Sturgeon
CIV-04 | CIV-04 | PI04320 | Verified | GT1B East side turbine upper level external access platform grating clips missing south east grating piece | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-09-04 | Tim Gallegos | 2019-10-04 | Joshua Sturgeon
CIV-04 | CIV-04 | PI04321 | Verified | GT1B East and West Generator to turbine steps, platforms, grating, and handrails not installed | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2020-01-06 | Tim Gallegos | 2020-01-09 | Kelvin Cook
CIV-04 | CIV-04 | PI04322 | Verified | GT1B East side turbine upper level external access platform Brace BRA/3 bolt loose on lower connection to colum south east corner of platform | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-09-04 | Tim Gallegos | 2019-10-04 | Joshua Sturgeon
CIV-04 | CIV-04 | PI04323 | Verified | GT1B Internall turbine access ladders not installed | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-09-04 | Tim Gallegos | 2019-10-04 | Joshua Sturgeon
CIV-04 | CIV-04 | PI04324 | Verified | GT1B Fuel Gas access platform west side grating is sprung tighten grating clips | B | S | Bobby Williams | McD | 2019-08-19 | Bobby Williams | Const | 2019-09-04 | Tim Gallegos | 2019-10-04 | Joshua Sturgeon
CIV-04 | CIV-04 | PI15403 | Verified | AAF Filter house - Monorail not installed over lube oil module | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-04 | CIV-04 | PI15404 | Verified | AAF Filter House platforms, gate springs not working correctly - Review all the gates | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-04 | CIV-04 | PI15405 | Verified | AAF Filter House - Remove temporary bracing and install permenant bracing ( MHI Approved temp bracing to stay then no action required) | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-04 | CIV-04 | PI15406 | Verified | AAF Filter House - Install Toe Plate below filter house | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-04 | CIV-04 | PI15407 | Verified | GCB Platform - Install Toe Plate at first landing | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-13 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-04 | CIV-04 | PI15408 | Verified | GCB Platform access - nosing at landing 1 & 2 | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-13 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-04 | CIV-04 | PI15409 | Verified | GCB Platform - Install toe plate at 2nd landing | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-13 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-04 | CIV-04 | PI15410 | Verified | GCB Platform -Grating clips at landing 2 | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-13 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-04 | CIV-04 | PI15411 | Verified | GCB Platform - Gap at handrail - correct | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-13 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-04 | CIV-04 | PI15412 | Verified | GCB Platform - IPB Crossover platform - install gates | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-15 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-04 | CIV-04 | PI15413 | Verified | GCB Platform - IPB Crossover platform - Ladder does not meet 15" clearance criteria | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-02 | Tim Gallegos | 2020-02-03 | Michael Law
CIV-04 | CIV-04 | PI15414 | Verified | GCB Platform - IPB Crossover platform - South Ladder needs cage or provide handrail protection | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-13 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-04 | CIV-04 | PI15415 | Verified | Control package - abrasive nosing @ landing - both stairs | C | S | James Strange | MHI | 2020-01-08 | James Strange | Const | 2020-06-08 | Ron McMurtry | 2020-07-21 | Satyam Gajjar
CIV-04 | CIV-04 | PI15416 | Verified | Control package - Gap at handrail at HVAC unit - extend handrail and add toe Plate | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-21 | Tim Gallegos | 2020-07-21 | Satyam Gajjar
CIV-04 | CIV-04 | PI15417 | Verified | Control package - four grating clips are required at each panel | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-04 | CIV-04 | PI15418 | Verified | MHI Platform - east - fix grating clips, Install missing grating clips | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-04 | CIV-04 | PI15419 | Verified | MHI Platform - east - Install toe plate at opening below panels | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-04 | CIV-04 | PI15420 | Verified | MHI Platform - east - Safety gate springs not installed | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-04 | CIV-04 | PI15421 | Verified | GCB platform anchor bolt washer plate weld is not complete | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-13 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-04 | CIV-04 | PI15422 | Verified | IPB Support steel - Anchor bolt washer plate weld is not complete | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-13 | Tim Gallegos | 2020-02-18 | Michael Law
CIV-04 | CIV-04 | PI15423 | Verified | Lube oil pipe support - tighten anchor bolts | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-04 | CIV-04 | PI15424 | Verified | Pipe support base plate has gap - grout base plate under pipe support - near GT package | D | S | Michael Law | McD | 2020-01-08 | Michael Law | Const | 2020-01-29 | Michael Law | 2020-01-29 | Michael Law
CIV-04 | CIV-04 | PI15498 | Verified | GT Gas Module - Stair width OTQ for SCPS acceptance | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const |  |  | 2020-01-30 | Michael Law
CIV-04 | CIV-04 | PI15500 | Verified | GT Gas Module - South End - Toe Plate required | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-19 | Tim Gallegos | 2020-07-21 | Satyam Gajjar
CIV-04 | CIV-04 | PI15520 | Verified | N- Gas Package - 1st Rung 14" 2nd -13" - revise rungs to align top rung with platform and subsequent evely spaced rungs - Safety gate spring not installed | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2021-04-21 | John Watts
CIV-04 | CIV-04 | PI15527 | Verified | NE- Lube Oil - 24" to first rung and 7" behind rung - modify brackets to move ladder out, extend to grating & positively attach | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-28 | Tim Gallegos | 2020-03-03 | Michael Law
CIV-04 | CIV-04 | PI15528 | Verified | SE -Lube Oil - 24" to first rung and 7" behind rung - modify brackets to move ladder out, extend to grating & positively attach | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-28 | Tim Gallegos | 2020-03-03 | Michael Law
CIV-04 | CIV-04 | PI15529 | Verified | W- Lube Oil - 24" to first rung and 7" behind rung - modify brackets to move ladder out, extend to grating & positively attach | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-28 | Tim Gallegos | 2020-03-03 | Michael Law
CIV-04 | CIV-04 | PI16815 | Verified | Install Support steel for Excitation Building HVAC. | C | S | Bobby Williams | McD | 2020-02-14 | Bobby Williams | Const | 2020-03-09 | Tim Gallegos | 2020-03-31 | Dave Goldak
CIV-04 | CIV-04 | PI16869 | Verified | Vertical i-beam is not welded to Control Oil horizontal angle iron support at Southwest corner of B GT Control Oil skid | B | S | Bobby Williams | McD | 2020-02-18 | Bobby Williams | Comm | 2020-04-03 | Tim Gallegos | 2020-04-07 | Bernard Stasse
CIV-04 | CIV-04 | PI17700 | Verified | CTG 1B - Install concrete stair landing at bottom of south stair. | C | C | Alan Huntsman | McD | 2020-03-04 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-04 | CIV-04 | PI18071 | Verified | Unit 1B GT Package North Ladder - The distance from the first rung to the ground is 14.75 inches. Refer to OSHA Regulation: 1910.23 (b)(2) and OSHA 1910.23 Figure D-2 | C | S | Tim Gallegos | McD | 2020-03-18 | Tim Gallegos | Comm | 2020-08-05 | Tim Gallegos | 2021-04-21 | John Watts
CIV-04 | CIV-04 | PI18072 | Verified | Unit 1B East Mid-Level to Manway Ladder - The distance between the centerline rung and the platform is 12.5 inches. Refer to OSHA Regulation: 1910.23 (d)(12)(i) | C | S | Tim Gallegos | McD | 2020-03-18 | Tim Gallegos | Comm | 2020-05-21 | Tim Gallegos | 2021-01-25 | Dave Goldak
CIV-04 | CIV-04 | PI18079 | Verified | 1B Inlet Filter House Stairs - The edge of the steps are slick and needs to be non-slip. Refer to OSHA Regulation: 1910.24 | C | C | James Strange | MHI | 2020-03-18 | James Strange | Comm | 2020-06-04 | Ron McMurtry | 2020-07-27 | Dave Goldak
CIV-04 | CIV-04 | PI18081 | Verified | Unit 1B Gas Control Valve Building - There is a narrow staircase to gas control valve building. Refer to OSHA Regulation: 1910.25(c)(4) | C | C | James Strange | MHI | 2020-03-18 | James Strange | Comm | 2021-04-21 | Eric Policarpio | 2021-04-21 | John Watts
CIV-04 | CIV-04 | PI18083 | Verified | Unit 1B Inlet Filter House Handrails - The railing in front of the hoods is severely bent in towards the hoods. | C | C | Tim Gallegos | McD | 2020-03-18 | Tim Gallegos | Comm | 2020-05-11 | Tim Gallegos | 2020-06-04 | Tanner Hillman
CIV-04 | CIV-04 | PI18089 | Verified | 1B GT Control Package Handrails - These handrails are made differently than all of the rest of the handrails in the plant. Instead of the handrail supports being offset so your hands can run freely down the handrails, the supports are mounted directly to the side of the handrails cause your hands to be stopped at each support. Refer to OSHA Regulation: 1910.29(f)(2) | D | S | James Strange | MHI | 2020-03-18 | James Strange | Comm | 2021-06-17 | Eric Policarpio | 2021-06-17 | John Watts
CIV-04 | CIV-04 | PI18332 | Verified | GT west, elev 509-6: Install toe plate under fire extinguisher at top of stairs. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-05-28 | Tim Gallegos | 2020-06-02 | Dave Goldak
CIV-04 | CIV-04 | PI18333 | Verified | GT west, elev 509-6: Install toe plate under ladder at Fuel Gas supply piping | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-05-28 | Tim Gallegos | 2020-06-02 | Dave Goldak
CIV-04 | CIV-04 | PI18334 | Verified | GT west, elev 509-6: Install toe plate under electrical term box 1BMBY92GH031 | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-05-28 | Tim Gallegos | 2020-06-02 | Dave Goldak
CIV-04 | CIV-04 | PI18335 | Verified | Install safety Gate closing springs at platforms leading to exhaust fans (3 locations east side, 3 locations west side) | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2020-06-08 | Ron McMurtry | 2020-06-16 | Dave Goldak
CIV-04 | CIV-04 | PI18336 | Verified | GT west, elev 513-3: Install closing spring at safety gate between GT enclosure and Gas package | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm |  |  | 2021-04-21 | John Watts
CIV-04 | CIV-04 | PI18337 | Verified | GT north: Patch gap in toe plate, northwest corner of upper platform under green Fisher valves. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-05-28 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-04 | CIV-04 | PI18338 | Verified | GT north: Reinstall loose grating hold-down clip, northwest corner of upper platform under green Fisher valves. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-05-28 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-04 | CIV-04 | PI18339 | Verified | GT west, elev 509-6: Remove uni-strut support foot on grating under GT Gas Detection panel box. Reinstall to eliminate trip hazard. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-05-28 | Tim Gallegos | 2020-06-02 | Dave Goldak
CIV-04 | CIV-04 | PI18340 | Verified | GT South stair to tabletop: Missing hillside washers on stair stringer channel, east and west handrail attachments from Elev 500 ground to table top (Four handrails). | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-05-28 | Tim Gallegos | 2020-06-22 | Dave Goldak
CIV-04 | CIV-04 | PI18341 | Verified | GT South stair to tabletop elev 506-8: Install toe plate on east and west sides of stair landing. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-05-28 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-04 | CIV-04 | PI18342 | Verified | Isophase cross-over platform: North handrail - one loose connection bolt. Install hillside washer. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-16 | Tim Gallegos | 2020-07-07 | Dave Goldak
CIV-04 | CIV-04 | PI18343 | Verified | Isophase cross-over platform: Continue elevating guardrail west side of west ladder, or install straps. Reove scaffold rails. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-07-02 | Tim Gallegos | 2020-07-07 | Dave Goldak
CIV-04 | CIV-04 | PI18344 | Verified | Elev 500: Install lid or grate on open/unused drain hubs. One northwest of CTG (under gas line), one at column XB/X2 | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-18 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-04 | CIV-04 | PI18345 | Verified | Circuit Breaker Platform: Install gap section of toeplate, Northeast side of platform. Remove wood 2x4. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-07-02 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-04 | CIV-04 | PI18346 | Verified | Circuit Breaker Platform: Install toeplate around open hole in floor under GCB (3-sides). | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-07-02 | Tim Gallegos | 2020-07-07 | Dave Goldak
CIV-04 | CIV-04 | PI18347 | Verified | GT south west door (Elev 515): Install abrasive nosing, edge of platform at stair. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-05-28 | Tim Gallegos | 2020-06-02 | Dave Goldak
CIV-04 | CIV-04 | PI18348 | Verified | GT south east door (Elev 515): Install abrasive nosing, edge of platform at stair. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-05-28 | Tim Gallegos | 2020-06-02 | Dave Goldak
CIV-04 | CIV-04 | PI18349 | Verified | B Filter House West Jacking platform: Add toe plate to fill gaps (one location south behind ladder)(two locations east side of platform). | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm |  |  | 2021-04-21 | John Watts
CIV-04 | CIV-04 | PI18350 | Verified | B Filter House east Jacking platform: Add toe plate to fill gaps (one location south behind ladder)(two locations west side of platform). | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-04-21 | Eric Policarpio | 2021-04-21 | John Watts
CIV-04 | CIV-04 | PI18351 | Verified | B Filter House east Jacking platform ladder: Adjust closing spring to allow safety gate to operate automatically. | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2020-06-08 | Ron McMurtry | 2020-06-22 | Dave Goldak
CIV-04 | CIV-04 | PI18352 | Verified | B Filter House east manway access platform: Install closing spring to allow safety gate to operate automatically. | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2020-06-08 | Ron McMurtry | 2020-06-22 | Dave Goldak
CIV-04 | CIV-04 | PI18353 | Verified | B Filter House east manway access platform: Extend handrail on north end of platform closer to duct | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-04-21 | Eric Policarpio | 2021-04-21 | John Watts
CIV-04 | CIV-04 | PI18354 | Verified | B Filter House main platform: Reinstall loose or missing grating clips as-needed entire platform. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-08 | Tim Gallegos | 2020-06-10 | Dave Goldak
CIV-04 | CIV-04 | PI18355 | Verified | B Filter House main platform: Install toe plate around open hole under filter housing (three sides). | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-04-21 | Eric Policarpio | 2021-04-21 | John Watts
CIV-04 | CIV-04 | PI18356 | Verified | B Filter House West DP Instrument panel platform: Add toe plate to fill gaps behind ladder. | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-04-21 | Eric Policarpio | 2021-04-21 | Johnny Campbell
CIV-04 | CIV-04 | PI18357 | Verified | B Filter House West DP Instrument panel platform: Bend toe plate back into position, north end of platform. | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-04-21 | Eric Policarpio | 2021-04-21 | John Watts
CIV-04 | CIV-04 | PI18358 | Verified | B Filter House West DP Instrument panel platform: Extend north handrail/midrail to duct plate. | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2021-04-21 | Eric Policarpio | 2021-04-21 | Johnny Campbell
CIV-04 | CIV-04 | PI18359 | Verified | B Filter House West DP Instrument panel platform: Install safety gate closing spring | C | S | James Strange | MHI | 2020-05-26 | James Strange | Comm | 2020-06-08 | Ron McMurtry | 2020-06-22 | Dave Goldak
CIV-04 | CIV-04 | PI18360 | Verified | B GT filter house: Complete handrail/midrail repair at cutout for pipe conflict - northeast side of platform. Detail Case 6, LK-10-000-GN-STL-0001-13 | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-11 | Tim Gallegos | 2020-06-24 | Dave Goldak
CIV-04 | CIV-04 | PI18361 | Verified | B Upper filter house stair: Install missing grating clips - 1st platform at filter access doors. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-11 | Tim Gallegos | 2020-06-22 | Dave Goldak
CIV-04 | CIV-04 | PI18362 | Verified | B Upper filter house stair: Remove unused deck penetration, fill hole with grating - 1st platform at filter access doors. | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-23 | Tim Gallegos | 2020-08-07 | Dave Goldak
CIV-04 | CIV-04 | PI18363 | Verified | Elev 500: Install lid or grate on open/unused drain hubs. One east of Lube oil enclosure | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-11 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-04 | CIV-04 | PI18364 | Verified | Elev 500: Install lid or grate on open/unused drain hubs. Two west of Lube oil enclosure | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-11 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-04 | CIV-04 | PI18365 | Verified | Elev 500: CO2 Tank anchor bolts missing 2nd jamb nut (QTY=8). | C | S | Tim Gallegos | McD | 2020-05-26 | Tim Gallegos | Comm | 2020-06-08 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-05 | CIV-05 | PI00697 | Verified | Install HRSG PDC rain gutters. | C | S | Robert Risher | McD | 2019-04-26 | Robert Risher | Const | 2019-05-23 | Tim Gallegos | 2019-06-03 | Dave Goldak
CIV-05 | CIV-05 | PI00699 | Verified | Clean rust from HRSG PDC pedestal columns. | C | S | Robert Risher | McD | 2019-04-26 | Robert Risher | Const | 2019-05-17 | Michael Law | 2019-06-24 | Michael Law
CIV-05 | CIV-05 | PI00701 | Verified | HRSG PDC needs touch up painting. | C | X | Leo Mendoza | McD | 2019-04-26 | Leo Mendoza | Const | 2019-05-17 | Michael Law | 2019-06-24 | Michael Law
CIV-05 | CIV-05 | PI00703 | Verified | No access to HRSG PDC HVAC disconnects. | D | E | Kevin Leppert | McD | 2019-04-26 | Kevin Leppert | Const | 2020-02-07 | Keith Pollock | 2020-02-21 | Keith Pollock
CIV-05 | CIV-05 | PI15213 | Verified | Conduit penetration through grating needs toeplate at 1A-NJS-PNL-0003; HRSG 1A Top MOV Distribution PNL 3 | C | S | Tim Gallegos | McD | 2020-01-06 | Tim Gallegos | Comm | 2020-06-15 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI15218 | Verified | Conduit penetration through grating needs toeplate at 1A-NJS-PNL-0004; HRSG 1A Top MOV Distribution PNL 4 | C | S | Tim Gallegos | MHI | 2020-01-06 | Tim Gallegos | Comm | 2020-06-15 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI15400 | Verified | Duct burner PLT - anchor botl washer plate weld is not complete | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-09 | Tim Gallegos | 2020-04-09 | Michael Law
CIV-05 | CIV-05 | PI15401 | Verified | Duct Burner PLT - Extend handrail, add mid rail and toe plate at pipe support | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-09 | Tim Gallegos | 2020-04-09 | Michael Law
CIV-05 | CIV-05 | PI15402 | Verified | Duct Burner PLT - Toe Plate required at the edge of the equipment skid | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-09 | Tim Gallegos | 2020-04-09 | Michael Law
CIV-05 | CIV-05 | PI15446 | Verified | HRSG PDC 1A - Install nosing on top of the stairs | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-07 | Tim Gallegos | 2020-05-07 | Michael Law
CIV-05 | CIV-05 | PI15486 | Verified | HRSG 1A Stair tower - Landing to HRSG attachment per Nooter detail | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-05 | CIV-05 | PI15487 | Verified | HRSG 1A stair tower top landing - HR gap - ADD handrail | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-08-07 | Tim Gallegos | 2021-04-21 | John Watts
CIV-05 | CIV-05 | PI15488 | Verified | HRSG 1A top platform - Pipe opening toe plate installation | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-08-06 | Tim Gallegos | 2021-06-17 | John Watts
CIV-05 | CIV-05 | PI15489 | Verified | HRSG 1A Top platform - Handrail missing - install handrail | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-08-07 | Tim Gallegos | 2021-04-21 | John Edwards
CIV-05 | CIV-05 | PI15496 | Verified | GT blade wash ladder landing concrete pad is required | B | S | Johnny Campbell | McD | 2020-01-08 | Johnny Campbell | Const | 2020-01-20 | Alan Huntsman | 2020-01-29 | Michael Law
CIV-05 | CIV-05 | PI15540 | Verified | W SCR Entrance-landing platform not sufficeint -space between the HRSG and Utility Rack basemat slabs to be filled with concete (stone alternate) to establish level surface at ladder access/egress | B | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Const | 2020-01-20 | Alan Huntsman | 2020-01-27 | Michael Law
CIV-05 | CIV-05 | PI15542 | Verified | LP Preheater Sec-Top Rung not flush-adjust top rung as required - Grout required below base plate | B | C | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-25 | Bobby Williams | 2020-02-27 | Michael Law
CIV-05 | CIV-05 | PI15543 | Verified | LP Preheater Sec-no access- Needs fall protection cable ladder 25'-cont'd Construction Activity - safetly system included in PCN - 027 to upfit of ladders for compliance to new OSHA rules | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2021-04-21 | John Watts
CIV-05 | CIV-05 | PI15544 | Verified | E SCR Manway-ground wire/trip hazard at landing-punchlist item - relocate ground | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Const | 2020-04-09 | Chris Colvin | 2020-04-14 | Joe Wickline
CIV-05 | CIV-05 | PI15545 | Verified | E Amonia Injection-no cage/ladder not secure at bottom-at SCPS, the SCR injection ladder has been accepted as limited use and accessible only by authorized Vendors to tune valves | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-05 | CIV-05 | PI15546 | Verified | E Turbine Exhaust Manway-ground wire/trip hazard at landing-punchlist item - relocate ground | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Const | 2020-04-09 | Chris Colvin | 2020-04-14 | Joe Wickline
CIV-05 | CIV-05 | PI15552 | Verified | HP Steam Safety-not secured at bottom - complete installation | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-08-20 | Tim Gallegos | 2021-04-21 | John Watts
CIV-05 | CIV-05 | PI15553 | Verified | HP Water-not secured at bottom - complete installation | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-04-07 | Michael Law
CIV-05 | CIV-05 | PI15554 | Verified | LP Steam Safety-not secured at bottom and top bracket not installed -complete installation | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-04-07 | Michael Law
CIV-05 | CIV-05 | PI15555 | Verified | Drum Transmitter-no access -Inspection Required | D | S | Michael Law | McD | 2020-01-08 | Michael Law | Const | 2020-01-29 | Michael Law | 2020-01-29 | Michael Law
CIV-05 | CIV-05 | PI15556 | Verified | Stack -not secured at bottom - complete installation | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-04-07 | Michael Law
CIV-05 | CIV-05 | PI15557 | Verified | Stack -Inspection Required | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const |  |  | 2020-01-30 | Michael Law
CIV-05 | CIV-05 | PI15558 | Verified | IP Drum Safety-not secured at bottom/bent-Safety gate not installed | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-04-07 | Michael Law
CIV-05 | CIV-05 | PI15559 | Verified | HP Water Drum-Tubing & Conduit in 30"x30" space, 7" clear on back of the ladder is not available 3rd and 6h step | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-04-02 | Michael Law
CIV-05 | CIV-05 | PI15560 | Verified | SE Main Steam Platform-not installed | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-14 | Bobby Williams | 2020-02-18 | Michael Law
CIV-05 | CIV-05 | PI15561 | Verified | SW Main Steam Platform-not installed | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-14 | Bobby Williams | 2020-02-18 | Michael Law
CIV-05 | CIV-05 | PI17702 | Verified | 1A HRSG PDC: West platform missing abrasive nosing at top of stairs. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-04 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-05 | CIV-05 | PI17703 | Verified | 1A HRSG PDC: Weld 90-deg elbows at handrail & midrail. West platform | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-05 | CIV-05 | PI17704 | Verified | 1A HRSG PDC: West door swing not in compliance with OSHA requirements. 22 inches clear required between door swing and top of stairs. | D | S | John Edwards | McD | 2020-03-06 | John Edwards | Const | 2021-04-21 | Eric Policarpio | 2021-04-21 | John Watts
CIV-05 | CIV-05 | PI17705 | Verified | 1A HRSG PDC: West stair - multiple broken or missing stair rail support brackets. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-05 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-05 | CIV-05 | PI17706 | Verified | 1A HRSG PDC: Re-attach gutter downspouts. Terminate into underground drain (four locations). | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2020-06-10 | Dave Goldak
CIV-05 | CIV-05 | PI17707 | Verified | 1A HRSG PDC: West door missing closer. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-19 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-05 | CIV-05 | PI17708 | Verified | 1A HRSG PDC: Water intrusion evident on south wall under 480V panels | C | E | Chris Colvin | McD | 2020-03-06 | Chris Colvin | Const | 2020-04-21 | Matt Gilmore | 2020-07-07 | Dave Goldak
CIV-05 | CIV-05 | PI17709 | Verified | 1A HRSG PDC: One of the doors should be 44x96 for equipment movement. | D | S | Charles Worthington | McD | 2020-03-06 | Charles Worthington | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
CIV-05 | CIV-05 | PI17710 | Verified | 1A HRSG PDC: East stair - bottom stair height not equal to remainder of steps | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-11 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-05 | CIV-05 | PI17711 | Verified | 1A HRSG PDC: East stair - multiple broken or missing stair rail support brackets. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-11 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-05 | CIV-05 | PI17712 | Verified | 1A HRSG PDC: East platform missing abrasive nosing at top of stairs. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-05 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-05 | CIV-05 | PI17713 | Verified | 1A HRSG PDC: East door - install fasteners with rubber gaskets at open holes around east door. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-19 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-05 | CIV-05 | PI17714 | Verified | 1A HRSG PDC: Mount 20# CO2 fire extinguisher to the wall at each door. | C | C | Jerry Smith | McD | 2020-03-06 | Jerry Smith | Const | 2020-03-09 | Jerry Smith | 2020-03-12 | John Watts
CIV-05 | CIV-05 | PI17764 | Verified | Complete fall arrest system on 16 ladders on HRSG 1A | C | C | Tim Gallegos | McD | 2020-03-10 | Tim Gallegos | Const | 2020-06-18 | Tim Gallegos | 2020-07-21 | Tim Gallegos
CIV-05 | CIV-05 | PI18075 | Verified | Unit 1A West Superheat/Reheat Section Ladder - There's a ground in the landing on this ladder. | C | E | Chris Colvin | McD | 2020-03-18 | Chris Colvin | Comm | 2020-04-09 | Chris Colvin | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18202 | Verified | 1A HRSG PDC area: CEA not full thread engagement | C | P | Tim Gallegos | McD | 2020-04-17 | Tim Gallegos | Const | 2020-05-11 | Tim Gallegos | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18203 | Verified | 1A HRSG PDC area: CEA bolts too long throughout area | C | P | Tim Gallegos | McD | 2020-04-17 | Tim Gallegos | Const | 2020-05-05 | Tim Gallegos | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18204 | Verified | 1A HRSG PDC area: House keeping (entire area) | C | C | Johnny Campbell | McD | 2020-04-17 | Johnny Campbell | Const | 2020-04-29 | Johnny Campbell | 2020-08-07 | Dave Goldak
CIV-05 | CIV-05 | PI18205 | Verified | 1A HRSG PDC area: "two" Unitstrut conduit supports not utilized and left in place | C | E | Chris Colvin | McD | 2020-04-17 | Chris Colvin | Const | 2020-04-28 | Matt Gilmore | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18206 | Verified | 1A HRSG PDC area: incomplete grating (typical area) | C | C | Tim Gallegos | McD | 2020-04-17 | Tim Gallegos | Const | 2020-05-05 | Tim Gallegos | 2020-08-07 | Dave Goldak
CIV-05 | CIV-05 | PI18207 | Verified | 1A HRSG PDC area: Inadequately secured grounding over dyke curb | C | E | Chris Colvin | McD | 2020-04-17 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18208 | Verified | 1A HRSG PDC area: Skid grounding ran through cable support tray | D | E | Michael Law | McD | 2020-04-17 | Michael Law | Const | 2020-06-11 | Mike Tabbert | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18209 | Verified | 1A Phosphate Containment area: containment finish coating has various chipped and delaminated areas | C | C | Sheri Fritz | BRA | 2020-04-17 | Sheri Fritz | Const | 2020-05-19 | Johnny Campbell | 2020-07-28 | Keith Pollock
CIV-05 | CIV-05 | PI18210 | Verified | 1A HRSG PDC: Both downspout not installed to drain | C | C | Tim Gallegos | McD | 2020-04-17 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2020-07-28 | Keith Pollock
CIV-05 | CIV-05 | PI18211 | Verified | 1A HRSG PDC: Support grout pad delaminating from foundation | C | C | Johnny Campbell | McD | 2020-04-17 | Johnny Campbell | Const | 2020-04-29 | Johnny Campbell | 2020-07-28 | Keith Pollock
CIV-05 | CIV-05 | PI18212 | Verified | 1A HRSG East area: incomplete installation (drain) | C | C | Tim Gallegos | McD | 2020-04-17 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18213 | Verified | 1A HRSG Blowdown area: Unistrut support missing grout pad | C | C | Johnny Campbell | McD | 2020-04-17 | Johnny Campbell | Const | 2020-04-29 | Johnny Campbell | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18214 | Verified | 1A HRSG Blowdown area: painting /coating tape left in place on Skid | C | C | Johnny Campbell | McD | 2020-04-17 | Johnny Campbell | Const | 2020-04-21 | Chris Colvin | 2020-08-07 | Dave Goldak
CIV-05 | CIV-05 | PI18384 | Verified | Elev 500: Ammonia Flow Control skid containment: Clean out rim of drain hub grate and reinstall. Grate does not sit flush. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-08 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-05 | CIV-05 | PI18385 | Verified | Elev 500: Install permanent covers on unused hub drains (R2/4, R1/6, R3/9, R5/12) | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18386 | Verified | Elev 500: Install permanent cover on unused hub drain (Row G at UT Rack support, southeast side of HRSG) | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18387 | Verified | Duct Burner Platform: Install missing anchor bolt jamb nut, southeast support column. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-08 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-05 | CIV-05 | PI18388 | Verified | Duct Burner Platform: Weld square plate washers at column baseplates, all six platform support columns. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-09 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-05 | CIV-05 | PI18389 | Verified | Duct Burner Platform: Two anchor bolt jamb nuts are not galvanized, northwest support column. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-08 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-05 | CIV-05 | PI18390 | Verified | Duct Burner Platform: Weld vertical handrail post material - east side at 1A-FGS-V-264 handwheel/pipe conflict. Use LK-10-000-GN-STL-0001-13, Case 2 or 4. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-06-24 | Dave Goldak
CIV-05 | CIV-05 | PI18391 | Verified | Elev 596-6: Utility support framing not installed at R6/14. Northeast side of HRSG. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-07-24 | Jason Ezell | 2020-11-11 | Dave Goldak
CIV-05 | CIV-05 | PI18392 | Verified | Elev 549-0: Utility support framing not installed at L6/7-8. West face of HRSG. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-07-24 | Jason Ezell | 2020-11-11 | Dave Goldak
CIV-05 | CIV-05 | PI18393 | Verified | Elev 520-9: Utility support framing not installed at L3/9-10. West face of HRSG. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-08-06 | Tim Gallegos | 2020-08-14 | Dave Goldak
CIV-05 | CIV-05 | PI18394 | Verified | Elev 500: Tighten anchor bolt nut, ladder base connection, east side of HRSG, approx R4/7. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-08 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-05 | CIV-05 | PI18395 | Verified | Elev 500: Install one missing jamb nut, 1A HRSG stack anchor bolt, west side. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-19 | Tim Gallegos | 2020-06-24 | Dave Goldak
CIV-05 | CIV-05 | PI18396 | Verified | Elev 500: Cold Galvanize paint toe plate weld, northwest side of blowdown tank containment. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-08 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-05 | CIV-05 | PI18406 | Verified | 1A Nooter Stairtower. North Walk-off platform Elev 21'4": install toe plate bolts at bottom of stair stringer from stair tower. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-17 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18407 | Verified | 1A Nooter Stairtower. South Walk-off platform Elev 34'9" (stair to platform #32): Missing stair rail connection bolt to stringer. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-15 | Tim Gallegos | 2020-07-22 | Dave Goldak
CIV-05 | CIV-05 | PI18408 | Verified | 1A Nooter Stairtower. South Walk-off platform Elev 34'9" (stair to platform #32): Stringer attachment clips are welded to top of Platform #32 grating, rather than support steel. Incorrect installation. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18409 | Verified | 1A Nooter Stairtower. South Walk-off platform Elev 34'9" (stair to platform #32): Bottom stair does not project beyond landing toe plate. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18410 | Verified | 1A Nooter Stairtower. South landing Elev 34'9": Install toe plate connection bolts to west stringer - stair up to elev 46-5. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-17 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18411 | Verified | 1A Nooter Stairtower. North Walk-off platform Elev 45'10": Stringer attachment clips are welded to top of Platform #31 grating, rather than support steel. Incorrect installation. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-17 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18412 | Verified | 1A Nooter Stairtower. South Walk-off platform Elev 58'1" (stair to platform #30): Stringer attachment clips are welded to top of Platform #30 grating, rather than support steel. Incorrect installation. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-20 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18413 | Verified | 1A Nooter Stairtower. North Walk-off platform Elev 69'9": Stringer attachment clips are welded to top of Platform #29 grating, rather than support steel. Incorrect installation. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-20 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18414 | Verified | 1A Nooter Stairtower. South landing Elev 104'9": Install toe plate splice connection bolts at top of stairs. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-15 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-05 | CIV-05 | PI18415 | Verified | 1A Nooter Stairtower. South landing Elev 104'9": Install toe plate under first stair up to Platform #1 | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-20 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18416 | Verified | 1A Nooter Stairtower. South landing Elev 104'9": Stair Stringer (up to platform #1) attachment clips are welded to top of Stair Landing platform grating, rather than support steel. Incorrect installation. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-20 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18417 | Verified | 1A Nooter Platform #35. Clean and remove trash and unused materials from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18418 | Verified | 1A Nooter Platform #35. Cold galv paint 2 handrail/midrail splice welds, northwest and southwest corners. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-07-30 | Tim Gallegos | 2020-08-14 | Dave Goldak
CIV-05 | CIV-05 | PI18419 | Verified | 1A Nooter Platform #36. Clean and remove trash and unused electrical conduit & materials from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18420 | Verified | 1A Nooter Platform #36. Cold galv paint 2 handrail/midrail splice welds, southeast and southwest corners. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2020-08-14 | Dave Goldak
CIV-05 | CIV-05 | PI18421 | Verified | 1A Nooter Platform #15. Adjust toeplate and close open gap, east side at Line 4. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18422 | Verified | 1A Nooter Platform #32-A. Install abrasive nosing at north edge of landing at stair down to Elev 31-10. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18423 | Verified | 1A Nooter Platform #32-A. Secure bent toeplate at south end of intermediate landing platform Elev 533. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18424 | Verified | 1A Nooter Platform #32 (elev 31'10"). Weld handrail/midrail splaice at bottom of steps. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18425 | Verified | 1A Nooter Platform #32 (elev 31'10"). Remove unused support steel from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-07 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18426 | Verified | 1A Nooter Platform #32 (elev 31'10"). Install banding/toeplate at two pipe penetrations. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18427 | Verified | 1A Nooter Platform #29. Remove scrap lumber from deck. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-05 | CIV-05 | PI18428 | Verified | 1A Nooter Platform #29. Impact support bolts to specified 28k pounds. Two locations plates not in contact with HRSG support columns. Refer to details A and P. Ensure torque on platform bolts. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-16 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-05 | CIV-05 | PI18429 | Verified | 1A Nooter Platform #28. Remove trash, folding chair, unused tray cover from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18430 | Verified | 1A Nooter Platform #28. Install banding/toeplate at two pipe penetrations. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-20 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18431 | Verified | 1A Nooter Platform #28. Install attachment clip to base of ladder up to Platform #34. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18432 | Verified | 1A Nooter Platform #34. Remove trash, water cooler, unused electric wire from deck. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18433 | Verified | 1A Nooter Platform #34. Weld Handrail/midrail splice, northeast corner. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-20 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18434 | Verified | 1A Nooter Platform upper platform knee brace. Impact/torque loose knee brace support bolts, Line 5 east. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-06 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18435 | Verified | 1A Nooter Platform #1 (top). Install loose/missing grating clips, scattered locations arounds . | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18436 | Verified | 1A Nooter Platform #1 (top). Repair/straighten bent toeplate at west side of stair to Platform #3 | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18437 | Verified | 1A Nooter Platform #1 (top). Weld accessible handrail/midrail splices south end of platform at superheater piping. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18438 | Verified | 1A Nooter Platform #1 (top). Restore cut-off HR post at 1A-FWS-V-8144. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18439 | Verified | 1A Nooter Platform #1 (top). Install missing toeplate at gaps behind DSH spray water piping (south west side) | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18440 | Verified | 1A Nooter Platform #1 (top). Weld caps on cut-off handrail/midrail at west stair down to platform #2 | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18441 | Verified | 1A Nooter Platform #1 (top). Weld caps on cut-off handrail at west valve actuator (red). | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18442 | Verified | 1A Nooter Platform #3 (top). Install abrasive nosing, two stair treads between Platforms #1 & #3 (top two treads). | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-07 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18443 | Verified | 1A Nooter Platform #3 (top). Extend handrail/midrail/toeplate to close gap between stair rail and east platform railing. Remove scaffold hard barricade. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-07 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18444 | Verified | 1A Nooter Platform #3 (top). Weld handrail/midrail splice south end of platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18445 | Verified | 1A Nooter Platform #3 (top). Weld handrail/midrail splice west end of platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18446 | Verified | 1A Nooter Platform #3 (top). Reinstall vertical extension to handrail, west of Platform #38. See drawing 170340-PF-E-08-02 SECTION A-A. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-20 | Tim Gallegos | 2021-01-25 | Dave Goldak
CIV-05 | CIV-05 | PI18447 | Verified | 1A Nooter Platform #3 (top). Install banding at cutouts for hot reheat and superheat outlet pipe supports. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-06 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18448 | Verified | 1A Nooter Platform #3 (top). Weld cap on cut-off handrail at west superheat pipe cut-out. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-20 | Tim Gallegos | 2021-01-25 | Dave Goldak
CIV-05 | CIV-05 | PI18449 | Verified | 1A Nooter Platform #38 (top). Missing east ladder. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-20 | Tim Gallegos | 2021-01-25 | Dave Goldak
CIV-05 | CIV-05 | PI18450 | Verified | 1A Nooter Platform #38 (top). Install clips to grating, base of west ladder. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-20 | Tim Gallegos | 2021-01-25 | Dave Goldak
CIV-05 | CIV-05 | PI18451 | Verified | 1A Nooter Platform #51. Install toe plate splice bolts west side, under drum ladder. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18452 | Verified | 1A Nooter Platform #51. Weld handrail/midrail splices northeast and southeast corners. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18453 | Verified | 1A Nooter Platform #52. Remove unused unistrut materials from deck. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-12 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18455 | Verified | 1A Nooter Platform #52. Install banding at heat trace/electrical conduit penetrations. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18456 | Verified | 1A Nooter Platform #52. Install toe plate gap filler, east side of platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18457 | Verified | 1A Nooter Platform #42. Anchor base of ladder to Platform #2 grating. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18458 | Verified | 1A Nooter Platform #42. Weld two handrail/midrail splices, northeast and southeast corners. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18459 | Verified | 1A Nooter Platform #7. Conduit conflict at bottom rung of ladder. 7inches clear required behind adder rung to any obstruction. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-20 | Tim Gallegos | 2021-01-25 | Dave Goldak
CIV-05 | CIV-05 | PI18460 | Verified | 1A Nooter Platform #50 (drum). Conduit and HT tubing conflict at bottom of ladder. 7inches clear required behind adder rung to any obstruction. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-06 | Tim Gallegos | 2021-04-21 | John Watts
CIV-05 | CIV-05 | PI18461 | Verified | 1A Nooter Platform #50 (drum). Obstructions to either side of ladder do not meet minimum clear distance. 15 inches clear (from ladder centerline) to any obstruction. Ref: 1A-CAB-HTS-0314,(left) Conduit (right) | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2021-01-25 | Dave Goldak
CIV-05 | CIV-05 | PI18462 | Verified | 1A Nooter Platform #2 (top), east stairway to platform #1. Loose bolt at base of west stair stringer. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18463 | Verified | 1A Nooter Platform #2 (top). Complete banding/toe plate installations at pipe,& electrical penetrations through grating (in progress). | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-06 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18464 | Verified | 1A Nooter Platform #2 (top). Weld two handrail/midrail splices, east side of platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18465 | Verified | 1A Nooter Platform #2 (top). Weld handrail/midrail splice, behind 1A-MBS-JB-8004 panel. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18466 | Verified | 1A Nooter Platform #2 (top). Loose stair rail connection to stringer, west stairway up to platform #1. Tighten bolts. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18467 | Verified | 1A Nooter Platform #2 (top). Loose C-Channel connection bolts to substructure. Located at north side of Platform #50. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18468 | Verified | 1A Nooter Platform #2 (top). Loose bolt , top of ladder at Platform #50. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18469 | Verified | 1A Nooter Platform #2 (top). Weld cap on midrail cut-out for pipe conflict - northwest and southwest sides of LP steam drum. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18470 | Verified | 1A Nooter Platform #2. Adjust toeplate and close open gap, west side of platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18471 | Verified | 1A Nooter Platform #2. Adjust toeplate and close open gap, north of LP Steam drum. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18472 | Verified | 1A Nooter Platform #2. Complete toeplate splice bolt installation, north of LP Steam drum. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18473 | Verified | 1A Nooter Platform #2. Kill threads on Platform #2V at stack bridge. See drawing 170340-PF-E-04-09, section C-C. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-06 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18474 | Verified | 1A Nooter Platform #2. Install clips to grating at base of ladder up to platform #5 | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18475 | Verified | 1A Nooter Platform #2. Install banding/toeplate at penetration through grating - north side of stack. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18476 | Verified | 1A Nooter Platform #5 ladder (stack). Paint cold galvanizing on ladder rail splice welds. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18477 | Verified | 1A HRSP IP Silencer #2 support. Tighten loose bolt connections at support base plate to structural steel. Southeast side of IP Steam drum. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18478 | Verified | 1A Nooter Platform #44. Platform not installed per drawing orientation. Ladder designed to be on north end of platform. Rotate 90-deg. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18479 | Verified | 1A Nooter Platform #44. Anchor clip ladder to platform #2 grating. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18480 | Verified | 1A Nooter Platform #44. Weld handrail/midrail splices. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18481 | Verified | 1A Nooter Platform #39. Platform not fastened to platform #2 grating. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18482 | Verified | 1A Nooter Platform #39. Anchor clip ladder to platform #2 grating. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18483 | Verified | 1A Nooter Platform #39. Weld handrail/midrail splices. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-14 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18484 | Verified | 1A Nooter Platform #40. Platform not installed per drawing orientation. Ladder designed to be on north end of platform. Rotate 90-deg. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-17 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18485 | Verified | 1A Nooter Platform #40. Anchor clip ladder to platform #2 grating. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-17 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18486 | Verified | 1A Nooter Platform #40. Weld handrail/midrail splices. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-17 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-05 | CIV-05 | PI18487 | Verified | 1A Nooter Platform upper platform knee brace. Impact/torque loose knee brace support bolts, Line 7 west. Connecting bolts on HRSG and intermediate connectors on double-L brace. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-16 | Tim Gallegos | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18488 | Verified | 1A Nooter Platform #10. Remove trash, #9 wire, etc from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18489 | Verified | 1A Nooter Platform #11. Remove trash, lumber, unused electrcal materials, etc. from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18490 | Verified | 1A Nooter Platform #11. Close bent toeplate gap at HRSG line 4. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-07 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18491 | Verified | 1A Nooter Platform #12. Weld handrail/midrail splices, northwest corner of platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-07 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18492 | Verified | 1A Nooter Platform #12. Remove unused large diameter bolts from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18493 | Verified | 1A Nooter Platform #13. Remove trash, cribbing, unused electrical materials, etc. from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18494 | Verified | 1A Nooter Platform #13. Repair gap in toe plate top of ladder from ground, west side. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-07 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18495 | Verified | 1A Nooter Platform #13. Repair gap in toe plate behind ladder to platform #27, east side. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-07 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18496 | Verified | 1A Nooter Platform #27. Remove trash, lumber, etc. from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18497 | Verified | 1A Nooter Platform #27. Install banding around HTS bundle penetration through grating. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-17 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18498 | Verified | 1A Nooter Platform #26. Remove trash, paint lids, unused electrcal materials, etc. from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18499 | Verified | 1A Nooter Platform #25. Remove trash, lumber, wire, snow fence, etc. from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18500 | Verified | 1A Nooter Platform #17. Weld handrail/midrail splices, 3 locations on east side of platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-12 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18501 | Verified | 1A Nooter Platform #17. Remove scaffold posts and timber decking between HRSG Columns 10-11. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2020-08-07 | Dave Goldak
CIV-05 | CIV-05 | PI18502 | Verified | 1A Nooter Platform #17. Paint cold galvanizing on handrail splice weld, west side of platform, south of HRSG column 12. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-07-30 | Tim Gallegos | 2020-08-07 | Dave Goldak
CIV-05 | CIV-05 | PI18503 | Verified | 1A Nooter Platform #17. Weld handrail/midrail splice west side of platform, north of HRSG Column 13. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-12 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18504 | Verified | 1A Nooter Platform #16. Weld handrail/midrail splice southwest corner of platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-12 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18505 | Verified | 1A Nooter Platform #16. Clip base of ladder to grating. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-12 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18506 | Verified | 1A Nooter Platform #16. Conduit conflict under top rung of ladder. 7inches clear required behind adder rung to any obstruction. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-07-30 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-05 | CIV-05 | PI18507 | Verified | 1A Nooter Platform #23. Remove trash and welding leads, etc. from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18508 | Verified | 1A Nooter Platform #22. Remove trash, wire, unused electrical materials, etc. from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18509 | Verified | 1A Nooter Platform #22. Reinstall handrail post cut off at north valve installation. Install caps as necessary. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-17 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18510 | Verified | 1A Nooter Platform #22. Close gap between toeplate and deck, northeast corner of platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-17 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-05 | CIV-05 | PI18511 | Verified | 1A Nooter Platform #21. Remove trash, unused electrical materials, etc. from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18512 | Verified | 1A Nooter Platform #20. Remove trash, unused electrical materials, etc. from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18513 | Verified | 1A Nooter Platform #20. Knee brace platform support plate has been welded to HRSG Column #5. Drawing 170340-PF-E-26-01, detail C indicates a bolted connection. Is there a RFI or Engineering disposition? | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2021-06-17 | John Watts
CIV-05 | CIV-05 | PI18514 | Verified | 1A Nooter Platform #19. Close gap between toeplate and deck, west side of platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-08-17 | Tim Gallegos | 2020-10-22 | Dave Goldak
CIV-05 | CIV-05 | PI18515 | Verified | 1A Nooter Platform #19. Remove trash, unused materials, etc. from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18516 | Verified | 1A Nooter Platform #18. Remove trash, unused electrical materials, spare valve handles, etc. from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18517 | Verified | 1A Nooter Platform #24. Remove trash, weldng leads, etc. from platform. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CIV-05 | CIV-05 | PI18518 | Verified | 1A Nooter Platform upper platform knee brace. Impact/torque loose intermediate connectors on double-L brace bolts, Line 6 west. | C | S | Tim Gallegos | McD | 2020-06-09 | Tim Gallegos | Const | 2020-06-16 | Tim Gallegos | 2020-10-22 | Dave Goldak
CIV-06 | CIV-06 | PI00698 | Verified | Install HRSG PDC rain gutters. | C | S | Robert Risher | McD | 2019-04-26 | Robert Risher | Const | 2019-05-23 | Tim Gallegos | 2019-06-03 | Dave Goldak
CIV-06 | CIV-06 | PI00700 | Verified | Clean rust from HRSG PDC pedestal columns. | C | S | Robert Risher | McD | 2019-04-26 | Robert Risher | Const | 2019-05-17 | Michael Law | 2019-06-24 | Michael Law
CIV-06 | CIV-06 | PI00702 | Verified | HRSG PDC needs touch up painting. | C | X | Leo Mendoza | McD | 2019-04-26 | Leo Mendoza | Const | 2019-05-17 | Michael Law | 2019-06-24 | Michael Law
CIV-06 | CIV-06 | PI00704 | Verified | No access to HRSG PDC HVAC disconnects. | D | E | Kevin Leppert | McD | 2019-04-26 | Kevin Leppert | Const | 2020-02-07 | Keith Pollock | 2020-02-21 | Keith Pollock
CIV-06 | CIV-06 | PI00705 | Verified | Install east stairway for the 1B HRSG PDC. | B | S | Robert Risher | McD | 2019-04-26 | Robert Risher | Const | 2019-05-23 | Tim Gallegos | 2019-06-12 | Mike Tabbert
CIV-06 | CIV-06 | PI15223 | Verified | Conduit penetration through grating needs toeplate at 1B-NJS-PNL-0003; HRSG 1B Top MOV Distribution PNL 3 | C | S | Tim Gallegos | McD | 2020-01-06 | Tim Gallegos | Comm | 2020-05-12 | Tim Gallegos | 2020-08-07 | Dave Goldak
CIV-06 | CIV-06 | PI15228 | Verified | Conduit penetration through grating needs toeplate at 1B-NJS-PNL-0004; HRSG 1B Top MOV Distribution PNL 4 | C | S | Tim Gallegos | McD | 2020-01-06 | Tim Gallegos | Comm | 2020-05-12 | Tim Gallegos | 2020-08-07 | Dave Goldak
CIV-06 | CIV-06 | PI15425 | Verified | Duct burner PLT - anchor botl washer plate weld is not complete | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-24 | Tim Gallegos | 2020-02-24 | Michael Law
CIV-06 | CIV-06 | PI15426 | Verified | Duct Burner PLT - Extend handrail, add mid rail and toe plate at pipe support | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-24 | Tim Gallegos | 2020-02-24 | Michael Law
CIV-06 | CIV-06 | PI15427 | Verified | Duct Burner PLT - Toe Plate required at the edge of the equipment skid | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-24 | Tim Gallegos | 2020-02-24 | Michael Law
CIV-06 | CIV-06 | PI15447 | Verified | HRSG PDC 1B - Correct handrail weld at the corner | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-07 | Tim Gallegos | 2020-05-07 | Michael Law
CIV-06 | CIV-06 | PI15448 | Verified | HRSG PDC 1B - Install nosing on top of the stairs | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-04 | Tim Gallegos | 2020-05-07 | Michael Law
CIV-06 | CIV-06 | PI15490 | Verified | HRSG 1B Stair tower - Landing to HRSG attachment per Nooter detail | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-07-21 | Satyam Gajjar
CIV-06 | CIV-06 | PI15491 | Verified | HRSG 1B stair tower top landing - HR gap - ADD handrail | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-07-21 | Satyam Gajjar
CIV-06 | CIV-06 | PI15492 | Verified | HRSG 1B top platform - Pipe opening toe plate installation | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-07-21 | Satyam Gajjar
CIV-06 | CIV-06 | PI15493 | Verified | HRSG 1B Top platform - Handrail missing - install handrail | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-07-21 | Satyam Gajjar
CIV-06 | CIV-06 | PI15521 | Verified | W- SCR Entrance - Landing doesn't meet standard - space between the HRSG and Utility Rack basemat slabs to be filled with concete (stone alternate) to establish level surface at ladder access/egress | B | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Const | 2020-01-20 | Alan Huntsman | 2020-01-27 | Michael Law
CIV-06 | CIV-06 | PI15524 | Verified | LP Preheater Sec - No Access 27 rungs No Fall arrest on ladder - cont'd Construction Activity - safetly system included in PCN - 027 to upfit of ladders for compliance to new OSHA rules | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2021-04-21 | John Watts
CIV-06 | CIV-06 | PI15525 | Verified | E Amonia Injection - No cage or fall arrest 70' ladder and not bolted at bottom - at SCPS, the SCR injection ladder has been accepted as limited use and accessible only by authorized Vendors to tune valves | D | S | Michael Law | McD | 2020-01-08 | Michael Law | Const |  |  | 2020-01-30 | Michael Johnson
CIV-06 | CIV-06 | PI15530 | Verified | E -Mid level to manway/low point drain MOV's - 12 and 1/2" across to the grating - cont'd Construction Activity - review after final bolt up | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-04-02 | Michael Law
CIV-06 | CIV-06 | PI15531 | Verified | HP Water - 7" clear not available due to conduits | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-04-02 | Michael Law
CIV-06 | CIV-06 | PI15532 | Verified | Drum Transmitter - No Access - cont'd Construction Activity | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-14 | Bobby Williams | 2020-02-18 | Michael Law
CIV-06 | CIV-06 | PI15533 | Verified | Stack - Did Not Climb - Inspection Required - safety cage on back of the ladder need to be installed | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-25 | Michael Law | 2020-02-25 | Michael Law
CIV-06 | CIV-06 | PI15534 | Verified | Stack - Did Not Climb - Inspection Required | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const |  |  | 2020-01-30 | Michael Law
CIV-06 | CIV-06 | PI15535 | Verified | HRSG ladder #28 - safety gate not installed and 7" clearance not available | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-04-07 | Michael Law
CIV-06 | CIV-06 | PI15536 | Verified | SE- Main Steam Platform - Install | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-14 | Bobby Williams | 2020-02-18 | Michael Law
CIV-06 | CIV-06 | PI15537 | Verified | SW -Main Steam Platform - Install | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-14 | Bobby Williams | 2020-02-18 | Michael Law
CIV-06 | CIV-06 | PI17715 | Verified | 1B HRSG PDC: West platform missing abrasive nosing at top of stairs. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-04 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-06 | CIV-06 | PI17716 | Verified | 1B HRSG PDC: Weld 90-deg elbows at handrail & midrail. West platform | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-04 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-06 | CIV-06 | PI17717 | Verified | 1B HRSG PDC: West door swing not in compliance with OSHA requirements. 22 inches clear required between door swing and top of stairs. | D | S | John Edwards | McD | 2020-03-06 | John Edwards | Const | 2021-04-21 | Eric Policarpio | 2021-04-21 | John Watts
CIV-06 | CIV-06 | PI17718 | Verified | 1B HRSG PDC: West stair - multiple broken stair rail support brackets. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-06 | CIV-06 | PI17719 | Verified | 1B HRSG PDC: West platform - trim handrail and mid rail. Digging into enclosure siding. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-04 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-06 | CIV-06 | PI17720 | Verified | 1A HRSG PDC: Re-attach gutter downspouts. Terminate into underground drain (four locations). | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2020-06-10 | Dave Goldak
CIV-06 | CIV-06 | PI17721 | Verified | 1B HRSG PDC: East door closer disconnected. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-19 | Tim Gallegos | 2020-07-07 | Dave Goldak
CIV-06 | CIV-06 | PI17722 | Verified | 1B HRSG PDC: Adjust east panic hardware and latch. Cannot open door from outside. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-11 | Tim Gallegos | 2020-07-07 | Dave Goldak
CIV-06 | CIV-06 | PI17723 | Verified | 1B HRSG PDC: One of the doors should be 44x96 for equipment movement. | D | S | Charles Worthington | McD | 2020-03-06 | Charles Worthington | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
CIV-06 | CIV-06 | PI17724 | Verified | 1B HRSG PDC: East stair - two broken and one missing stair rail support brackets. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-04 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-06 | CIV-06 | PI17725 | Verified | 1B HRSG PDC: East platform missing abrasive nosing at top of stairs. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-04 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-06 | CIV-06 | PI17726 | Verified | 1B HRSG PDC: East door - install fasteners with rubber gaskets at open holes around east door. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-04 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-06 | CIV-06 | PI17727 | Verified | 1B HRSG PDC: Mount 20# CO2 fire extinguisher to the wall at each door. 1B HRSG PDC missing one extinguisher. | C | C | Jerry Smith | McD | 2020-03-06 | Jerry Smith | Const | 2020-03-09 | Jerry Smith | 2020-03-12 | John Watts
CIV-06 | CIV-06 | PI17765 | Verified | Complete fall arrest system on 16 ladders on HRSG 1B | C | C | Tim Gallegos | McD | 2020-03-10 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-07-21 | Tim Gallegos
CIV-06 | CIV-06 | PI18073 | Verified | Unit 1B HP Water Ladder - There's no swing gate at the top of the HP Water ladder. Refer to OSHA Regulation: 1910.23(a)(2) | C | S | Tim Gallegos | McD | 2020-03-18 | Tim Gallegos | Comm | 2020-07-27 | Eric Policarpio | 2020-07-27 | Dave Goldak
CIV-06 | CIV-06 | PI18170 | Verified | Support stand needs to be grouted west of 1BMBH05AC301 GT cooling air | C | C | Johnny Campbell | McD | 2020-03-21 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-05-26 | Randy Carpenter
CIV-06 | CIV-06 | PI18397 | Verified | Elev 500: Ammonia Flow Control skid containment: Clean out rim of drain hub grate and reinstall. Grate does not sit flush. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-08 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-06 | CIV-06 | PI18398 | Verified | Elev 500: Install permanent covers on unused hub drains (R2/4, R1/6, R3/9, R5/12, L3/9, L1/6) | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-06 | CIV-06 | PI18399 | Verified | Elev 500: Install permanent cover on unused hub drain (Row G at UT Rack support, southeast side of HRSG) | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-06 | CIV-06 | PI18400 | Verified | Duct Burner Platform: Install three missing anchor bolt jamb nuts, southwest support column. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-08 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-06 | CIV-06 | PI18401 | Verified | Duct Burner Platform: Weld square plate washers at column baseplates, all six platform support columns. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-06 | CIV-06 | PI18402 | Verified | Duct Burner Platform: Weld vertical handrail post material - east side at V-264 handwheel/pipe conflict. Use LK-10-000-GN-STL-0001-13, Case 2 or 4. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-06-24 | Dave Goldak
CIV-06 | CIV-06 | PI18403 | Verified | Elev 596-6: Utility support framing not installed at R6/14. Northeast side of HRSG. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-11-11 | Dave Goldak
CIV-06 | CIV-06 | PI18404 | Verified | Elev 549-0: Utility support framing not installed at L6/7-8. West face of HRSG. | C | S | Tim Gallegos | McD | 2020-06-05 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2020-11-11 | Dave Goldak
CIV-06 | CIV-06 | PI18541 | Verified | 1B Nooter Platform #11. Close gap between toeplate and grating, west side of platform at HRSG Col line 4. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18542 | Verified | 1B Nooter Platform #35. Weld handrail/midrail splices, NW & SW corners | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-06 | CIV-06 | PI18543 | Verified | 1B Nooter Platform #36. Weld handrail/midrail splices, SE & SW corners | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-06 | CIV-06 | PI18544 | Verified | 1B Nooter Platform #36. Close gap between toeplate and grating, South side of platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-11-11 | Dave Goldak
CIV-06 | CIV-06 | PI18545 | Verified | 1B Nooter Platform #16. Conduit conflict under top rung of ladder. 7 inches clear required behind ladder rung to any obstruction. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-20 | Dave Goldak
CIV-06 | CIV-06 | PI18546 | Verified | 1B Nooter Platform #17. Close gap between toeplate and grating, multiple locations east side of platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18547 | Verified | 1B Nooter Platform #15. Close gap between toeplate and grating, east side of platform, HRSG Line 4 at splice. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18548 | Verified | 1B Nooter Platform #32. Elev 533: Secure toe plate on south end of intermediate platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18549 | Verified | 1B Nooter Platform #32 Elev 533. Install abrasive nosing at north edge of intermediate landing (stair down to Elev 31-10). | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18550 | Verified | 1B Nooter Platform #32 (elev 31'10"). Remove or install unused support steel from platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-08-12 | Tim Gallegos | 2020-08-21 | Dave Goldak
CIV-06 | CIV-06 | PI18551 | Verified | 1B Nooter Platform #32 (elev 31'10"). Install banding/toeplate at two pipe penetrations. North end. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18552 | Verified | 1B Nooter Platform #32 (elev 31'10"). Weld handrail/midrail splices, two locations west side. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18553 | Verified | 1B Nooter Platform #32 (elev 31'10"). Complete toe plate at edge of platform, west side underneath duct burner valves and piping. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18554 | Verified | 1B Nooter Platform #30. Close gap between toeplate and grating, north side of platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18555 | Verified | 1B Nooter Platform #29. Close gap between toeplate and grating, east side of platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-06 | CIV-06 | PI18556 | Verified | 1B Nooter Stairtower. South landing Elev 11'5": Stair stringers not clipped & welded to Platform #15 support framing. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18557 | Verified | 1B Nooter Stairtower. North Walk-off platform Elev 21'4": Stair stringers not clipped & welded to Platform #33 support framing. One clip missing. One sitting on top of grating at Platform #33. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18558 | Verified | 1B Nooter Stairtower. South landing Elev 34'9": Stair stringers not clipped & welded to Platform #32 support framing. Incorrect installation. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18559 | Verified | 1B Nooter Stairtower. South Walk-off platform Elev 34'9" (stair to platform #32): Bottom stair tread does not project beyond landing toe plate. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18560 | Verified | 1B Nooter Stairtower. North Walk-off platform Elev 45'10": Stringer attachment clips are welded to top of Platform #31 grating, rather than support steel framing. Incorrect installation. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18561 | Verified | 1B Nooter Stairtower. South Walk-off platform Elev 58'1" (stair to platform #30): One stringer attachment clip missing, the other is not welded to Platform #30 support steel. Incorrect installation. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18562 | Verified | 1B Nooter Stairtower. North Walk-off platform Elev 69'9": Stringer attachment clips are welded to top of Platform #29 grating, rather than support steel. Incorrect installation. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18563 | Verified | 1B Nooter Stairtower. South landing Elev 104'9": Install toe plate under first stair up to Platform #1 | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-06 | CIV-06 | PI18564 | Verified | 1B Nooter Stairtower. South landing Elev 104'9": Stair Stringer (up to platform #1) attachment clips are missing. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-06 | CIV-06 | PI18565 | Verified | 1B Nooter Platform #28. Install banding/toeplate at pipe penetration. North end. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-06 | CIV-06 | PI18566 | Verified | 1B Nooter Platform #28. Remove unused electrical material and handrail section, etc. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-18 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18567 | Verified | 1B Nooter Platform #28. Weld four midrail caps at cut out section for pipe support. North end. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-06 | CIV-06 | PI18568 | Verified | 1B Nooter Platform #28. Weld two midrail caps at cut out section for valve. Northeast end. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-06 | CIV-06 | PI18569 | Verified | 1B Nooter Platform #28. Weld handrail/midrail splice, south end. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-06 | CIV-06 | PI18570 | Verified | 1B Nooter Platform #28. Close gap between toeplate and grating, west and east sides of platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-06 | CIV-06 | PI18571 | Verified | 1B Nooter Platform #34. Weld handrail/midrail splice, northeast corner. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-06 | CIV-06 | PI18572 | Verified | 1B Nooter Platform #34. Weld cap on cutoff handrail post, southeast corner. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-06 | CIV-06 | PI18573 | Verified | 1B Nooter Platform #23. Remove step ladder and unused electrical materials from platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-08-12 | Tim Gallegos | 2020-11-11 | Dave Goldak
CIV-06 | CIV-06 | PI18574 | Verified | 1B Nooter Platform #22. Weld handrail/midrail splice, east side of platform at HRSG window. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18575 | Verified | 1B Nooter Platform #20. Knee brace platform support plate has been welded to HRSG Column #5. Drawing 170340-PF-E-26-01, detail C indicates a bolted connection. Is there a RFI or Engineering disposition? | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-08-06 | Tim Gallegos | 2021-06-17 | John Watts
CIV-06 | CIV-06 | PI18576 | Verified | 1B Nooter Platform #20. Re-install section of handrail and posts cut out and removed from north end of platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18577 | Verified | 1B Nooter Platform #20. Install banding/toeplate at two penetrations through grating for piping and support. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18578 | Verified | 1B Nooter Platform #20. Weld cut toe plate - north end. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-14 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18579 | Verified | 1B Nooter Platform #19. Close gap between toeplate and grating, west side of platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18580 | Verified | 1B Nooter Platform #19. Weld cut toe plate - east side of platform behind ladder. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18581 | Verified | 1B Nooter Platform #24. Close gap between toeplate and grating, east and west sides of platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-08-06 | Tim Gallegos | 2020-11-11 | Dave Goldak
CIV-06 | CIV-06 | PI18582 | Verified | 1B Nooter Platform #27. Close gap between toeplate and grating, three locations on east side and one location on west side of platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18583 | Verified | 1B Nooter Platform #27. Cold galv paint midrail splice weld, wes side of platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18584 | Verified | 1B Nooter Platform #27. Instal banding/toeplate at Heat trace tubing penetration through deck. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-24 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18585 | Verified | 1B Nooter Platform #26. Close gap between toeplate and grating, one location on east side (behind ladder) and two locations on west side of platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-28 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-06 | CIV-06 | PI18586 | Verified | 1B Nooter Platform #25. Loose bolts at platform support knee brace connection to HRSG Col#11. Lower connection. Upper connection also appears loose, but can't reach to verify. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-16 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18587 | Verified | 1B Nooter Platform #3 (top). Complete banding and toeplate at penetrations through grating (in progress). | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-30 | Mike Tabbert | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18588 | Verified | 1B Nooter Platform #3 (top). Weld handrail/midrail splice, northwest railing. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18589 | Verified | 1B Nooter Platform #3 (top). Weld handrail/midrail splice, southeast railing. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18590 | Verified | 1B Nooter Platform #3 (top). Install toe plate on west edge of platform, under Hot Reheat steam piping. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-30 | Mike Tabbert | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18591 | Verified | 1B Nooter Platform #3 (top). Remove braided cable sling, west edge of platform, under Hot Reheat steam piping. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18592 | Verified | 1B Nooter Platform #3 (top). Reinstall guard rail vertical extension, west of Platform #38. Refer to Nooter Drawing 170340-PF-E-08-02, Section A-A. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-30 | Mike Tabbert | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18593 | Verified | 1B Nooter Platform #3 (top). Extend handrail/midrail to close gap between stair rail and east platform railing at bottom of stairs from Platform #1. Remove scaffold hard barricade. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-08 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18594 | Verified | 1B Nooter Platform #3 (top). Install two missing bolts to fasten toeplate to structure, east platform railing at bottom of stairs from Platform #1. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-08 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18595 | Verified | 1B Nooter Platform #3 (top). Close gap between toeplate and grating, west of stair stringer, bottom of steps. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-08 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18596 | Verified | 1B Nooter Platform #1 (top). Complete banding and toeplate at penetrations through grating (in progress). | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-30 | Mike Tabbert | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18597 | Verified | 1B Nooter Platform #1 (top). Weld caps (2) on handrail cutoffs, west side at red valve actuator. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18598 | Verified | 1B Nooter Platform #1 (top). Secure toeplate at top of west stairs down to Platform #2. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18599 | Verified | 1B Nooter Platform #1 (top). Cold galvanize paint existing handrail/midrail caps at top of stair down to Platform #2. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18600 | Verified | 1B Nooter Platform #1 (top). Complete toe plate installation, east end of HP Steam drum. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-06 | CIV-06 | PI18601 | Verified | 1B Nooter Platform #1 (top). Secure toeplate at top of east stairs down to Platform #2. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18602 | Verified | 1B Nooter Platform #2 (top). Weld handrail/midrail splice and install bolts in toeplate splice, east end behind 1B-HTS-CAB-0109. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-01 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18603 | Verified | 1B Nooter Platform #2 (top). Remove unused instrument support base plate from deck, east end behind 1B-HTS-CAB-0109. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18604 | Verified | 1B Nooter Platform #2 (top). Complete banding and toeplate at penetrations through grating (in progress). | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18605 | Verified | 1B Nooter Platform #2 (top). Install toeplate, east and west ends of IP and LP steam drums. Remove 2x4 lumber. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-08 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18606 | Verified | 1B Nooter Platform #2 (top). Install toeplate splice bolts, north side of LP steam drum. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18607 | Verified | 1B Nooter Platform #2 (top). Weld four midrail cap ends at cutout sections, north side of LP steam drum. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18608 | Verified | 1B Nooter Platform #2 (top). Install toeplate behind ladder to Platform #52 (west). | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18609 | Verified | 1B Nooter Platform #2 (around stack). Remove unused expanded metal stand-off screening material from the platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18610 | Verified | 1B Nooter Platform #2 (around stack). Install toe plate around cable tray penetration through grating - north side of stack. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18611 | Verified | 1B Nooter Platform #2 (around stack). Kill threads on Platform #2V at stack bridge. See drawing 170340-PF-E-04-09, section C-C. Four bolts. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18612 | Verified | 1B Nooter Platform #38 (top). Platform installation is incomplete. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18637 | Verified | 1B Nooter Platform #37. Weld handrail/midrail splice northwest corner behind ladder. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-07 | CIV-07 | PI00986 | Verified | Install grating CT Chem Storage Foundation x 5 | B | C | Bobby Williams | McD | 2019-05-06 | Bobby Williams | Const | 2019-07-17 | Michael Law | 2019-10-03 | Kelvin Cook
CIV-07 | CIV-07 | PI04719 | Verified | Cooling TWR PDC A/C Unit is damaged. | B | E | Shane Crowe | McD | 2019-09-03 | Shane Crowe | Const | 2020-02-27 | Michael Law | 2020-03-04 | Nelson Eichelberger
CIV-06 | CIV-06 | PI18636 | Verified | 1B Nooter Platform #40. Install ladder safety gate | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-06 | CIV-06 | PI18635 | Verified | 1B Nooter Platform #40. Install ladder base clips to Platform #2 grating. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-01 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18634 | Verified | 1B Nooter Platform #40. Weld handrail/midrail splices (2 loc). | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-01 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18633 | Verified | 1B Nooter Platform #50 (drum). Obstructions to either side of ladder do not meet minimum clear distance. 15 inches clear (from ladder centerline) to any obstruction. Ref: 1A-CAB-HTS-0314,(left) Conduit (right) | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2021-01-25 | Dave Goldak
CIV-06 | CIV-06 | PI18632 | Verified | 1B Nooter Platform #52. Weld handrail/midrail splice, southeast corner. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18631 | Verified | 1B HRSP IP Silencer #2 support. Tighten loose bolt connections at support base plate to structural steel. Southeast side of IP Steam drum. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-01 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-06 | CIV-06 | PI18630 | Verified | 1B Nooter Platform #7 (Drum). Weld handrail/midrail splices (2 loc). | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-01 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18629 | Verified | 1B Nooter Platform #39. Install ladder base clips to Platform #2 grating. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-01 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18628 | Verified | 1B Nooter Platform #39. Platform not bolted to PF#2 deck grating. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-01 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18627 | Verified | 1B Nooter Platform #39. Weld handrail/midrail splices (2 loc). | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-01 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18626 | Verified | 1B Nooter Platform #42. Install ladder base clips to Platform #2 grating. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18625 | Verified | 1B Nooter Platform #42. Weld handrail/midrail splices (2 loc). | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-01 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18624 | Verified | 1B Nooter Platform #44. Platform not in orientation shown on drawings. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-06 | CIV-06 | PI18623 | Verified | 1B Nooter Platform #44. Install ladder base to Platform #2 grating. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-01 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18622 | Verified | 1B Nooter Platform #44. Ladder attachment bolts are loose. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-01 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18621 | Verified | 1B Nooter Platform #44. Weld handrail/midrail splices (2 loc). | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-01 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18620 | Verified | 1B Nooter Platform #51. Weld caps on cut handrail post, north side of platform at valve handles. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18619 | Verified | 1B Nooter Platform #51. One loose ladder support bolt to Platform #2 connection. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18618 | Verified | 1B Nooter Platform #51. Weld handrail/midrail splices northeast and southeast corner of platform. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-08 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18617 | Verified | 1B Nooter Platform #6 (top). Minor housekeeping and debris removal. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-07-30 | Dave Goldak
CIV-06 | CIV-06 | PI18616 | Verified | 1B Nooter Platform #43 (top). Platform installation is incomplete. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18615 | Verified | 1B Nooter Platform #38 (top). Install east ladder and safety gate. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18614 | Verified | 1B Nooter Platform #38 (top). Connect west ladder base to Platform #3 grating. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-06 | CIV-06 | PI18613 | Verified | 1B Nooter Platform #38 (top). Bolt platform feet to Platform #3 grating. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2020-07-10 | Dave Goldak
CIV-07 | CIV-07 | PI14414 | Verified | CoolTwr Pump Deck: Grating at elev 509'-1.5" landing short at stairway. Missing abrasive nosing. | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2020-02-02 | Tim Gallegos | 2020-02-05 | Shannon Scott
CIV-07 | CIV-07 | PI14439 | Verified | PDC west stair: missing abrasive stair nosing at platform | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2020-01-09 | Tim Gallegos | 2020-01-17 | Shannon Scott
CIV-07 | CIV-07 | PI14440 | Verified | PDC south stair: missing abrasive stair nosing at platform | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2020-01-09 | Tim Gallegos | 2020-01-17 | Shannon Scott
CIV-07 | CIV-07 | PI14441 | Verified | PDC HVAC disconnects to be installed north and south | C | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const | 2020-03-31 | Matt Gilmore | 2020-07-22 | Dave Goldak
CIV-07 | CIV-07 | PI14442 | Verified | PDC exterior: Install GFCI receptacle north wall | D | E | Michael Law | McD | 2019-12-06 | Michael Law | Const | 2020-07-20 | Mike Tabbert | 2020-07-22 | Dave Goldak
CIV-07 | CIV-07 | PI14443 | Verified | PDC exterior: complete downspout connection to UG drains | C | S | Tim Gallegos | McD | 2019-12-06 | Tim Gallegos | Const | 2020-03-20 | Tim Gallegos | 2020-07-22 | Dave Goldak
CIV-07 | CIV-07 | PI14444 | Verified | PDC exterior: north guttering damaged or paint issue. | C | S | Tim Gallegos | McD | 2019-12-06 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-07-22 | Dave Goldak
CIV-07 | CIV-07 | PI14445 | Verified | PDC Handrail: Install straight and corner handrail splice couplings (all - south and east) | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2020-01-09 | Tim Gallegos | 2020-01-17 | Shannon Scott
CIV-07 | CIV-07 | PI14446 | Verified | PDC West door: Reinstall automatic door closer | C | S | Tim Gallegos | McD | 2019-12-06 | Tim Gallegos | Const | 2020-01-06 | Tim Gallegos | 2020-01-17 | Shannon Scott
CIV-07 | CIV-07 | PI14447 | Verified | PDC West door: Reinstall door threshold. | C | S | Tim Gallegos | McD | 2019-12-06 | Tim Gallegos | Const | 2020-01-06 | Tim Gallegos | 2020-01-17 | Shannon Scott
CIV-07 | CIV-07 | PI14448 | Verified | PDC Souh Door: Reinstall automatic door closer | C | S | Tim Gallegos | McD | 2019-12-06 | Tim Gallegos | Const | 2020-01-06 | Tim Gallegos | 2020-01-17 | Shannon Scott
CIV-07 | CIV-07 | PI15461 | Verified | Cooling tower PDC - Landing is not 3' from end of stairs - West stairs | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-07 | CIV-07 | PI15462 | Verified | Cooling Tower PDC - Install absrasive nosing on landing ( both stairs) | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-15 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-07 | CIV-07 | PI15463 | Verified | Cooling tower PDC - Stairs not compliant with 7" height | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-07 | CIV-07 | PI15464 | Verified | Cooling tower PDC - Handrail Not complete on south platform | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-15 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-07 | CIV-07 | PI15466 | Verified | CT Chem Feed - Repair concrete at ladder attachment | B | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Const | 2020-01-20 | Alan Huntsman | 2020-01-27 | Michael Law
CIV-07 | CIV-07 | PI15467 | Verified | CT Chem Feed - Repair concrete wall at handrail anchorage (2 location) | B | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Const | 2020-01-20 | Alan Huntsman | 2020-01-27 | Michael Law
CIV-07 | CIV-07 | PI15468 | Verified | CT Basin platform - Grating is not extended to flange at stair and nosing required | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-24 | Tim Gallegos | 2020-01-27 | Michael Law
CIV-07 | CIV-07 | PI15469 | Verified | CT Basin - Revise ladder per latest drawing | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-24 | Tim Gallegos | 2020-01-27 | Michael Law
CIV-07 | CIV-07 | PI15470 | Verified | CT Chem Feed - Toe Plate around equipment and conduits | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-03-09 | Tim Gallegos | 2020-03-11 | Michael Law
CIV-07 | CIV-07 | PI15471 | Verified | CT Chem Feed - Extend grating at Ladder | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-15 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-07 | CIV-07 | PI15472 | Verified | CT Chem Feed - cable tray - anchot bolts not tighten | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-15 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-07 | CIV-07 | PI15494 | Verified | CT PDC Cable tray - Cable support welded to bracing - Get Engineering approval | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-10 | Michael Law | 2020-01-10 | Michael Law
CIV-07 | CIV-07 | PI16546 | Verified | Complete cooling tower PDC downspouts. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-03-18 | Johnny Campbell | 2020-07-30 | Dave Goldak
CIV-07 | CIV-07 | PI16547 | Verified | Remove nails, wires & point & patch all PDC columns. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16548 | Verified | Remove nails, wires & point & patch all pads at the cooling tower PDC (stairs, transformers, cable tray foundation, etc). | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI16549 | Verified | Remove buried wood on the west side of the transformers south of the cooling tower PDC. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI16550 | Verified | Point & patch any over-bush-hammering on the cooling tower PDC grating supports. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI16551 | Verified | Complete all grading / stone surfacing. | C | C | Brooks Baker | McD | 2020-02-06 | Brooks Baker | Const | 2020-05-01 | Brooks Baker | 2020-08-05 | Dave Goldak
CIV-07 | CIV-07 | PI16552 | Verified | Remove all nails, wires, fill holes & point & patch all cooling tower basin walls. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16553 | Verified | Clean out cooling tower basin - west end, east of screens - elev. 480. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16554 | Verified | Re-caulk CJ on south cooling tower wall (near service air drop). | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16555 | Verified | Point & patch honeycombing on bypass saddles on south side of cooling tower basin. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI14415 | Verified | One broken stair nosing - stair pump deck (south). | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2020-01-02 | Tim Gallegos | 2020-01-17 | Shannon Scott
CIV-07 | CIV-07 | PI14416 | Verified | Several missing/broken fasteners - stair nosing - south pump deck. | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2020-01-15 | Tim Gallegos | 2020-02-05 | Shannon Scott
CIV-07 | CIV-07 | PI14417 | Verified | Ladder - north pump bay. Remove and reinstall per Detail A & Section 5-5. Install checker plate per detail. | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2020-03-12 | Johnny Campbell | 2020-03-12 | John Watts
CIV-07 | CIV-07 | PI14418 | Verified | Additional tray support tube steel added at W10 cantilever section between PDC and Cooling Tower. Patch paint welds. | C | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const | 2020-02-07 | Alan Huntsman | 2020-02-10 | Fred Michael
CIV-07 | CIV-07 | PI14419 | Verified | Grout cable tray support frame baseplates. Cooling Tower area tray supports between PDC and CoolTwr. 9 locations. | C | C | Johnny Campbell | McD | 2019-12-06 | Johnny Campbell | Const | 2019-12-11 | Jack White | 2020-01-06 | Shannon Scott
CIV-07 | CIV-07 | PI14420 | Verified | Missing and/or loose nuts on tray support baseplate anchor bolts between Chemical Storage and Cooling Twr. Three locations. | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2019-12-31 | Bobby Williams | 2020-01-07 | Shannon Scott
CIV-07 | CIV-07 | PI14421 | Verified | CoolTWR Chem Storage: Complete shed roofing, gutter, downspout | C | S | Sheri Fritz | MOO | 2019-12-06 | Sheri Fritz | Const | 2020-03-10 | Tim Mills | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI14422 | Verified | Cooling Tower Chem feed: Spalled concrete at southwest ladder anchorage to containment wall. | C | C | Johnny Campbell | McD | 2019-12-06 | Johnny Campbell | Const | 2019-12-12 | Jack Fields | 2020-01-06 | Shannon Scott
CIV-07 | CIV-07 | PI14423 | Verified | CoolingTwr Chemical: Missing (QTY=4) jamb nuts and (QTY=4) square plate washers at Sulfuric Tank Anchor bolts. | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2019-12-31 | Bobby Williams | 2020-01-07 | Shannon Scott
CIV-07 | CIV-07 | PI14424 | Verified | Cooling Tower Chem feed: Spalled concrete at southwest electrical anchorage to containment wall. Mortar rub. | C | C | Johnny Campbell | McD | 2019-12-06 | Johnny Campbell | Const | 2019-12-12 | Jack Fields | 2020-01-06 | Shannon Scott
CIV-07 | CIV-07 | PI14425 | Verified | Cooling Tower Chem feed: Damaged structural concrete at handrail anchorage, top of sodium hypochlorite containment. 2 Locations, west wall. | C | C | Alan Huntsman | McD | 2019-12-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2021-04-21 | John Watts
CIV-07 | CIV-07 | PI14426 | Verified | Cooling Twr Chem: Apply coating to bush-hammered tops of housekeeping and equipment pads | C | C | Johnny Campbell | McD | 2019-12-06 | Johnny Campbell | Const | 2020-04-08 | Johnny Campbell | 2020-04-24 | Mark Williamson
CIV-07 | CIV-07 | PI14427 | Verified | Cooling Tower Chem feed: Coating is chipping at center containment walls/curbs. | C | C | Sheri Fritz | BRA | 2019-12-06 | Sheri Fritz | Const | 2020-04-28 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI14428 | Verified | Cooling Twr Chem: Patch coating/liner in hypochlorite tank contain where holes were drilled in wrong location. | C | C | Alan Huntsman | McD | 2019-12-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI14429 | Verified | Cooling Tower Chem feed: Additional grating required to edge of support flange at ladder - Sulfuric Acid platform. | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2019-12-31 | Bobby Williams | 2020-01-07 | Dave Goldak
CIV-07 | CIV-07 | PI14430 | Verified | Cooling Tower Chem feed: Reinstall toeplate or banding at equiment and electrical penetrations thru grating - Sulfuric Acid platform. | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2020-02-02 | Tim Gallegos | 2020-02-05 | Shannon Scott
CIV-07 | CIV-07 | PI14431 | Verified | Cooling Tower Chem feed: Cold galv touch-up - east ladder support clips. | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2019-12-31 | Tim Gallegos | 2020-01-07 | Dave Goldak
CIV-07 | CIV-07 | PI14432 | Verified | Cooling Tower Chem feed: Northwest WT7 vertical brace is reversed. | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2020-02-05 | Tim Gallegos | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI14433 | Verified | Cooling Tower Chem feed: Southeast WT7 vertical brace is reversed. | C | S | Tim Gallegos | McD | 2019-12-06 | Tim Gallegos | Const | 2020-04-29 | Tim Gallegos | 2020-08-05 | Dave Goldak
CIV-07 | CIV-07 | PI14434 | Verified | Cooling Tower Chem feed: Missing grating clips, sulfuric acid skid platform. | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2019-12-31 | Tim Gallegos | 2020-01-07 | Dave Goldak
CIV-07 | CIV-07 | PI14435 | Verified | Cooling Tower Chem feed: Clean sandblast grit out of each sump. 5 locations. | C | C | Alan Huntsman | McD | 2019-12-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2021-02-01 | Dave Goldak
CIV-07 | CIV-07 | PI14436 | Verified | Cooling Tower Chem feed: Install grating clips to sump covers, 5 locations. | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2020-01-09 | Tim Gallegos | 2020-01-17 | Shannon Scott
CIV-07 | CIV-07 | PI14437 | Verified | Cooling Tower Chem feed: Minor clean-out of secondary containments. | C | C | Alan Huntsman | McD | 2019-12-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2021-02-01 | Dave Goldak
CIV-07 | CIV-07 | PI14438 | Verified | PDC west stair: Handrail supports bent and/or cracked, both sides. | C | S | Bobby Williams | McD | 2019-12-06 | Bobby Williams | Const | 2020-01-09 | Tim Gallegos | 2020-01-17 | Shannon Scott
CIV-07 | CIV-07 | PI16556 | Verified | Remove hoses inside the southeast end of the cooling tower basin. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16557 | Verified | Remove c-post & wood stake near 10-FPS-PIV-0250 at road across from the 1B HRSG PDC. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI16558 | Verified | Remove electrical cable at southeast corner of the cooling tower area near 10-FPS-PIV-0250 at road across from the 1B HRSG PDC. | C | C | Chris Colvin | McD | 2020-02-06 | Chris Colvin | Const | 2020-03-31 | Matt Gilmore | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI16559 | Verified | Re-caulk CJ on the cooling tower basin wall - north side, east of service air drop. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16560 | Verified | Point & patch at service air / service water support on the north side of the cooling tower basin. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16561 | Verified | Remove rebar (2) on the north side of the cooling tower basin. | C | E | Chris Colvin | McD | 2020-02-06 | Chris Colvin | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16562 | Verified | Remove ground cable on the north side of the cooling tower basin. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16563 | Verified | Remove sheet metal from cooling tower basin - northwest corner near chem feed pipe. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-06-16 | Dave Goldak
CIV-07 | CIV-07 | PI16564 | Verified | Remove wire & point & patch at the 2 foundations at the northeast corner of the cooling tower basin. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI16565 | Verified | Point & patch unused anchors & bolt holes at the sufuric acid containment wall. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16566 | Verified | Remove nails & wires & point & patch cooling tower chemical feed foundations. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16567 | Verified | Remove nails & point & patch northwest side of circ water pump foundation. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI16568 | Verified | Remove nails, wires & point & patch at north circ water pump stair landing. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16569 | Verified | Remove debris - spare elec cable from west side - grade elevation by circ water pump cable tray. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI16570 | Verified | Wire brush oxidation & cold gal. all structural hardware, anchor bolts, etc. | C | C | Johnny Campbell | McD | 2020-02-06 | Johnny Campbell | Const | 2020-04-23 | Johnny Campbell | 2020-04-24 | Mark Williamson
CIV-07 | CIV-07 | PI16571 | Verified | Surface stair pad on south side of circ water pumps needs prep seal work. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16572 | Verified | Stair nose fasterners need to be tightened down / replace missing on south side of circ water pumps | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-09 | Tim Gallegos | 2020-03-12 | John Watts
CIV-07 | CIV-07 | PI16573 | Verified | Cooling tower screen rails need to be cut flush with grating deck eliminating trip hazards. Point & patch. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-09 | Tim Gallegos | 2020-03-12 | John Watts
CIV-07 | CIV-07 | PI16574 | Verified | Point & patch concrete at top of ladder on north side of grating deck circ water pumps. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-14 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16575 | Verified | Grind & cold galv anchor holes on pipe support on north side circ water pump. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-20 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI16576 | Verified | Housekeeping needed on grating deck by circ water pumps. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-19 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16577 | Verified | Elevation 509 - stairs to platform between pumps missing abrasive nosing on treads. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-09 | Tim Gallegos | 2020-03-12 | John Watts
CIV-07 | CIV-07 | PI16578 | Verified | Grout welding receptacle stand at circ water pump area. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-19 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16579 | Verified | Grout stands under cooling tower PDC. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-19 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16580 | Verified | Remove backer rod at control joints at the cooling tower basin. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-19 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16581 | Verified | Caulk both sides of expansion joints at the cooling tower basin. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-02-19 | Alan Huntsman | 2020-03-04 | Dave Goldak
CIV-07 | CIV-07 | PI16582 | Verified | Investigate drain hub on south side of cooling tower PDC. | C | P | James Beech | McD | 2020-02-06 | James Beech | Const | 2020-04-06 | Michael Law | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI12698 | Verified | Need final cleaning inside Cooling Tower PDC enclosure. | C | E | Chris Colvin | McD | 2019-11-01 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-05-26 | Randy Carpenter
CIV-07 | CIV-07 | PI17749 | Verified | Replace bent grating clip. Cooling tower pump bay, southwest corner. | C | C | Tim Gallegos | McD | 2020-03-10 | Tim Gallegos | Const | 2020-05-07 | Tim Gallegos | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI17750 | Verified | Valve 10-RWS-V-0101: Insulation and cladding not installed properly. Prohibits valve operation. | C | Q | Sheri Fritz | PCI | 2020-03-10 | Sheri Fritz | Const | 2020-04-29 | Michael Law | 2020-06-03 | Dave Goldak
CIV-07 | CIV-07 | PI17847 | Verified | Cooling Tower Bleach Grating - The grating at the ladder between the pump containment and the tank containment on the cooling tower bleach tank is not flushed with the concrete. | C | C | Tim Gallegos | McD | 2020-03-16 | Tim Gallegos | Const | 2020-04-29 | Tim Gallegos | 2020-08-17 | Dave Goldak
CIV-07 | CIV-07 | PI18087 | Verified | There's a damaged step on the stairway located Plant South of the CW Discharge. Location: Stairway located Plant South of the CW Discharge (Adjacent to the Cooling Tower's West Stairway) | C | S | Tim Gallegos | McD | 2020-03-18 | Tim Gallegos | Comm | 2020-05-11 | Tim Gallegos | 2020-06-03 | John Watts
CIV-08 | CIV-08 | PI14870 | Verified | 10-MWS-JB-0310 - Below the Heater Control Junction Box, there's an area that creates fall hazard. | B | C | Bobby Williams | McD | 2019-12-24 | Bobby Williams | Comm |  |  | 2020-01-15 | Nelson Eichelberger
CIV-08 | CIV-08 | PI15514 | Verified | Disc Filter - Swing gate install - Inspection required | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-15 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-08 | CIV-08 | PI15515 | Verified | Circ Water Basin - First step conduit--- 3 1/2" behind rung - move ladder out to create 7” clear requirement to conduit | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-15 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-08 | CIV-08 | PI16702 | Verified | Service Water Area - point & patch pads for 10-SWS-P-0100A & B including drain hub at pump A. | C | C | Alan Huntsman | McD | 2020-02-13 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16703 | Verified | Service Water Area - Remove & patch bolts on east side of service water pump containment. | C | C | Alan Huntsman | McD | 2020-02-13 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16704 | Verified | Complete final grading. | C | C | Brooks Baker | McD | 2020-02-13 | Brooks Baker | Const | 2020-05-05 | Brooks Baker | 2021-04-21 | John Watts
CIV-08 | CIV-08 | PI16705 | Verified | Service Water Area - remove stake on east side of service water tank. | C | C | Johnny Campbell | McD | 2020-02-13 | Johnny Campbell | Const | 2020-05-21 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-08 | CIV-08 | PI16706 | Verified | Service Water Area - point & patch pad for 10-FPS-AOV-0100 (top & sides) north of service water tank. | C | C | Alan Huntsman | McD | 2020-02-13 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16707 | Verified | Service Water Area - patch service water tank foundation - north side near U/G pipe tie-in. | C | C | Johnny Campbell | McD | 2020-02-13 | Johnny Campbell | Const | 2020-05-21 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-08 | CIV-08 | PI16708 | Verified | Fire Pump House Area - point & patch where needed on the fire pump house foundation including unused anchor bolts. | C | C | Alan Huntsman | McD | 2020-02-13 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16709 | Verified | Fire Pump House Area - check on U/G stug up south of fire pump house - cap not correct size. | C | P | James Beech | McD | 2020-02-13 | James Beech | Const | 2020-05-07 | James Beech | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16710 | Verified | Oily Water Separator Area - point & patch bug holes on the OWS truck unloading curb. | C | C | Alan Huntsman | McD | 2020-02-13 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16711 | Verified | Batch Neutralization Area - remove nails, point & patch BNS ladder pad on north side. | C | C | Alan Huntsman | McD | 2020-02-13 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16712 | Verified | Finish stone grade - all areas. | C | C | Brooks Baker | McD | 2020-02-13 | Brooks Baker | Const | 2020-04-09 | Michael Law | 2020-04-09 | Michael Law
CIV-08 | CIV-08 | PI16713 | Verified | Batch Neutralization Area - patch BNS containment wall down to stone grade. | C | C | Johnny Campbell | McD | 2020-02-13 | Johnny Campbell | Const | 2020-04-01 | Johnny Campbell | 2020-04-28 | Mark Williamson
CIV-08 | CIV-08 | PI16714 | Verified | Batch Neutralization Area - patch damaged areas including pipe pentratings in the paint coating in the BNS containment. | C | C | Sheri Fritz | BRA | 2020-02-13 | Sheri Fritz | Const | 2020-04-28 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16715 | Verified | Batch Neutralization Area - patch pad for pipe support on the west side of WWT pumps. | C | C | Sheri Fritz | BRA | 2020-02-13 | Sheri Fritz | Const | 2020-04-28 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16716 | Verified | Batch Neutralization Area - point & patch all pipe support pads. | C | C | Johnny Campbell | McD | 2020-02-13 | Johnny Campbell | Const | 2020-04-01 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16717 | Verified | Batch Neutralization Area - point & patch the WWT pre-cast vault/sump. | C | C | Johnny Campbell | McD | 2020-02-13 | Johnny Campbell | Const | 2020-04-08 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16718 | Verified | Batch Neutralization Area - point & patch the BNS containment wall (all sides). | C | C | Johnny Campbell | McD | 2020-02-13 | Johnny Campbell | Const | 2020-04-01 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16719 | Verified | Batch Neutralization Area - apply coating on the WWT pump housekeeping pads. | C | C | Sheri Fritz | BRA | 2020-02-13 | Sheri Fritz | Const | 2020-04-28 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16720 | Verified | Batch Neutralization Area - apply coating to unused support holes in the WWT pump containment. | C | C | Sheri Fritz | BRA | 2020-02-13 | Sheri Fritz | Const | 2020-04-28 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16721 | Verified | Batch Neutralization Area - double nut anchor bolts on the BNS tanks. | C | M | Shane Crowe | McD | 2020-02-13 | Shane Crowe | Const | 2020-04-30 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16722 | Verified | Batch Neutralization Area - touch up the caulked control joints on the BNS tank containment walls. | C | C | Johnny Campbell | McD | 2020-02-13 | Johnny Campbell | Const | 2020-04-08 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16723 | Verified | Batch Neutralization Area - complete joint caulking on the north BNS containment wall. | C | C | Johnny Campbell | McD | 2020-02-13 | Johnny Campbell | Const | 2020-04-01 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16724 | Verified | Complete all paving. | C | C | Brooks Baker | BEA | 2020-02-13 | Brooks Baker | Const | 2020-08-05 | Jason Ezell | 2021-06-17 | John Watts
CIV-08 | CIV-08 | PI16725 | Verified | Make-up Water Chem. Feed Area - complete downspouts to drain hubs. If no drain hub - complete to 6" above grade. | C | C | Tim Gallegos | McD | 2020-02-13 | Tim Gallegos | Const |  |  | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16726 | Verified | Make-up Water Chem. Feed Area - install banding at grating cut-outs on the MW chem treatment platform. | C | S | Tim Gallegos | McD | 2020-02-13 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-08 | CIV-08 | PI16727 | Verified | Make-up Water Chem. Feed Area - extend grating to edge of beam at both ladders on the MW chem treatment platform. | C | S | Tim Gallegos | McD | 2020-02-13 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-08 | CIV-08 | PI16728 | Verified | Make-up Water Chem. Feed Area - cold galv all weld sports for cable tray supports & pipe hangers in the chemical feed structure. | C | P | James Beech | McD | 2020-02-13 | James Beech | Const | 2020-04-22 | James Beech | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16729 | Verified | Make-up Water Chem. Feed Area - complete caulking at ladder landing on the north side of the chemical treatment containment. | C | C | Alan Huntsman | McD | 2020-02-13 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-08 | CIV-08 | PI16816 | Verified | Need isolation joint between polymer foundation and the chemical feed containment. | C | C | Johnny Campbell | McD | 2020-02-14 | Johnny Campbell | Const | 2020-04-01 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-08 | CIV-08 | PI16817 | Verified | Caulk joint between polymer enclosure & pad on north side for 10-MWS-XFM-0001. | C | C | Brooks Baker | McD | 2020-02-14 | Brooks Baker | Const | 2020-04-01 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16818 | Verified | Thin set the bushed area at the polymer skid inside enclosure after commissioning cleans out enclosure. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16819 | Verified | Point & patch the perimeter of the polymer metering pump skid after commissioning cleans out enclosure. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16820 | Verified | Polymer enclosure - doors missing exit signs. | D | S | Charles Worthington | McD | 2020-02-14 | Charles Worthington | Const | 2020-05-11 | Michael Law | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16821 | Verified | Polymer enclosure - west door needs threshold. | C | C | Tim Gallegos | McD | 2020-02-14 | Tim Gallegos | Const | 2020-04-16 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16822 | Verified | Polymer enclosure - cauld threshold for north door. | C | C | Tim Gallegos | McD | 2020-02-14 | Tim Gallegos | Const | 2020-04-16 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16823 | Verified | Patch concrete at U/G pipe stub-up on the SE corner of the polymer enclosure. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16824 | Verified | Polymer enclosure - seal electrical penetrations (inside & outside). | C | E | Chris Colvin | McD | 2020-02-14 | Chris Colvin | Const | 2020-08-06 | Chris Colvin | 2020-10-06 | Dave Goldak
CIV-08 | CIV-08 | PI16825 | Verified | Polymer enclosure - seal under sill plate (perimeter). | C | C | Johnny Campbell | McD | 2020-02-14 | Johnny Campbell | Const | 2020-04-08 | Johnny Campbell | 2020-04-28 | Mark Williamson
CIV-08 | CIV-08 | PI16826 | Verified | Clarifier Caustic - extend downspouts to 6" above grade. | C | S | Sheri Fritz | MOO | 2020-02-14 | Sheri Fritz | Const | 2020-03-10 | Tim Mills | 2020-03-12 | John Watts
CIV-08 | CIV-08 | PI16827 | Verified | Clarifier Caustic structure - west vertical brace is installed backwards. | C | S | Tim Gallegos | McD | 2020-02-14 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-08 | CIV-08 | PI16828 | Verified | Clarifier Caustic platform - fill 5 holes in the grating & remove cut grating bar at the elec conduit penetration at north end. | C | S | Bobby Williams | McD | 2020-02-14 | Bobby Williams | Const | 2020-03-13 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16829 | Verified | Clarifier Disc Filter - touch up paint on guardrails. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-11 | Alan Huntsman | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16830 | Verified | Clarifier - remove rebar on east side at stair support pad. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16831 | Verified | Clarifier - cut off bolts on east side of wall above light. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16832 | Verified | Clarifier - seal all stub-ups at southeast corner. | C | E | Chris Colvin | McD | 2020-02-14 | Chris Colvin | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16833 | Verified | Clarifier - remove bolt & nails at top of stairs on east wall. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16834 | Verified | Top of Clarifier - excessive gaps between handrails. | C | S | Bobby Williams | McD | 2020-02-14 | Bobby Williams | Const | 2020-02-28 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16835 | Verified | Top of Clarifier - need toe board around Krebs cyclones. | C | S | Bobby Williams | McD | 2020-02-14 | Bobby Williams | Const | 2020-03-06 | Tim Gallegos | 2020-03-12 | John Watts
CIV-08 | CIV-08 | PI16836 | Verified | Top of Clarifier - cold galv rust spots on grating - north area by handrail. | C | C | Johnny Campbell | McD | 2020-02-14 | Johnny Campbell | Const | 2020-05-21 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-08 | CIV-08 | PI16837 | Verified | Top of Clarifier - grout support beams on top of clarifier wall. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-11 | Alan Huntsman | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16838 | Verified | Clairifer - need toe plate at 1st stair landing. | C | S | Bobby Williams | McD | 2020-02-14 | Bobby Williams | Const | 2020-02-28 | Tim Gallegos | 2020-03-09 | Dave Goldak
CIV-08 | CIV-08 | PI16839 | Verified | Clarifier - adjust bowed top plate at 1st stair landing. | C | S | Bobby Williams | McD | 2020-02-14 | Bobby Williams | Const | 2020-03-06 | Tim Gallegos | 2020-03-12 | John Watts
CIV-08 | CIV-08 | PI16840 | Verified | Filter Press area - point & patch the pre-cast sump vault tops. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16841 | Verified | Filter Press building - complete downspouts to drain hubs. | C | S | Sheri Fritz | MOO | 2020-02-14 | Sheri Fritz | Const | 2020-03-10 | Tim Mills | 2020-03-12 | John Watts
CIV-08 | CIV-08 | PI16842 | Verified | Filter Press building - point & patch at southwest filter press platform support. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16843 | Verified | Filter Press building - bolt handrails at joints / corners. | C | S | Bobby Williams | McD | 2020-02-14 | Bobby Williams | Const | 2020-03-12 | Bobby Williams | 2020-03-12 | John Watts
CIV-08 | CIV-08 | PI16844 | Verified | Filter Press building - grating uneven at north center area, northwest corner and southwest side. | C | S | Bobby Williams | McD | 2020-02-14 | Bobby Williams | Const | 2020-03-12 | Bobby Williams | 2020-03-12 | John Watts
CIV-08 | CIV-08 | PI16845 | Verified | Sludge Thickener Tank - need abrasive nosing at top of stairs. | C | S | Bobby Williams | McD | 2020-02-14 | Bobby Williams | Const | 2020-03-13 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16846 | Verified | Sludge Thickener Tank - point & patch foundation. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16847 | Verified | Sludge Thickener Tank - touch up paint needed. | C | C | Johnny Campbell | McD | 2020-02-14 | Johnny Campbell | Const | 2020-05-21 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-08 | CIV-08 | PI16848 | Verified | Filter Press Feed Pumps - install grating (at panels). | C | S | Bobby Williams | McD | 2020-02-14 | Bobby Williams | Const | 2020-03-13 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16849 | Verified | Filter Press Feed Pumps - point & patch on pump housekeeping pads. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16850 | Verified | Filter Press Feed Pumps - grid down the cut bolts & point & patch at northeast corner of containment wall. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16851 | Verified | Filter Press Chem. Feed Shed - complete roofing. | C | S | Sheri Fritz | MOO | 2020-02-14 | Sheri Fritz | Const | 2020-03-16 | Jerry Smith | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16852 | Verified | Filter Press Chem. Feed Shed - complete downspouts. | C | S | Sheri Fritz | MOO | 2020-02-14 | Sheri Fritz | Const | 2020-03-16 | Jerry Smith | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16853 | Verified | Remove T-post at northeast corner of Filter Press Chem. Feed containment. | C | C | Alan Huntsman | McD | 2020-02-14 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16854 | Verified | Cold galv embedded plates - West side of clarifier. Pipe/tray support beam removed. | C | C | Alan Huntsman | McD | 2020-02-17 | Alan Huntsman | Const | 2020-03-11 | Alan Huntsman | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI16855 | Verified | Add extension to bring inlet grate up to grade. Catch basin B-5 by clearwell. | C | S | Brooks Baker | McD | 2020-02-17 | Brooks Baker | Const | 2020-04-09 | Brooks Baker | 2020-04-28 | Mark Williamson
CIV-08 | CIV-08 | PI16856 | Verified | Filter Press enclosure: Field weld square upper plate washers to column baseplates. Minumum three sides each. QTY=24 locations. Per Anchor Bolt Schedule notes. | C | S | Bobby Williams | McD | 2020-02-17 | Bobby Williams | Const | 2020-03-13 | Tim Gallegos | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI17755 | Verified | Repair peeling concrete liner in Caustic Containment. | C | C | Sheri Fritz | BRA | 2020-03-10 | Sheri Fritz | Const | 2020-04-28 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI17756 | Verified | Repair chipped/peeling concrete liner in Coagulent Containment (two locations, west wall). | C | C | Alan Huntsman | McD | 2020-03-10 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI17757 | Verified | Repair chipped/peeling concrete liner in Hypochlorite (bleach) Containment (two locations, west wall). | C | C | Alan Huntsman | McD | 2020-03-10 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-19 | Dave Goldak
CIV-08 | CIV-08 | PI17758 | Verified | Remove unused unistruct support fame from southeast column, Caustic Storage Shed. | C | C | Johnny Campbell | McD | 2020-03-10 | Johnny Campbell | Const | 2020-05-21 | Johnny Campbell | 2020-05-26 | Dave Goldak
CIV-08 | CIV-08 | PI18147 | Verified | The Filter Press's temporary handrails hit the press when running. | C | M | Shane Crowe | McD | 2020-03-20 | Shane Crowe | Comm | 2020-04-30 | Tim Gallegos | 2020-06-03 | John Watts
CIV-09 | CIV-09 | PI00284 | Verified | Touch up exterior paint. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00285 | Verified | Remove tape for west wall above exterior door. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00286 | Verified | Tie site ground grid into building perimeter ground grid. | A | E | Shannon Savoy | McD | 2019-03-29 | Shannon Savoy | Const | 2019-04-01 | Shannon Savoy | 2019-04-03 | Mike Tabbert
CIV-09 | CIV-09 | PI00287 | Verified | Complete all outdoor lighting. | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-10 | Mike Tabbert
CIV-09 | CIV-09 | PI00288 | Verified | Complete functional test of all electrical and mechanical systems. | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-10 | Mike Tabbert
CIV-09 | CIV-09 | PI00289 | Verified | Provide certification of backflow preventer test. | B | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2020-01-09 | Sheri Fritz | 2020-01-09 | Michael Law
CIV-09 | CIV-09 | PI00290 | Verified | Flush potable water lines and provide certification. | B | P | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const |  |  | 2020-01-09 | Michael Law
CIV-09 | CIV-09 | PI00291 | Verified | Provide all completion forms and final permits. | B | M | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2020-03-05 | Michael Law | 2020-03-05 | Michael Law
CIV-09 | CIV-09 | PI00292 | Verified | Install all door closer arms. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-11 | Tim Mills | 2019-04-11 | Donovan Anderson
CIV-09 | CIV-09 | PI00293 | Verified | Clean smudge on wall over window in west vestibule. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-11 | Donovan Anderson
CIV-09 | CIV-09 | PI00294 | Verified | Perform "point up" in all rooms. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-11 | Donovan Anderson
CIV-09 | CIV-09 | PI00295 | Verified | Install threshold at the north control room door. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-11 | Donovan Anderson
CIV-09 | CIV-09 | PI00296 | Verified | Adjust control room floor tiles - check for tile not fully set. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-11 | Donovan Anderson
CIV-09 | CIV-09 | PI00297 | Verified | Install all window blinds. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-11 | Donovan Anderson
CIV-09 | CIV-09 | PI00298 | Verified | Replace rusted hardware on stoop canopies. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-05-01 | Neil Simon
CIV-09 | CIV-09 | PI00299 | Verified | Complete all concrete work for building (stoop pads, gutters, sidewalks etc.). | A | C | Johnny Campbell | McD | 2019-03-29 | Johnny Campbell | Const | 2019-07-16 | Johnny Campbell | 2019-11-19 | Michael Law
CIV-09 | CIV-09 | PI00300 | Verified | Clean bottom half of the building exterior after rock has been installed. | A | C | Johnny Campbell | McD | 2019-03-29 | Johnny Campbell | Const | 2019-07-16 | Johnny Campbell | 2019-07-17 | Michael Law
CIV-09 | CIV-09 | PI00301 | Verified | Clean bottom building exterior - approx. 4 ft. & up. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-06-24 | Michael Law
CIV-09 | CIV-09 | PI00302 | Verified | Cover the 1x4 wood at the bottom of the HVAC units with sheet metal. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-11 | Tim Mills | 2019-04-24 | Michael Law
CIV-09 | CIV-09 | PI00303 | Verified | Install vent on HVAC condensate drain. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-24 | Michael Law
CIV-09 | CIV-09 | PI00304 | Verified | Install any missing plugs on the HVAC units. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-24 | Michael Law
CIV-09 | CIV-09 | PI00305 | Verified | Install tags on outside panels on west side of building. | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-12 | Bernard Stasse
CIV-09 | CIV-09 | PI00306 | Verified | Check HVAC grills for bowing. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-11 | Donovan Anderson
CIV-09 | CIV-09 | PI00307 | Verified | Flatten down HVAC curbing. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-11 | Donovan Anderson
CIV-09 | CIV-09 | PI00308 | Verified | Caulk top of vertical run PVC at the 4 exterior corners of the building. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-11 | Tim Mills | 2019-04-24 | Michael Law
CIV-09 | CIV-09 | PI00309 | Verified | Caulking needed above east door. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-11 | Donovan Anderson
CIV-09 | CIV-09 | PI00310 | Verified | Complete low voltage system for HVAC Unit (condulet covers) | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-08 | Mike Tabbert
CIV-09 | CIV-09 | PI00311 | Verified | Vent on south side of building needs a gooseneck & birdscreen. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-11 | Donovan Anderson
CIV-09 | CIV-09 | PI00312 | Verified | Disconnect Switches at HVAC need to be tagged and energized. | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const |  |  | 2019-04-08 | Mike Tabbert
CIV-09 | CIV-09 | PI00313 | Verified | Properly secure baseboard to wall at Office South wall. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00314 | Verified | Add Support to drop ceiling at supply air vent in Office. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00315 | Verified | Repair caulking around the inside South entry door inside. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00316 | Verified | Seal around GFCI receptical in Women's bathroom | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00317 | Verified | Seal around GFCI receptical in Men's bathroom. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00318 | Verified | Complete Insulation at Hot Water line in Men's bathroom. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00319 | Verified | Touch up Paint at Suspended Ceiling Wall support at Southwest corner of Kitchen. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00320 | Verified | Clean Paint of all receptical and lighting covers. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-11 | Tim Mills | 2019-04-23 | Neil Simon
CIV-09 | CIV-09 | PI00321 | Verified | Touch up paint at Window well in Kitchen. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00322 | Verified | Remove paint from all Glazing. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00323 | Verified | Seal of Baseboard at Kitchen pass through. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-11 | Tim Mills | 2019-04-23 | Neil Simon
CIV-09 | CIV-09 | PI00324 | Verified | Replace damaged tile in Janitor's closet. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00325 | Verified | Install all fire exstigushers | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00326 | Verified | Counter top cabinet door damaged at first door of lower cabinet closes to Janitor's closet. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00327 | Verified | Repair damage to wall at South wall next to double door. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00328 | Verified | Damage on wood door in vestibule. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00329 | Verified | Remove plastic from beyween floor panels under desk on west wall near double doors (2 locations). | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00330 | Verified | Ceiling panels pushed up in LAN room. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00331 | Verified | Install cove for Back flow preventor in LAN room. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00332 | Verified | Repair floor at 3 locations on Southeast wall in DCS room. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00333 | Verified | Repair floor at 2 locations on North and Northeast wall in DCS room. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00334 | Verified | Adjust flooring in DCS room behind DCS cabinets. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00335 | Verified | Final finish missing od 4" concrete lip under West window. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00336 | Verified | Repair scratch on window well at West window. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00337 | Verified | Repair scratch on door to Electrical. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00338 | Verified | Repair base board behind transformer in Southwest corner of Electrical room. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00339 | Verified | Trim around conduits penetrating ceiling in Electrical room. | A | C | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-09 | Neil Simon
CIV-09 | CIV-09 | PI00340 | Verified | Install sanitary drains | A | P | Kelvin Cook | McD | 2019-03-29 | Kelvin Cook | Const | 2019-06-24 | Michael Law | 2019-07-24 | Shannon Scott
CIV-09 | CIV-09 | PI00341 | Verified | Blank covers on all electrical junction boxes | A | E | Sheri Fritz | JAN | 2019-03-29 | Sheri Fritz | Const | 2019-04-15 | Ed Gober | 2019-04-15 | Bernard Stasse
CIV-09 | CIV-09 | PI00342 | Verified | Label disconnect switch in kitchen closet | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-12 | Bernard Stasse
CIV-09 | CIV-09 | PI00343 | Verified | Fix receptaclce in kitchen closet | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-08 | Mike Tabbert
CIV-09 | CIV-09 | PI00344 | Verified | Receptacle in men bathroom is crooked | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-08 | Mike Tabbert
CIV-09 | CIV-09 | PI00345 | Verified | Update panelboard schedules in panelboards, wire tags on cables in panelboards in the electrical room. | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-11 | Tim Mills | 2019-06-13 | Mike Tabbert
CIV-09 | CIV-09 | PI00346 | Verified | Bolt down transformers in electrical room | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-08 | Mike Tabbert
CIV-09 | CIV-09 | PI00347 | Verified | Verify all receptacles are polarity checked | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-10 | Mike Tabbert
CIV-09 | CIV-09 | PI00348 | Verified | Check angle of all emergency lights | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-10 | Mike Tabbert
CIV-09 | CIV-09 | PI00349 | Verified | Kill power and check Exit and emergency lights | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-10 | Mike Tabbert
CIV-09 | CIV-09 | PI00350 | Verified | Exterior ground on seal tight connectors in electrical room | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-07-19 | Luis Cantu | 2019-07-19 | Mike Tabbert
CIV-09 | CIV-09 | PI00351 | Verified | Tighten all seal tight connectors in electrical room | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-04 | Tim Mills | 2019-04-08 | Mike Tabbert
CIV-09 | CIV-09 | PI00352 | Verified | Clean paint off all receptacle and switch coverss | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-05-24 | Mike Tabbert
CIV-09 | CIV-09 | PI00353 | Verified | Install Exit light in operating room | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-05-24 | Mike Tabbert
CIV-09 | CIV-09 | PI00354 | Verified | Remove scratches on panelboard on the southwest side of electrical room | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-04-09 | Tim Mills | 2019-04-10 | Mike Tabbert
CIV-09 | CIV-09 | PI00355 | Verified | Receptacles missing identification tags | A | E | Sheri Fritz | MOO | 2019-03-29 | Sheri Fritz | Const | 2019-05-16 | Mike Tabbert | 2019-05-16 | Mike Tabbert
CIV-09 | CIV-09 | PI00968 | Verified | "Admin Building Roof Drains to CB RFI-119-PI-009 Material on 15-FR-00063" | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-06-28 | Terry Deaton | 2019-07-19 | Justin Houdeshell
CIV-09 | CIV-09 | PI15562 | Verified | Control Room - The plant north door in the control room is shutting too hard. Malfunctioning door | C | C | Tim Gallegos | MOO | 2020-01-08 | Tim Gallegos | Comm |  |  | 2020-01-15 | Nelson Eichelberger
CIV-09 | CIV-09 | PI18069 | Verified | The awning on the control room is bent. Location: Plant East | C | C | Josh Koerner | MOO | 2020-03-18 | Josh Koerner | Comm | 2020-06-18 | Josh Koerner | 2020-07-29 | John Watts
CIV-09 | CIV-09 | PI18112 | Verified | Control Room - The control room has several ceiling leaks. | C | C | Josh Koerner | MOO | 2020-03-20 | Josh Koerner | Comm | 2020-06-18 | Josh Koerner | 2020-07-29 | John Watts
CIV-09 | CIV-09 | PI18123 | Verified | Control Room HVAC has failed the past two days. Currently, it is 76 degrees in the LAN and DCS Cabinet Room. | C | C | Sheri Fritz | MOO | 2020-03-20 | Sheri Fritz | Comm | 2020-04-28 | Michael Law | 2020-04-30 | John Watts
CIV-10 | CIV-10 | PI00535 | Verified | Finish base course paving. | A | C | Sheri Fritz | PSC | 2019-04-15 | Sheri Fritz | Const | 2019-05-08 | Michael Law | 2019-05-08 | Michael Law
CIV-10 | CIV-10 | PI00536 | Verified | Install all Man door landings. | A | C | Jessie Pipes | McD | 2019-04-15 | Jessie Pipes |  |  |  | 2019-04-15 | Ed Gober
CIV-10 | CIV-10 | PI00538 | Verified | Install all Man door landings. | A | C | Johnny Campbell | McD | 2019-04-15 | Johnny Campbell | Const | 2019-06-24 | Johnny Campbell | 2019-06-24 | Neil Simon
CIV-10 | CIV-10 | PI00539 | Verified | Install Ramps and Bollards at Roll up doors. | A | C | Johnny Campbell | McD | 2019-04-15 | Johnny Campbell | Const | 2019-06-24 | Johnny Campbell | 2019-06-24 | Neil Simon
CIV-10 | CIV-10 | PI00540 | Verified | Remove Forms from Curbs . | A | C | Jessie Pipes | McD | 2019-04-15 | Jessie Pipes | Const | 2019-04-15 | Jessie Pipes | 2019-04-15 | Neil Simon
CIV-10 | CIV-10 | PI00541 | Verified | Connect Downcommers to Drain lines. | C | C | Tim Gallegos | McD | 2019-04-15 | Tim Gallegos | Const | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
CIV-10 | CIV-10 | PI00542 | Verified | Rub down exterior walls and repair Tie holes/Tie wires. | A | C | Johnny Campbell | McD | 2019-04-15 | Johnny Campbell | Const | 2019-09-04 | Johnny Campbell | 2019-11-19 | Michael Law
CIV-10 | CIV-10 | PI00543 | Verified | Caulk expansion Joint at Northwest corner. | A | C | Johnny Campbell | McD | 2019-04-15 | Johnny Campbell | Const | 2019-09-04 | Johnny Campbell | 2019-11-19 | Michael Law
CIV-10 | CIV-10 | PI00544 | Verified | Remove rebar from South Overhead door entrance and repair concrete. | A | C | Johnny Campbell | McD | 2019-04-15 | Johnny Campbell | Const | 2019-07-24 | Jack Fields | 2019-11-19 | Michael Law
CIV-10 | CIV-10 | PI00546 | Verified | Install Cable Tray throughout building. | A | E | Dustin Futrell | McD | 2019-04-15 | Dustin Futrell | Const | 2019-07-19 | Luis Cantu | 2019-11-19 | Michael Law
CIV-10 | CIV-10 | PI00548 | Verified | Seal all exterior penetration of conduit. | A | E | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-15 | Tim Mills | 2019-04-15 | Neil Simon
CIV-10 | CIV-10 | PI00549 | Verified | Install all exterior receptacles. | A | E | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-15 | Tim Mills | 2019-04-15 | Neil Simon
CIV-10 | CIV-10 | PI00550 | Verified | Run Lightning protection down from roof to grounding grid at Southeast corner. | A | E | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-05-06 | Tim Mills | 2019-05-06 | Neil Simon
CIV-10 | CIV-10 | PI00551 | Verified | Grout bolt pocket under columns. Dry pack was used. | A | C | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-15 | Tim Mills | 2019-04-15 | Neil Simon
CIV-10 | CIV-10 | PI00552 | Verified | Install Digital lighting control panel. | A | E | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00553 | Verified | Ground Structural Steel. | A | E | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-15 | Tim Mills | 2019-04-15 | Neil Simon
CIV-10 | CIV-10 | PI00554 | Verified | Provide 4/0 Ground to all Panels and transformer to the grounding loop per Drawing E301. | A | E | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-15 | Tim Mills | 2019-04-15 | Neil Simon
CIV-10 | CIV-10 | PI00555 | Verified | Install equipment Grounding Bus. | A | E | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00556 | Verified | Clean all dirt and mud from Structural Steel. | A | C | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00557 | Verified | Secure Sill to Curb where required at Curbs that were poured after erection of walls. | A | C | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00558 | Verified | Install all Doors at Man door openings and Hardware. | A | C | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00559 | Verified | Complete Coatings where required. | A | C | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-05-06 | Tim Mills | 2019-05-06 | Neil Simon
CIV-10 | CIV-10 | PI00603 | Verified | Patch demin. bldg. concrete floor - various spots. | B | C | Johnny Campbell | McD | 2019-04-15 | Johnny Campbell | Const | 2019-10-08 | Johnny Campbell | 2019-10-15 | Shannon Scott
CIV-10 | CIV-10 | PI00604 | Verified | General clean-up needed when all work in bldg. is complete. | B | C | Johnny Campbell | McD | 2019-04-15 | Johnny Campbell | Const | 2019-10-08 | Johnny Campbell | 2019-10-15 | Shannon Scott
CIV-10 | CIV-10 | PI00605 | Verified | Remove temporary lights in bldg. | B | E | Luis Cantu | McD | 2019-04-15 | Luis Cantu | Const | 2019-06-21 | Luis Cantu | 2019-07-11 | Shannon Scott
CIV-10 | CIV-10 | PI00606 | Verified | Install all fire extinguishers. | A | C | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00607 | Verified | Adjust exit lights. | A | E | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00608 | Verified | Rub down curbs & patch nail holes - SE corner interior. | B | C | Johnny Campbell | McD | 2019-04-15 | Johnny Campbell | Const | 2019-08-19 | Jack Fields | 2019-11-19 | Michael Law
CIV-10 | CIV-10 | PI00609 | Verified | Remove concrete from conduits - SE corner interior. | B | C | Johnny Campbell | McD | 2019-04-15 | Johnny Campbell | Const | 2019-07-25 | Jack Fields | 2019-11-19 | Michael Law
CIV-10 | CIV-10 | PI00610 | Verified | Remove insulation from heater - SE corner interior. | A | C | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00611 | Verified | Repair concrete floor surface at SE corner interior. | B | C | Johnny Campbell | McD | 2019-04-15 | Johnny Campbell | Const | 2019-09-04 | Johnny Campbell | 2019-11-19 | Michael Law
CIV-10 | CIV-10 | PI00612 | Verified | Remove C-clamp in ceiling beam. | B | S | Robert Risher | McD | 2019-04-15 | Robert Risher | Const | 2019-06-03 | Tim Gallegos | 2019-07-11 | Shannon Scott
CIV-10 | CIV-10 | PI00613 | Verified | Remove packing list from purlin brace - west wall. | A | C | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00614 | Verified | Screen latches missing from 2 exhaust fans 10-HVA-EFN-2003 & 2004 - north wall. | A | M | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-05-24 | Tim Mills | 2019-05-24 | Neil Simon
CIV-10 | CIV-10 | PI00615 | Verified | Add supports for conduit on north wall. | A | E | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00616 | Verified | Tighten loose bolts on girt on north wall. | A | S | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-05-24 | Tim Mills | 2019-05-24 | Neil Simon
CIV-10 | CIV-10 | PI00617 | Verified | Bolt missing at girt / beam connection at the NE corner. | A | S | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-05-06 | Tim Mills | 2019-05-06 | Neil Simon
CIV-10 | CIV-10 | PI00618 | Verified | Support conduit above roll up door. | A | E | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00619 | Verified | Install external sealtite ground at panel 10-ESL-PNL-0003 - east wall. | A | E | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00620 | Verified | Complete all light switches. | A | E | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00621 | Verified | Replace rusted hardware on door canopies. | A | S | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00622 | Verified | Touch up paint needed on all door canopies. | A | S | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2020-01-15 | Tim Mills | 2020-01-29 | Michael Law
CIV-10 | CIV-10 | PI00623 | Verified | Remove shims & complete caulking on south door. | A | S | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00624 | Verified | Install glazing on south door. | A | S | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00625 | Verified | Redo cad shots for lightning protection at the SE corner. | A | E | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-05-06 | Tim Mills | 2019-07-15 | Fred Michael
CIV-10 | CIV-10 | PI00626 | Verified | Bottom trim piece of exterior panel missing at the NW corner. | A | S | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-05-06 | Tim Mills | 2019-05-06 | Neil Simon
CIV-10 | CIV-10 | PI00627 | Verified | Replace broken screws on bottom trim piece on west ext. wall. | A | S | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-04-24 | Tim Mills | 2019-04-24 | Neil Simon
CIV-10 | CIV-10 | PI00628 | Verified | Complete bottom trim on north ext. wall. | A | S | Sheri Fritz | MOO | 2019-04-15 | Sheri Fritz | Const | 2019-05-06 | Tim Mills | 2019-05-06 | Neil Simon
CIV-10 | CIV-10 | PI00892 | Verified | Install all bollards in the fire pump house area. | C | C | Jerry Smith | McD | 2019-05-01 | Jerry Smith | Const | 2019-09-06 | Jerry Smith | 2019-09-11 | Nelson Eichelberger
CIV-10 | CIV-10 | PI00984 | Verified | Install grating Demin Water Pump Foundation | B | P | Tim Gallegos | McD | 2019-05-06 | Tim Gallegos | Const | 2019-07-23 | Tim Gallegos | 2019-10-03 | Kelvin Cook
CIV-10 | CIV-10 | PI00987 | Verified | Install grating Waste Water Unloading | B | C | Bobby Williams | McD | 2019-05-06 | Bobby Williams | Const | 2019-07-26 | Tim Gallegos | 2019-10-03 | Kelvin Cook
CIV-10 | CIV-10 | PI15428 | Verified | Demin Building - Anchor wash plate weld are not complete - washer plate missing at some locations | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-30 | Tim Gallegos | 2020-04-30 | Michael Law
CIV-10 | CIV-10 | PI15495 | Verified | Demin Building - Stairs exceeds height limit ( add one more step at concrete level) | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-04 | Tim Gallegos | 2020-05-07 | Michael Law
CIV-10 | CIV-10 | PI15504 | Verified | Demin Bldg - Bending around pipe at stel overs | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-10 | CIV-10 | PI15505 | Verified | Demin Bldg - Flip Grating panel - installed incorrectly | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-10 | CIV-10 | PI15506 | Verified | Demin Bldg - New Equipment Ladder does not meet headroom requirement or step over requirement | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-10 | CIV-10 | PI15507 | Verified | Demin Tank - Did Not Climb - ladder is OSHA compliant - equiped with SAF-T-CLIMB system and compatible harness equipment | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const |  |  | 2020-01-10 | Michael Law
CIV-10 | CIV-10 | PI15508 | Verified | Demin Tank - Did Not Climb - ladder is OSHA compliant - equiped with SAF-T-CLIMB system and compatible harness equipment | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const |  |  | 2020-01-10 | Michael Law
CIV-10 | CIV-10 | PI15509 | Verified | Oily Water Seperator - Insufficent gap on upper hand rails - modify ladder brackets to move ladder outward and create clearance or eliminate due to infrequent access | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-27 | Tim Gallegos | 2020-01-29 | Michael Law
CIV-10 | CIV-10 | PI15512 | Verified | Bleach Tank - Installation Complete - inspection required | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const |  |  | 2020-01-10 | Michael Law
CIV-10 | CIV-10 | PI15513 | Verified | Coagulant Tank - Installation Complete - inspection required | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const |  |  | 2020-01-10 | Michael Law
CIV-10 | CIV-10 | PI17313 | Verified | Demin Bldg: Remove ladder and anchor bolts on east end of RO unit. Not OSHA compliant. Platform to remain. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-10 | CIV-10 | PI17314 | Verified | Demin Bldg: Grout pad on east end of RO unit. | C | C | Johnny Campbell | McD | 2020-02-28 | Johnny Campbell | Const | 2020-04-02 | Johnny Campbell | 2020-04-28 | Mark Williamson
CIV-10 | CIV-10 | PI17731 | Verified | Demin Building: Terminate gutter downspouts to underground drain piping. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-10 | CIV-10 | PI17732 | Verified | Demin Building: Install flashing around pipe penetrations, northeast corner of building. | C | P | Bobby Williams | McD | 2020-03-06 | Bobby Williams | Const | 2020-03-31 | Bobby Williams | 2020-05-21 | Dave Goldak
CIV-10 | CIV-10 | PI17733 | Verified | Demin Building: Install flashing around pipe penetrations, southwest corner of building. | C | P | Bobby Williams | McD | 2020-03-06 | Bobby Williams | Const | 2020-03-31 | Bobby Williams | 2020-05-21 | Dave Goldak
CIV-10 | CIV-10 | PI17734 | Verified | Demin Building: Install flashing around pipe penetrations, east side of building (2 locations). | C | P | Bobby Williams | McD | 2020-03-06 | Bobby Williams | Const | 2020-03-31 | Bobby Williams | 2020-05-21 | Dave Goldak
CIV-10 | CIV-10 | PI17735 | Verified | Demin Building: Remove nails, point and patch south door stoop concrete slab | C | C | Alan Huntsman | McD | 2020-03-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-21 | Dave Goldak
CIV-10 | CIV-10 | PI17736 | Verified | Demin Building: Complete stone surfacing and backfill around building perimeter | C | C | Brooks Baker | McD | 2020-03-06 | Brooks Baker | Const | 2020-04-01 | Brooks Baker | 2020-05-21 | Dave Goldak
CIV-10 | CIV-10 | PI17737 | Verified | Demin Building: Complete asphalt to door aprons | C | C | Sheri Fritz | BEA | 2020-03-06 | Sheri Fritz | Const | 2020-04-28 | Michael Law | 2020-05-21 | Dave Goldak
CIV-10 | CIV-10 | PI17738 | Verified | Demin Building: Finish door hardware east door. Missing lock cylinder | C | S | Sheri Fritz | ITS | 2020-03-06 | Sheri Fritz | Const | 2020-04-28 | Mike Tabbert | 2020-05-21 | Dave Goldak
CIV-10 | CIV-10 | PI17739 | Verified | Demin Building: Install square plate washers to building column baseplates (where missing). Weld plate washers er anchor bolt schedule instructions (3-sided) | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-10 | CIV-10 | PI17740 | Verified | Demin Building: Adjust southwest Ventilation Louver so blades fully close. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-11 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-10 | CIV-10 | PI17741 | Verified | Demin Building: Straighten bent frame at ventilation louver, south wall, east of door. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-07 | Tim Gallegos | 2020-05-21 | Dave Goldak
CIV-10 | CIV-10 | PI17742 | Verified | Demin Building: Patch chips and damaged sections of coating at chem tote storage area. | C | C | Sheri Fritz | BRA | 2020-03-06 | Sheri Fritz | Const | 2020-04-28 | Johnny Campbell | 2020-05-21 | Dave Goldak
CIV-10 | CIV-10 | PI17743 | Verified | Demin Building: Reinstall missing grating clips, chem tote storage grating. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-04-30 | Tim Gallegos | 2020-05-21 | Dave Goldak
CIV-10 | CIV-10 | PI17744 | Verified | Demin Building: Add top stair treads at top of concrete elevation for each assembly to chem tote storage elevation. Does not meet standard (gap between stair tread and landing) . | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-04 | Tim Gallegos | 2020-05-21 | Dave Goldak
CIV-10 | CIV-10 | PI17745 | Verified | Demin Building: Turn one grating panel over so that serrated edges are exposed. Install clips. North end of chem tote storage area. | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-10 | CIV-10 | PI17746 | Verified | Demin Building: Remove wood from subgrade, east side of south concrete door stoop. | C | C | Alan Huntsman | McD | 2020-03-06 | Alan Huntsman | Const | 2020-03-13 | Johnny Campbell | 2020-05-21 | Dave Goldak
CIV-10 | CIV-10 | PI17747 | Verified | Demin Building: Install grates or covers over unused floor hub drains | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Const | 2020-08-06 | Tim Gallegos | 2021-04-21 | John Watts
CIV-10 | CIV-10 | PI17748 | Verified | Demin Building: Complete wire terms - northeast unit heater 10-HVA-UHE-2103 | C | E | Sheri Fritz | MOO | 2020-03-06 | Sheri Fritz | Const | 2020-04-28 | Michael Law | 2020-05-21 | Dave Goldak
CIV-10 | CIV-10 | PI18068 | Verified | The grating near the chemical skids in the Demin Building are not flushed and creates a trip hazard. | C | C | Tim Gallegos | McD | 2020-03-18 | Tim Gallegos | Comm | 2020-06-08 | Tim Gallegos | 2021-04-21 | John Watts
CIV-10 | CIV-10 | PI18077 | Verified | Demin Building's Stairs to Chemical Skids - All six (6) stairs to the totes have a 6" opening from the step to the concrete. Refer to NFPA 101-722361 and NFPA 101-722364. | C | C | Tim Gallegos | McD | 2020-03-18 | Tim Gallegos | Comm | 2020-05-04 | Tim Gallegos | 2020-07-27 | Dave Goldak
CIV-11 | CIV-11 | PI15449 | Verified | Ammonia - Flip the safety gate to allow min. 18" from laddeter rung to opening | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-15 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-11 | CIV-11 | PI15450 | Verified | Ammonia - complete welding on handrail | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-15 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-11 | CIV-11 | PI15451 | Verified | Ammonia - top rung is 4" above Tank Landing, Extend grating at landing on lower platform | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-03-09 | Tim Gallegos | 2020-04-02 | Michael Law
CIV-11 | CIV-11 | PI15586 | Verified | Repair cracked grout at SE corner of 'A' Fuel Gas Filter Separator | C | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-05-27 | Dave Goldak
CIV-11 | CIV-11 | PI15587 | Verified | Surface of A & B Fuel Gas Filter Separator concrete pad foundation needs to be refinished. Apply finish to surfaces damaged by bush hammer and not grouted. | C | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Comm | 2020-02-19 | Alan Huntsman | 2020-02-25 | Keith Pollock
CIV-11 | CIV-11 | PI15589 | Verified | Remove unused base plate for vertical stanchion at W side of 10-FGS-T0205; Fuel Gas Filter Separator Drains Tank. Remove unused grout and trim anchors flush to grade. | C | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Comm | 2020-02-19 | Alan Huntsman | 2020-02-25 | Keith Pollock
CIV-11 | CIV-11 | PI16521 | Verified | Grind down bolts protuding on south wall & west wall. Point & patch. | C | C | Alan Huntsman | McD | 2020-02-04 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-20 | Dave Goldak
CIV-11 | CIV-11 | PI16522 | Verified | Steps to the aqueous ammonia skid are not equal. Bottom is 8 1/2", all others are 7". | C | S | Bobby Williams | McD | 2020-02-04 | Bobby Williams | Const | 2020-02-18 | Bobby Williams | 2020-02-25 | Keith Pollock
CIV-11 | CIV-11 | PI16523 | Verified | Need grating clips at top of stairs / all south area of Aqueous Ammoia skid. | C | S | Bobby Williams | McD | 2020-02-04 | Bobby Williams | Const | 2020-02-18 | Bobby Williams | 2020-02-25 | Keith Pollock
CIV-11 | CIV-11 | PI16524 | Verified | Fill / repair hole in grating on west side of Aqueous Ammonia Skid, north of panel 10-DWS-H-0002. | C | S | Bobby Williams | McD | 2020-02-04 | Bobby Williams | Const | 2020-02-18 | Bobby Williams | 2020-02-25 | Keith Pollock
CIV-11 | CIV-11 | PI16525 | Verified | Extend grating to over the beam under gate / ladder to containment. | C | S | Bobby Williams | McD | 2020-02-04 | Bobby Williams | Const | 2020-02-18 | Bobby Williams | 2020-02-25 | Keith Pollock
CIV-11 | CIV-11 | PI16526 | Verified | Point & patch on Aqueous Ammonia Tank south saddle. | C | C | Alan Huntsman | McD | 2020-02-04 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-20 | Dave Goldak
CIV-11 | CIV-11 | PI16527 | Verified | Complete final grading. | C | C | Brooks Baker | McD | 2020-02-04 | Brooks Baker | Const | 2020-05-13 | Brooks Baker | 2020-08-05 | Dave Goldak
CIV-11 | CIV-11 | PI16528 | Verified | Complete paving. | C | C | Sheri Fritz | McD | 2020-02-04 | Sheri Fritz | Const | 2020-04-28 | Michael Law | 2020-08-05 | Dave Goldak
CIV-11 | CIV-11 | PI16529 | Verified | Aqueous Ammonia Tank platform - ladder top rung should be even with deck. | C | S | Bobby Williams | McD | 2020-02-04 | Bobby Williams | Const | 2020-02-18 | Bobby Williams | 2020-02-25 | Keith Pollock
CIV-11 | CIV-11 | PI16530 | Verified | Aqueous Ammonia Tank platform - ladder top rail extensions are not "graspable". | C | S | Bobby Williams | McD | 2020-02-04 | Bobby Williams | Const | 2020-02-18 | Bobby Williams | 2020-02-25 | Keith Pollock
CIV-11 | CIV-11 | PI16531 | Verified | Aqueous Ammonia Tank platform - ladder top rail extensions are too narrow - need 24" minimum. | C | S | Bobby Williams | McD | 2020-02-04 | Bobby Williams | Const | 2020-02-18 | Bobby Williams | 2020-02-25 | Keith Pollock
CIV-11 | CIV-11 | PI16532 | Verified | Aqueous Ammonia Tank platform - east side - repair mid-rail that has been cut for pipe. | C | S | Bobby Williams | McD | 2020-02-04 | Bobby Williams | Const | 2020-02-18 | Bobby Williams | 2020-02-25 | Keith Pollock
CIV-11 | CIV-11 | PI16533 | Verified | Aqueous Ammonia Tank platform - northwest corner mid-rail needs welding. | C | S | Bobby Williams | McD | 2020-02-04 | Bobby Williams | Const | 2020-02-18 | Bobby Williams | 2020-02-25 | Keith Pollock
CIV-11 | CIV-11 | PI16536 | Verified | Remove all nails & wires from foundations. | C | C | Alan Huntsman | McD | 2020-02-04 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-20 | Dave Goldak
CIV-11 | CIV-11 | PI16537 | Verified | Seal construction joint at elec. duct bank stub-ups on the west side of the separator foundation and at meter pad next to road. | C | C | Johnny Campbell | McD | 2020-02-04 | Johnny Campbell | Const | 2020-03-31 | Johnny Campbell | 2020-05-20 | Dave Goldak
CIV-11 | CIV-11 | PI16538 | Verified | Complete stone fill at the fuel gas separator area. | C | C | Brooks Baker | McD | 2020-02-04 | Brooks Baker | Const | 2020-04-14 | Brooks Baker | 2020-05-20 | Dave Goldak
CIV-11 | CIV-11 | PI16539 | Verified | Seal construction joint at Calorie Meter. | C | C | Alan Huntsman | McD | 2020-02-04 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-20 | Dave Goldak
CIV-11 | CIV-11 | PI16541 | Verified | Point & patch needed at the fuel gas calorie meter pad. | C | C | Alan Huntsman | McD | 2020-02-04 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-20 | Dave Goldak
CIV-11 | CIV-11 | PI16542 | Verified | Calorie Meter shed not per (CBI) drawing. | C | S | Bobby Williams | McD | 2020-02-04 | Bobby Williams | Const | 2020-02-18 | Bobby Williams | 2020-03-05 | Dave Goldak
CIV-12 | CIV-12 | PI15432 | Verified | BFP 1A - Stair landing is not 3' from end of stairs | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-12 | CIV-12 | PI15433 | Verified | BFP 1A - Toe PL required @ first landing | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-18 | Tim Gallegos | 2020-07-21 | Satyam Gajjar
CIV-12 | CIV-12 | PI15434 | Verified | BFP 1A - Fix bent toe plate on platform | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-08 | Tim Gallegos | 2020-05-11 | Michael Law
CIV-12 | CIV-12 | PI15435 | Verified | BFP 1A - Provide grating support at pipe support opening | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-30 | Tim Gallegos | 2020-04-30 | Michael Law
CIV-12 | CIV-12 | PI15436 | Verified | BFP 1A - Fix Handrail around pipe support | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-18 | Tim Gallegos | 2020-07-21 | Satyam Gajjar
CIV-12 | CIV-12 | PI15437 | Verified | BFP 1A - Correct installation of monorail | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-12 | Bobby Williams | 2020-02-18 | Michael Law
CIV-12 | CIV-12 | PI15438 | Verified | BFP 1A - Install Roof at enclosure structure | B | M | Shane Crowe | McD | 2020-01-08 | Shane Crowe | Const |  |  | 2020-01-10 | Michael Law
CIV-12 | CIV-12 | PI15439 | Verified | BFP 1B - Stair landing is not 3' from end of stairs | B | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-21 | Michael Law
CIV-12 | CIV-12 | PI15440 | Verified | BFP 1B - Toe PL required @ first landing | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-30 | Tim Gallegos | 2020-04-30 | Michael Law
CIV-12 | CIV-12 | PI15441 | Verified | BFP 1B - Fix bent toe plate on platform | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-30 | Tim Gallegos | 2020-04-30 | Michael Law
CIV-12 | CIV-12 | PI15442 | Verified | BFP 1B - Provide grating support at pipe support opening | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-30 | Tim Gallegos | 2020-04-30 | Michael Law
CIV-12 | CIV-12 | PI15443 | Verified | BFP 1B - Fix Handrail around pipe support | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-08 | Tim Gallegos | 2020-05-11 | Michael Law
CIV-12 | CIV-12 | PI15444 | Verified | BFP 1B - Correct installation of monorail | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-02-12 | Bobby Williams | 2020-02-18 | Michael Law
CIV-12 | CIV-12 | PI15445 | Verified | BFP 1B - Install Roof at enclosure structure | B | M | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const |  |  | 2020-01-10 | Michael Law
CIV-12 | CIV-12 | PI15473 | Verified | BFP mezz floor - correct handrail at pipe supports | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-08 | Tim Gallegos | 2020-05-11 | Michael Law
CIV-12 | CIV-12 | PI15501 | Verified | BFP 1A/1B - add toe plate and guard rail below pipe (mid rail) | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-08 | Tim Gallegos | 2020-05-11 | Michael Law
CIV-12 | CIV-12 | PI15518 | Verified | Pipe rack - Tower anchor bolts are not tighten - Near BFP | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-04-02 | Michael Law
CIV-12 | CIV-12 | PI15522 | Verified | BFP Mezz Deck - No cage or fall arrest 25" ladder and not bolted at bottom - ladder is OSHA compliant with installed cable style safety system supplied with ladder | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-28 | Tim Gallegos | 2021-04-21 | John Watts
CIV-12 | CIV-12 | PI15541 | Verified | BFP Mezz Deck-No Cage-ladder is OSHA compliant with installed cable style safety system supplied with ladder | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2021-04-21 | John Watts
CIV-12 | CIV-12 | PI16583 | Verified | Loose stair nosing 1A Finger rack top of stairs Elev 522. Approx column line P. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-06 | James Beech | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16584 | Verified | Replace one broken abrasive stair nosing. One step up from intermediate platform at elev 511-5. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-05-11 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16585 | Verified | 1A finger rack Elev 522-8. Supplemental grating support required for panels near top of stair, at cut-out location for FWS pipe support. Approx column line P. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-05-08 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16586 | Verified | 1A Finger rack. Banding required at numerous grating cut-out locations, elev 522. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-06-18 | Tim Gallegos | 2020-07-27 | Dave Goldak
CIV-12 | CIV-12 | PI16587 | Verified | 1A Finger rack Elev 522-8. West handrail, Column line 9.6 (2 locations). Finish guardrail/toeplate at FWS piping crossing. Detail Case 5 or 6, drawing LK-10-000-GN-CE-STL-0001-13. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-07-27 | Dave Goldak
CIV-12 | CIV-12 | PI16588 | Verified | 1A Finger Rack Elev 522-8. Restore toe plate /HR removed for AOV support installation (2 locations) south end of platform. Column line N. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-06-02 | Tim Gallegos | 2020-07-27 | Dave Goldak
CIV-12 | CIV-12 | PI16589 | Verified | 1A Finger Rack stair, intermediate landing Elev 511-5. Missing toe plate under 1st stair to Elev 522-8. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-06-02 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-12 | CIV-12 | PI16590 | Verified | 1A Finger rack: Ladder at N.3 needs cage or fall protection system. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2021-04-21 | John Watts
CIV-12 | CIV-12 | PI16591 | Verified | 1A Finger rack elev 522-8 at top of ladder. Need grating extension to edge of supporting flange (nom 4" per drawing). | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2021-04-21 | John Watts
CIV-12 | CIV-12 | PI16592 | Verified | 1A Finger rack: Column N/10 anchor bolts missing (Q=2) jamb nuts at base plate. Q=2 others are loose. Tighten and torque as necessary. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16593 | Verified | 1A Finger rack: Column N/11 anchor bolt missing (Q=1) jamb nut at base plate. Q=3 others are loose. Tighten and torque as necessary. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16594 | Verified | 1A Finger rack: Column M/10 anchor bolts missing (Q=3) jamb nuts at base plate. Q=1 other is loose. Tighten and torque as necessary. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16595 | Verified | 1A Finger rack: Column M/11 anchor bolt jamb nuts at base plate: Q=4 are loose. Tighten and torque as necessary. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16596 | Verified | 1A Finger rack: Column L/11 anchor bolt nut is loose at base plate. Tighten and torque as necessary. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16597 | Verified | 1A Finger rack: Complete shed roof over Phosphate skid bay | C | S | Sheri Fritz | MOO | 2020-02-06 | Sheri Fritz | Const | 2020-03-10 | Tim Mills | 2020-03-12 | John Watts
CIV-12 | CIV-12 | PI16598 | Verified | 1A Finger rack Phosphate skid bay: Connect gutters and downspouts form shed roof to UG drain. | C | S | Sheri Fritz | MOO | 2020-02-06 | Sheri Fritz | Const | 2020-03-10 | Tim Mills | 2020-03-12 | John Watts
CIV-12 | CIV-12 | PI16599 | Verified | 1A Phosphate Skid Containment: Patch minor chips and damage from equipment installation. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16600 | Verified | 1A Phosphate Skid Containment: Install coating on tops of bush-hammered housekeeping pads. | C | C | Sheri Fritz | BRA | 2020-02-06 | Sheri Fritz | Const | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
CIV-12 | CIV-12 | PI16601 | Verified | 1B Finger Rack stair Elev 500. Complete anchor bolt installation at base of stair stringers. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16602 | Verified | 1B Finger rack stair. Two missing fasteners at abrasive nosings. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-14 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16603 | Verified | 1B Finger rack stair, intermediate landing Elev 511-5. Missing abrasive nosing at top of stair to grade. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-14 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16604 | Verified | 1B Finger Rack stair, intermediate landing Elev 511-5. Missing toe plate under 1st stair to Elev 522-8. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-14 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16605 | Verified | 1B Finger rack stair. Replace broken abrasive nosing top of stair at 522-8. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-14 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16606 | Verified | 1B finger rack Elev 522-8. Supplemental grating support required for panels near top of stair, at cut-out location for FWS pipe support. Approx column line P. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16607 | Verified | 1B Finger rack. Banding required at numerous grating cut-out locations, elev 522. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16608 | Verified | 1B Finger rack Elev 522-8. West handrail, Column line 13.6 (2 locations). Finish guardrail/toeplate at FWS piping crossing. Detail Case 5 or 6, drawing LK-10-000-GN-CE-STL-0001-13. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-05-08 | Tim Gallegos | 2020-06-16 | Dave Goldak
CIV-12 | CIV-12 | PI16609 | Verified | 1B Finger rack elev 522-8. Need grating extension at top of ladder to edge of supporting flange (nom 4" per drawing). | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2021-04-21 | John Watts
CIV-12 | CIV-12 | PI16610 | Verified | 1B Finger Rack Elev 522-8. Install safety gate at top of ladder, approx column N.3/10. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2021-04-21 | John Watts
CIV-12 | CIV-12 | PI16611 | Verified | 1B Finger Rack Elev 522-8. Restore toe plate /HR removed for AOV support installation, south end of platform. Column line N. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-30 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16612 | Verified | 1B Finger Rack elev 522-8. Replace broken/missing grating clips. Numerous locations. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-16 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16613 | Verified | 1B Finger rack: Ladder at N.3 needs cage or fall protection system. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-08-05 | Tim Gallegos | 2021-04-21 | John Watts
CIV-12 | CIV-12 | PI16614 | Verified | 1B Finger rack: Column R/13.6 anchor bolts missing (Q=4) jamb nuts at base plate. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16615 | Verified | 1B Finger rack: Column R/14 anchor bolts missing (Q=2) jamb nuts at base plate. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-30 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16616 | Verified | 1B Finger rack: Columns at P+10'2": Both columns missing anchor bolt (Q=8) jamb nuts at base plate. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16617 | Verified | 1B Finger rack: Column P/13.6 anchor bolts missing (Q=4) jamb nuts at base plate. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16618 | Verified | 1B Finger rack: Column P/15 anchor bolt missing (Q=1) jamb nut at base plate. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16619 | Verified | 1B Finger rack: Column N.6/13.6 anchor bolts missing (Q=3) jamb nuts at base plate. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16620 | Verified | 1B Finger rack: Column N.3/13.6 anchor bolts missing (Q=4) jamb nuts at base plate. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16621 | Verified | 1B Finger rack: Column M/14: Loose double nut (Q=1) at base plate. Tighten and torque as necessary. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16622 | Verified | 1B Finger rack: Column L/14: Loose double nuts (Q=2) at base plate. Tighten and torque as necessary. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16623 | Verified | 1B Finger rack: Column L/15: Loose double nut (Q=1) at base plate. Tighten and torque as necessary. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16624 | Verified | 1B Finger rack: Complete shed roof over Phosphate skid bay | C | S | Sheri Fritz | MOO | 2020-02-06 | Sheri Fritz | Const | 2020-03-10 | Tim Mills | 2020-03-12 | John Watts
CIV-12 | CIV-12 | PI16625 | Verified | 1B Finger rack Phosphate skid bay: Connect gutters and downspouts form shed roof to UG drain. | C | S | Sheri Fritz | MOO | 2020-02-06 | Sheri Fritz | Const | 2020-03-10 | Tim Mills | 2020-03-12 | John Watts
CIV-12 | CIV-12 | PI16626 | Verified | 1B Phosphate Skid Containment: Patch bond failures, minor chips and damage from equipment installation. Curbs and floor. | C | C | Alan Huntsman | McD | 2020-02-06 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16627 | Verified | 1B Phosphate Skid Containment: Install coating on tops of bush-hammered housekeeping pads. | C | C | Jerry Smith | McD | 2020-02-06 | Jerry Smith | Const | 2020-03-31 | Johnny Campbell | 2020-05-27 | Dave Goldak
CIV-12 | CIV-12 | PI16628 | Verified | Main Pipe Rack Elevation 552'-11.5": Handrail installed backwards southwest corner of platform (Line G). | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16629 | Verified | Main Pipe Rack Elevation 552'-11.5": Weld handrail splices on north end (two locations). | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-16 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16630 | Verified | Main Pipe Rack Elevation 552'-11.5": Toe plate missing under 1A-MSS-HGR-0013 | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-22 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16631 | Verified | Main Pipe Rack Elevation 552'-11.5": Terminate cut handrail, midrail at 1A-MSS-HGR-0013. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-22 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16632 | Verified | Main Pipe Rack Elevation 552'-11.5": Install toeplate under bottom stair to Elev 558'1" (Detail S4B) | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-22 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16633 | Verified | Main Pipe Rack Elevation 552'-11.5": Repair cut handrail, midrail, toeplate on Line J, behind pipe support. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-14 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16634 | Verified | Main Pipe Rack Elevation 552'-11.5": Install banding and grating clips on Line J, at Pipe support | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-16 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16635 | Verified | Main Pipe Rack Elevation 552'-11.5": Ladder not checked (no access) | D | S | Dave Goldak | McD | 2020-02-06 | Dave Goldak | Const | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
CIV-12 | CIV-12 | PI16636 | Verified | Main Pipe Rack Elevation 544': Anchor base of ladder to elevation 553. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-30 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-12 | CIV-12 | PI16637 | Verified | Main Pipe Rack Elevation 544': Weld handrail/midrail splice at G/9.6 | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-14 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16638 | Verified | Main Pipe Rack Elevation 544': Weld handrail/midrail splice at G/10 | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-14 | Tim Gallegos | 2020-06-10 | Dave Goldak
CIV-12 | CIV-12 | PI16639 | Verified | Main Pipe Rack Elevation 544': Weld handrail/midrail splice at L/9.6 | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-14 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16640 | Verified | Main Pipe Rack Elevation 544': Fix or bridge the elevation bust between grating and STG concrete, southwest side of platform. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-14 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-12 | CIV-12 | PI16641 | Verified | Main Pipe Rack Elevation 544': Fix or bridge the large gap between grating and STG concrete, northwest side of platform. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-16 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-12 | CIV-12 | PI16642 | Verified | Main Pipe Rack Elevation 544': Replace panel removed from center of platform. Install grating clips. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-30 | Tim Gallegos | 2020-05-26 | Dave Goldak
CIV-12 | CIV-12 | PI16643 | Verified | Main Pipe Rack Elevation 544': Install toe plate at column web (row J - STG). | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-22 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16644 | Verified | Main Pipe Rack Elevation 544': Complete toe plate on east side of platform (row 10) | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-14 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16645 | Verified | Main Pipe Rack Elevation 544': Patch gap in grating, install banding at pipe support (L/9) nortwest corner. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-14 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16646 | Verified | Main Pipe Rack Elevation 544': Finish HR/Toeplate installation and termination. Northwest edge (L/9) | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-14 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16647 | Verified | Main Pipe Rack Elevation 544': Replace damaged and bent grating panel at pipe support- north end (L/9.6) | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16648 | Verified | Main Pipe Rack Elevation 544': Install banding at pipe support- north end (L/9.6) | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16649 | Verified | Main Pipe Rack Elevation 544': Install banding at pipe support- northeast end (L/9.6) | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16650 | Verified | Main Pipe Rack Elevation 544': Complete toe plate at pipe support- northeast end (L/9.6) | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16651 | Verified | Main Pipe Rack Elevation 544': Install banding around valve operators, pipe and electrical penetrations through grating, multiple locations. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-02 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16652 | Verified | Main Pipe Rack Elevation 544': Complete handrail , midrail, toeplate patches where cut out for equipment and piping installation. South end of platform, Line G. | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-14 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16653 | Verified | Main Pipe Rack Elevation 544': Close gap between platform and toe plate, north end on Line L. Standard Detail S5Q | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-22 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16654 | Verified | Main Pipe Rack Elevation 555'10"': Close gap between platform and toe plate, north and south sides, entire length of platform. Standard Detail S5Q | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-08-24 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-12 | CIV-12 | PI16655 | Verified | Main Pipe Rack Elevation 555'10"': Patch paint handrail splice welds, entire platform | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-04-22 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16656 | Verified | Main Pipe Rack Elevation 555'10"': Install toe plate underneath first stair to elev 558'1". Std Detail S4B | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-08-24 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-12 | CIV-12 | PI16657 | Verified | Main Pipe Rack Elevation 558'1" (bridge between rows 10-11): Close gap between platform and toe plate, north and south sides, entire length of platform. Standard Detail S5Q | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-08-24 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-12 | CIV-12 | PI16658 | Verified | Main Pipe Rack Elevation west stair to Elev 558'1": replace broken abrasive nosing (one location). | C | S | Tim Gallegos | McD | 2020-02-06 | Tim Gallegos | Const | 2020-08-24 | Tim Gallegos | 2020-10-06 | Dave Goldak
CIV-12 | CIV-12 | PI16659 | Verified | Main Pipe Rack Elevation 555'10"': Remove piece of scrap angle iron from platform over 1B HRSG duct | C | C | Johnny Campbell | McD | 2020-02-06 | Johnny Campbell | Const | 2020-03-31 | Johnny Campbell | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16660 | Verified | Main Pipe Rack Elevation 555'10"': Remove wired piecemark tags from handrail from fabricator. Multiple locations. | C | C | Johnny Campbell | McD | 2020-02-06 | Johnny Campbell | Const | 2020-03-31 | Johnny Campbell | 2020-10-06 | Dave Goldak
CIV-12 | CIV-12 | PI16661 | Verified | Main Pipe Rack Elevation 555'10"': Patch paint welded connection to HRSG 1A steel. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI16662 | Verified | Main Pipe Rack Elevation 555'10"': Patch paint welded connection to HRSG 1B steel. | C | S | Bobby Williams | McD | 2020-02-06 | Bobby Williams | Const | 2020-03-25 | Tim Gallegos | 2020-05-28 | Dave Goldak
CIV-12 | CIV-12 | PI18525 | Verified | 1B-A BFP Enclosure: Replace damaged/bent roof panels. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-08-18 | Jason Ezell | 2020-08-18 | Jason Ezell
CIV-12 | CIV-12 | PI18526 | Verified | 1A-B BFP Enclosure: Replace damaged/bent roof panels. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-08-18 | Jason Ezell | 2020-08-18 | Jason Ezell
CIV-12 | CIV-12 | PI18527 | Verified | 1A-A BFP Enclosure: Replace damaged/bent roof panels. | C | S | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-08-18 | Jason Ezell | 2020-08-18 | Jason Ezell
CIV-13 | CIV-13 | PI09729 | Verified | Fix multiple leaks in the Main PDC. | B | C | Johnny Campbell | McD | 2019-10-21 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2020-02-15 | Shannon Scott
CIV-13 | CIV-13 | PI15455 | Verified | Main PDC - Install abrasive nosing at platform landing (both stairs) | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-30 | Tim Gallegos | 2020-04-30 | Michael Law
CIV-13 | CIV-13 | PI15456 | Verified | Main PDC - Close handrail pipe ends at stairs (both stairs) | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const | 2020-03-09 | Tim Gallegos | 2020-04-02 | Michael Law
CIV-13 | CIV-13 | PI15503 | Verified | Main PDC - Gap in Toe plate exceeds 1" laterally, correct the gap | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-05-07 | Tim Gallegos | 2020-05-07 | Michael Law
CIV-13 | CIV-13 | PI17663 | Verified | HVAC 2 vent has a slat that is damaged in the Main PDC. | C | M | Mike Tabbert | McD | 2020-03-04 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-30 | John Watts
CIV-13 | CIV-13 | PI17768 | Verified | Main PDC: Reinstall loose green ground jumper between HVAC-1 conduit and cable tray GND above south door. | C | C | Chris Colvin | McD | 2020-03-12 | Chris Colvin | Const | 2020-04-16 | Chris Colvin | 2020-06-03 | Dave Goldak
CIV-13 | CIV-13 | PI17769 | Verified | Main PDC: Seal opening in floor below 10-NJS-PNL-0001 | C | E | Chris Colvin | McD | 2020-03-12 | Chris Colvin | Const | 2020-04-16 | Chris Colvin | 2020-06-24 | Dave Goldak
CIV-13 | CIV-13 | PI17770 | Verified | Main PDC: East access doors are not weaher tight. Daylight visible around weatherstrip and at sill. | C | C | Chris Colvin | McD | 2020-03-12 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2021-04-21 | John Watts
CIV-13 | CIV-13 | PI17771 | Verified | Diesel Gen: Point/patch chips/pop-outs on foundation and housekeeping pedesal. | C | C | Johnny Campbell | McD | 2020-03-12 | Johnny Campbell | Const | 2020-04-01 | Johnny Campbell | 2020-06-03 | Dave Goldak
CIV-13 | CIV-13 | PI18084 | Verified | Main PDC Step - The bottom step of the Main PDC appears to have been hit and is now separated from the grating. Location: Plant South | C | C | Johnny Campbell | McD | 2020-03-18 | Johnny Campbell | Comm | 2020-04-02 | Johnny Campbell | 2020-07-28 | Keith Pollock
CIV-13 | CIV-13 | PI18684 | Verified | Main PDC: Install faceplates at exterior GFCI - at north door. | C | E | Chris Colvin | McD | 2020-06-25 | Chris Colvin | Const | 2020-06-26 | Mike Tabbert | 2020-07-10 | Dave Goldak
CIV-13 | CIV-13 | PI18685 | Verified | Main PDC: Install faceplates at exterior GFCI - at south door. | C | E | Chris Colvin | McD | 2020-06-25 | Chris Colvin | Const | 2020-07-20 | Chris Colvin | 2020-07-22 | Dave Goldak
CIV-13 | CIV-13 | PI18686 | Verified | Main PDC: Install faceplates at exterior GFCI - two locations on west wall. | C | E | Chris Colvin | McD | 2020-06-25 | Chris Colvin | Const | 2020-06-26 | Mike Tabbert | 2020-07-28 | Keith Pollock
CIV-14 | CIV-14 | PI02463 | Verified | Install fence at CO2 area. | A | C | Sheri Fritz | McD | 2019-07-22 | Sheri Fritz | Const | 2019-12-18 | Jerry Smith | 2019-12-18 | Randy Carpenter
CIV-14 | CIV-14 | PI02464 | Verified | Install bollards at the CO2 area. | A | C | Jerry Smith | McD | 2019-07-22 | Jerry Smith | Const | 2019-09-06 | Jerry Smith | 2019-09-11 | Richard Rothwell
CIV-14 | CIV-14 | PI04787 | Verified | Requesting an extra gate be installed on the east side of the fence. CO2 Skid | C | C | Josh Koerner | BEA | 2019-09-06 | Josh Koerner | Const | 2020-06-03 | Dave Goldak | 2020-06-03 | Dave Goldak
CIV-15 | CIV-15 | PI17231 | Verified | 1AMH101 has been paved over. Locate, bring manhole up to grade, and patch asphalt. | C | C | Brooks Baker | McD | 2020-02-26 | Brooks Baker | Const | 2020-04-09 | Brooks Baker | 2020-04-28 | Mark Williamson
CIV-15 | CIV-15 | PI17773 | Verified | Main PDC: Numerous open conduit stup-ups from UG ductbank under PDC. Install caps or seal conduits. | C | E | Chris Colvin | McD | 2020-03-12 | Chris Colvin | Const | 2020-04-29 | Matt Gilmore | 2020-06-24 | Dave Goldak
CIV-16 | CIV-16 | PI13381 | Verified | Complete tray system in STG needs the grounding installed. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2020-02-27 | Michael Law | 2020-02-27 | Mike Tabbert
CIV-16 | CIV-16 | PI13119 | Verified | Missing divider on the cable tray, additional support for above vertical 90, and missing hold down clamps on the horizontal 90 | C | E | Chris Colvin | McD | 2019-11-16 | Chris Colvin | Const |  |  | 2019-12-23 | Mike Tabbert
CIV-16 | CIV-16 | PI08232 | Verified | Complete cable tray dividers on control & instrument trays. | B | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const | 2020-03-26 | Chris Colvin | 2021-03-03 | John Watts
CIV-16 | CIV-16 | PI09133 | Verified | Cable tray rack west of HRSG 1A PDC, Cable tray needs two hole clamps bolted to angle iron suports on cable tray waterfall all levels. | C | E | Chris Colvin | McD | 2019-10-05 | Chris Colvin | Const | 2020-03-19 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI09139 | Verified | Cable tray rack west of HRSG 1B PDC, after waterfall headed south all the way to pipe rack, need hold down clamps and Cable Tray Labels. | B | E | Chris Colvin | McD | 2019-10-05 | Chris Colvin | Const | 2020-03-26 | Chris Colvin | 2020-04-02 | Mike Tabbert
CIV-16 | CIV-16 | PI14643 | Verified | No Cable Tray lables on east west running tray south side. | C | E | Chris Colvin | McD | 2019-12-08 | Chris Colvin | Const | 2020-05-04 | Matt Gilmore | 2020-05-19 | Mike Tabbert
CIV-16 | CIV-16 | PI14644 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, Cables are going over top of divder and must be fixed. | C | E | Chris Colvin | McD | 2019-12-08 | Chris Colvin | Const | 2020-03-19 | Chris Colvin | 2020-04-29 | Mike Tabbert
CIV-16 | CIV-16 | PI01286 | Verified | Cable Tray Rack turns north on the east side of STG, 90 degree horizontal bend needs support on all levels. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const | 2020-03-04 | Chris Colvin | 2020-03-04 | Mike Tabbert
CIV-16 | CIV-16 | PI01287 | Verified | Cable Tray Rack incline up to main pipe rack on east side of STG, all hold down clamps not installed on west side of rack all levels, cable tray labels need to be installed. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const | 2020-03-10 | Chris Colvin | 2020-03-10 | Mike Tabbert
CIV-16 | CIV-16 | PI01288 | Verified | Cable Tray Rack at top of incline 90 degree horizontal bend to the east needs supports all levels. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const | 2020-03-05 | Chris Colvin | 2020-03-06 | Mike Tabbert
CIV-16 | CIV-16 | PI01290 | Verified | Cable Tray offset to the north just east of GT 1A needs supports on levels, hold down clamps missing and cable tray labels need to be installed. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI01291 | Verified | Cable Tray Rack at waterfall to GT 1A Control Building missing supports 90 degree horizontal bend to the south all levels, missing supports on vertical offset all levels, missing hold down clamps on vertical 90 degree to the south. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI01292 | Verified | Cable Tray Rack, Main Pipe Rack east end, 90 degree horizontal transition to horizontal Tee's need suports all levels. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI01293 | Verified | Cable Tray Rack, waterfall to GT 1A control building missing supports on vertical trays. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI01295 | Verified | Cable Tray Rack GT 1A, from offset to control building, cable tray labels need to be installed. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI00949 | Verified | Cable Tray Rack on north end of Main PDC, some missing splice plate bolts, missing hold down clamps, missing cable tray labels and grounding incomplete. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI00950 | Verified | Cable Tray Rack turns north on the east side of STG, 90 degree horizontal bend needs support on all levels. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2020-03-04 | Chris Colvin | 2020-03-04 | Mike Tabbert
CIV-16 | CIV-16 | PI00951 | Verified | Cable Tray Rack incline up to main pipe rack on east side of STG, all hold down clamps not installed on west side of rack all levels, grounding incomplete, cable tray labels need to be installed. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2020-03-10 | Chris Colvin | 2020-03-10 | Michael Law
CIV-16 | CIV-16 | PI00952 | Verified | Cable Tray Rack at top of incline 90 degree horizontal bend to the east needs supports all levels. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2020-03-05 | Chris Colvin | 2020-03-06 | Mike Tabbert
CIV-16 | CIV-16 | PI00954 | Verified | Cable Tray offset to the north just east of GT 1A needs supports on levels, also grounding not complete, hold down clamps missing and cable tray labels need to be installed. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2020-03-26 | Chris Colvin | 2020-04-02 | Mike Tabbert
CIV-16 | CIV-16 | PI00955 | Verified | Cable Tray Rack at waterfall to GT 1A Control Building missing supports 90 degree horizontal bend to the south all levels, missing supports on vertical offset all levels, missing hold down clamps on vertical 90 degree to the south. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2020-03-12 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI00956 | Verified | Cable Tray Rack, Main Pipe Rack east end, 90 degree horizontal transition to horizontal Tee's need suports all levels. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2020-03-10 | Chris Colvin | 2020-03-10 | Mike Tabbert
CIV-16 | CIV-16 | PI00957 | Verified | Cable Tray Rack to 1B Control Building 90 degree horizontal bend to the south and vertical drop heading south missing supports and hold down clamps. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2020-03-12 | Chris Colvin | 2020-03-16 | Mike Tabbert
CIV-16 | CIV-16 | PI00958 | Verified | Cable Tray Rack to 1B Control Building, hold down clamps missing along entire run all levels. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2020-03-19 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI00937 | Verified | Cable Tray Rack turns north on the east side of STG, 90 degree horizontal bend needs support on all levels. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2020-03-04 | Chris Colvin | 2020-03-04 | Mike Tabbert
CIV-16 | CIV-16 | PI00938 | Verified | Cable Tray Rack incline up to main pipe rack on east side of STG, all hold down clamps not installed on west side of rack all levels, grounding incomplete, cable tray labels need to be installed. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2020-03-26 | Chris Colvin | 2020-04-02 | Mike Tabbert
CIV-16 | CIV-16 | PI00939 | Verified | Cable Tray Rack at top of incline 90 degree horizontal bend to the east needs supports all levels. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2020-03-05 | Chris Colvin | 2020-03-06 | Mike Tabbert
CIV-16 | CIV-16 | PI00942 | Verified | Cable Tray Rack at waterfall to GT 1A Control Building missing supports 90 degree horizontal bend to the south all levels, missing supports on vertical offset all levels, missing hold down clamps on vertical 90 degree to the south. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI00943 | Verified | Cable Tray Rack, Main Pipe Rack east end, 90 degree horizontal transition to horizontal Tee's need suports all levels. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2020-03-26 | Chris Colvin | 2020-04-02 | Mike Tabbert
CIV-16 | CIV-16 | PI00944 | Verified | Cable Tray Rack, Main Pipe Rack east end, at waterfall leadint to GT 1B Control Building, missing supports at vertical outside 90 degree bends and vertical inside 90 degree bends | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI00945 | Verified | Cable Tray Rack to 1B Control Building 90 degree horizontal bend to the south and vertical drop heading south missing supports and hold down clamps. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI00946 | Verified | Cable Tray Rack to 1B Control Building, hold down clamps missing along entire run all levels. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI05077 | Verified | GT east side cable tray - needs label. | C | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2020-04-16 | Chris Colvin | 2020-04-21 | Mike Tabbert
CIV-16 | CIV-16 | PI05086 | Verified | NRG enclosure 1ABAW11GH001 - label cable tray on west side. | C | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2020-04-16 | Chris Colvin | 2020-04-21 | Mike Tabbert
CIV-16 | CIV-16 | PI05039 | Verified | GT east side cable tray - label. | C | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CIV-16 | CIV-16 | PI08226 | Verified | Label all cable trays. | C | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const | 2020-04-23 | Chris Colvin | 2020-04-23 | Mike Tabbert
CIV-16 | CIV-16 | PI12610 | Verified | Repair cable tray support sagging. | B | E | Chris Colvin | McD | 2019-10-29 | Chris Colvin | Const | 2019-11-13 | Brad Stanford | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI14769 | Verified | Put covers on the cable tray from Thy building to the excitation transformer | B | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2020-03-10 | Chris Colvin | 2020-03-11 | Mike Tabbert
CIV-16 | CIV-16 | PI06863 | Verified | The following cable trays do not have hold down clamps from Phophate Skid to HRSG PDC, 1ATK152002, 1ATC152002 and 1AtX152002. | B | E | Chris Colvin | McD | 2019-09-23 | Chris Colvin | Const | 2019-12-08 | Brad Stanford | 2020-01-22 | Mike Tabbert
CIV-16 | CIV-16 | PI06958 | Verified | The following cable trays do not have hold down clamps from HRSG PDC to above boiler feed water, 1ATL152002, 1ATK152002, 1ATC2002, 1ATX152002. | B | E | Chris Colvin | McD | 2019-09-24 | Chris Colvin | Const | 2020-03-20 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI06961 | Verified | The following cable trays do not have hold down clamps from HRSG PDC to above boiler feed water, 1BTL153002, 1BTK153002, 1BTC53002, 1BTX153002. | B | E | Chris Colvin | McD | 2019-09-24 | Chris Colvin | Const | 2020-03-26 | Chris Colvin | 2020-04-02 | Mike Tabbert
CIV-16 | CIV-16 | PI12962 | Verified | 1ATK111014, 1ATK111012, 1ATK111013, 1ATK111031, 1ATK111032, Cable Trays install covers. | C | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2020-03-31 | Chris Colvin | 2020-04-29 | Mike Tabbert
CIV-16 | CIV-16 | PI09146 | Verified | Label all cable trays. | C | E | Chris Colvin | McD | 2019-10-07 | Chris Colvin | Const | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
CIV-16 | CIV-16 | PI00712 | Verified | 1ATL121701, Install cover on Cable Tray. | C | E | Chris Colvin | McD | 2019-04-26 | Chris Colvin | Const | 2020-03-31 | Chris Colvin | 2020-04-02 | Mike Tabbert
CIV-16 | CIV-16 | PI00730 | Verified | 1BTL121701, Install cover on Cable Tray. | C | E | Chris Colvin | McD | 2019-04-26 | Chris Colvin | Const | 2020-03-31 | Chris Colvin | 2020-04-02 | Mike Tabbert
CIV-16 | CIV-16 | PI13811 | Verified | Need plastic end caps at sharp edges of ladder cable trays to prevent cable insulation damage, under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Shannon Scott
CIV-16 | CIV-16 | PI13828 | Verified | Need plastic end caps at sharp edges of ladder cable trays to prevent cable insulation damage, under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Shannon Scott
CIV-16 | CIV-16 | PI01272 | Verified | Cable Tray Rack on north end of Main PDC, some missing splice plate bolts, missing hold down clamps, missing cable tray labels. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const | 2020-03-19 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI01273 | Verified | Cable Tray Rack turns north on the east side of STG, 90 degree horizontal bend needs support on all levels. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const | 2020-03-04 | Chris Colvin | 2020-03-04 | Mike Tabbert
CIV-16 | CIV-16 | PI01274 | Verified | Cable Tray Rack incline up to main pipe rack on east side of STG, all hold down clamps not installed on west side of rack all levels, cable tray labels need to be installed. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const | 2020-03-10 | Chris Colvin | 2020-03-10 | Mike Tabbert
CIV-16 | CIV-16 | PI01275 | Verified | Cable Tray Rack at top of incline 90 degree horizontal bend to the east needs supports all levels. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const | 2020-03-05 | Chris Colvin | 2020-03-06 | Mike Tabbert
CIV-16 | CIV-16 | PI01277 | Verified | Cable Tray offset to the north just east of GT 1A needs supports on levels, hold down clamps missing and cable tray labels need to be installed. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const | 2020-03-18 | Chris Colvin | 2020-03-18 | Mike Tabbert
CIV-16 | CIV-16 | PI01278 | Verified | Cable Tray Rack at waterfall to GT 1A Control Building missing supports 90 degree horizontal bend to the south all levels, missing supports on vertical offset all levels, missing hold down clamps on vertical 90 degree to the south. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI01279 | Verified | Cable Tray Rack, Main Pipe Rack east end, 90 degree horizontal transition to horizontal Tee's need suports all levels. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const | 2020-03-10 | Chris Colvin | 2020-03-10 | Mike Tabbert
CIV-16 | CIV-16 | PI01280 | Verified | Cable Tray Rack, waterfall to GT 1A control building missing supports on vertical trays. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI01283 | Verified | Cable Tray Rack GT 1A, at control building waterfall, missing supports. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI13790 | Verified | Need plastic end caps at sharp edges of ladder cable trays to prevent cable insulation damage, under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Shannon Scott
CIV-16 | CIV-16 | PI13793 | Verified | Remove all unsued wire from cable trays under B PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-03 | Shannon Scott | 2020-01-03 | Shannon Scott
CIV-16 | CIV-16 | PI13773 | Verified | Need plastic end caps at sharp edges of ladder cable trays to prevent cable insulation damage, under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Shannon Scott
CIV-16 | CIV-16 | PI13776 | Verified | Remove all unsued wire from cable trays under B PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Shannon Scott
CIV-16 | CIV-16 | PI01806 | Verified | Put cables neat and orderly in cable trays, and secured to cable tray rungs, ty-raps tails trimmed. | C | E | Chris Colvin | McD | 2019-07-01 | Chris Colvin | Const | 2020-03-23 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI13373 | Verified | 1CTL201101, 1CTL201001, 1CTL201101, 1CTC201001, Cable Tray North of Main PDC, X-Tray cables to be straightened out and tie rapped neatly. | C | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2020-04-16 | Chris Colvin | 2020-04-21 | Mike Tabbert
CIV-16 | CIV-16 | PI13374 | Verified | 1CTL201101, 1CTL201001, 1CTL201101, 1CTC201001, Cable Tray North of Main PDC, Cable Tray riser going into STG Building needs support above lower vertical 90 degree elbow, needs support midway up, below upper vertical 90 degree elbow and above upper vetical 90 degree elbow . | B | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2020-03-23 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI13375 | Verified | 1CTL201101, 1CTL201001, 1CTL201101, 1CTC201001, Cable Tray North of Main PDC, Needs divider complete and needs labels installed. | B | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2020-03-26 | Chris Colvin | 2020-04-02 | Mike Tabbert
CIV-16 | CIV-16 | PI13376 | Verified | 1CTL201101, 1CTL201001, 1CTL201101, 1CTC201001, Cable Tray North of Main PDC, Horizontal 90 degree elbow at top of riser needs supports. | B | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-02 | Mike Tabbert
CIV-16 | CIV-16 | PI03742 | Verified | Demin Bldg, Cable tray access opening in North West corner of building needs more support both sides. | B | S | Bobby Williams | McD | 2019-08-09 | Bobby Williams | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI05806 | Verified | Label cable trays. | C | E | Chris Colvin | McD | 2019-09-13 | Chris Colvin | Const | 2020-04-23 | Chris Colvin | 2020-04-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15143 | Verified | Dwg. LK-10-003-PL-EE-CT-0001 - divider in SW corner needs to be anchored properly. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-01-23 | Jared Stimpson | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15144 | Verified | Dwg. LK-10-003-PL-EE-CT-0001 - divider in SW corner needs splice cap. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
CIV-16 | CIV-16 | PI15145 | Verified | Dwg. LK-10-003-PL-EE-CT-0001 - re-route hanging cable in SW corner to remove slack. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-01-23 | Jared Stimpson | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15146 | Verified | Dwg. LK-10-003-PL-EE-CT-0001 - extend cable tray divider connectors. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-01-23 | Jared Stimpson | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15147 | Verified | Dwg. LK-10-003-PL-EE-CT-0001 - Install edge guards or straighten cables where cables are in contact with cable tray | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-01-23 | Jared Stimpson | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15148 | Verified | Dwg. LK-10-003-PL-EE-CT-0001 - secure / ty-wrap all cables neatly in tray. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-30 | Jared Stimpson
CIV-16 | CIV-16 | PI15149 | Verified | Dwg. LK-10-003-PL-EE-CT-0001 - NE corner of cable tray - ground to earth. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-01-23 | Jared Stimpson | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15150 | Verified | Dwg. LK-10-531-PL-EE-CT-0001 - cut all ty-wrap tails. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
CIV-16 | CIV-16 | PI15151 | Verified | Dwg. LK-10-531-PL-EE-CT-0001 - secure / ty-wrap / straighten all cables neatly. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-02 | Mike Tabbert
CIV-16 | CIV-16 | PI15152 | Verified | Dwg. LK-10-531-PL-EE-CT-0001 - add labels to the west side of the cable trays. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-03-12 | Chris Colvin | 2020-03-16 | Mike Tabbert
CIV-16 | CIV-16 | PI15153 | Verified | Dwg. LK-10-531-PL-EE-CT-0001 - plumb up vertical tray at entry to the WTB. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-09 | Fred Michael
CIV-16 | CIV-16 | PI15154 | Verified | Dwg. LK-10-531-PL-EE-CT-0001 - seal penetration at cable tray entry to the WTB. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-09 | Mike Tabbert
CIV-16 | CIV-16 | PI15155 | Verified | Dwg. LK-10-531-PL-EE-CT-0001 - add dividers in horizontal tray at entry to the WTB. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
CIV-16 | CIV-16 | PI15156 | Verified | Dwg. LK-10-531-PL-EE-CT-0001 - install hold down clamps & support at vertical 90 (top & bottom) at entry to the WTB. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-03-20 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15157 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - install drop-outs at vertical 90 at waterfall - south end. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-03-19 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15158 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - install heavy duty hold down clamps at vertical tray - south end. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
CIV-16 | CIV-16 | PI15159 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - secure horizontal tray to support - south end. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-09 | Mike Tabbert
CIV-16 | CIV-16 | PI15160 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - add supports to overhead trays at 90 on SW corner. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CIV-16 | CIV-16 | PI15161 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - add cable tray labels on both sides of all trays - Note: tray labels at SW corner of containment and NW corner of Clarifier are incorrect. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
CIV-16 | CIV-16 | PI15162 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - east side cable tray "T" - south side of "T" needs hold down clamps. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CIV-16 | CIV-16 | PI15163 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - Need splice caps - east side. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CIV-16 | CIV-16 | PI15164 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - missing hold down clamps - south end. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
CIV-16 | CIV-16 | PI15165 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - complete divider on south end cable tray. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CIV-16 | CIV-16 | PI15166 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - straighten & ty-wrap all cables in area. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-02 | Mike Tabbert
CIV-16 | CIV-16 | PI15167 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - complete divider on north end cable tray. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-03-19 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15168 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - missing splice caps. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
CIV-16 | CIV-16 | PI15169 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - complete divider on west side. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CIV-16 | CIV-16 | PI15170 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - straighten cable tray divider. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-02 | Mike Tabbert
CIV-16 | CIV-16 | PI15171 | Verified | Dwg. LK-10-531-PL-EE-CT-0004 - straighten cables in trays. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-02 | Mike Tabbert
CIV-16 | CIV-16 | PI15173 | Verified | Need heavy duty clamps on vertical trays at NW & SW corners of CW pumps - ground level. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
CIV-16 | CIV-16 | PI15174 | Verified | Need additional ty-wraps on cables in vertical trays at NW & SW corners of CW pumps - ground level. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
CIV-16 | CIV-16 | PI15175 | Verified | Trim ty-wraps in horizontal tray under 10-CWS-JB-0001. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
CIV-16 | CIV-16 | PI15176 | Verified | Install 12" drop-outs on horizontal trays at NW & SW corners of CW pumps - ground level. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
CIV-16 | CIV-16 | PI15177 | Verified | Missing strut support caps at NW & SW corners of CW pumps - ground level. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
CIV-16 | CIV-16 | PI15178 | Verified | Missing standard cable tray hold down clamp at north side of 10-CWS-P-0001A. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
CIV-16 | CIV-16 | PI15179 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - clean up at U/G conduit stub ups at west end of CT PDC. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-02 | Mike Tabbert
CIV-16 | CIV-16 | PI15180 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - attach ground to conduit lug at west end of CT PDC. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15181 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - straighten & ty-wrap all cbles in vertical tray at west end of CT PDC. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-03-12 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15182 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - seal all conduits under / at the CT PDC. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-02 | Mike Tabbert
CIV-16 | CIV-16 | PI15183 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - build enclosure at U/G stub ups at west end of CT PDC. | C | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-06-26 | Chris Colvin | 2020-07-10 | Mike Tabbert
CIV-16 | CIV-16 | PI15184 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - missing cable tray labels at transition tray at NE corner of CT PDC ( 2 separate sets of labels ). | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15185 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - cut all ty-wrap tails. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CIV-16 | CIV-16 | PI15186 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - any cables outside of cable trays need to be re-routed to be inside of tray at CT PDC. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-02 | Mike Tabbert
CIV-16 | CIV-16 | PI15187 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - sort, dress, ty-wrap all cables in 24" tray directly under CT PDC. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-02 | Mike Tabbert
CIV-16 | CIV-16 | PI15188 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - dress all fan motor feeder cables on south side of CT PDC. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-03-16 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15189 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - attach all ground cables under CT PDC. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-03-26 | Chris Colvin | 2020-04-29 | Mike Tabbert
CIV-16 | CIV-16 | PI15190 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - add cable trays under CT PDC at west end from the four 5" stub ups to the existing tray. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-03-19 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15191 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - box in cables at stub ups on south side of CT PDC. | C | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-06-26 | Chris Colvin | 2020-07-10 | Mike Tabbert
CIV-16 | CIV-16 | PI15192 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - need tray end caps at east end under CT PDC. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15193 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - box in cables at stub ups on east end under CT PDC. | C | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-06-26 | Chris Colvin | 2020-07-10 | Mike Tabbert
CIV-16 | CIV-16 | PI15194 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - clean all stub up conduit nipples - wire brush & cold galv at CT PDC. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-03-12 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15195 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - add supports on 1st vertical riser after CT PDC going to CT. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-02-10 | Fred Michael
CIV-16 | CIV-16 | PI15196 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - missing hold down clamps on riser to CT. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15197 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - straighten strut under tray on CT riser. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-02 | Mike Tabbert
CIV-16 | CIV-16 | PI15198 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - missing hold down clamps on vertical risers (3) at top of CT - south side. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15199 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - missing hold down clamps on north/south horizontal tray at risers. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15200 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - missing hold down clamps on north/south horizontal tray after waterfall going to fans (all trays). | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15201 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - complete divider in north/south bottom tray at 90 to east/west tray. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15202 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - missing hold down claps at north/south bottom tray at 90 to east/west tray. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15203 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - secure cables in center east/west bottom tray at 90 for north/south tray at A/B fans. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-03-23 | Chris Colvin | 2020-03-27 | Mike Tabbert
CIV-16 | CIV-16 | PI15204 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - missing hold down in all 3 east/west trays at A/B fans. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15205 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - broken tray support in bottom north/south tray at tray intersection of C & D fans. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const | 2020-03-23 | Chris Colvin | 2020-03-27 | Mike Tabbert
CIV-16 | CIV-16 | PI15206 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - cut back all north/south trays near fan motors to the support. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15207 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - missing hold downs in top & bottom trays in east/west trays between E & F fans. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15208 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - missing hold downs in top & bottom trays in east/west trays between G & H fans. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15209 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - missing hold downs in top & bottom trays in east/west trays between G & J fans. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15210 | Verified | Dwg. LK-10-511-PL-EE-CT-0001 - label all cable trays - top of cooling tower. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
CIV-16 | CIV-16 | PI15215 | Verified | Clean up cable tray on north side of 1A-NJS-PNL-0003; HRSG 1A Top MOV Distribution PNL 3 | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2021-03-03 | John Watts
CIV-16 | CIV-16 | PI15220 | Verified | Clean up cable tray on north side of 1A-NJS-PNL-0004; HRSG 1A Top MOV Distribution PNL 4 | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2021-03-03 | John Watts
CIV-16 | CIV-16 | PI15225 | Verified | Cable tray divider on top tray missing south of 1B-NJS-PNL-0004; HRSG-1B Top MOV Distribution PNL 3 | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2021-03-03 | John Watts
CIV-16 | CIV-16 | PI15328 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - organize & ty-wrap all cables & trim all ty-wrap tails. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-20 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15329 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - remove all un-used cables. | C | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-19 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15330 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - clean / remove all tape & trash from trays. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CIV-16 | CIV-16 | PI15331 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - tray 1BTC323806/C & /K - place cables in proper service level. Remove cables from over the top of the divider & ensure cables lay in trays following the 90's. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-20 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15332 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - tray 1BTC323806/C & /K - move cables from under tray to top of tray & remove all slack. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-20 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15333 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - the four vertical trays on the east side need dropouts. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const |  |  | 2020-02-07 | Fred Michael
CIV-16 | CIV-16 | PI15334 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - permanently seal all penetrations into the control package. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const |  |  | 2020-02-07 | Fred Michael
CIV-16 | CIV-16 | PI15335 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - tray 1BTC3233004/X & /C - resolve issue of cables jumping from one tray to another. | C | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-05-13 | Chris Colvin | 2020-05-13 | Mike Tabbert
CIV-16 | CIV-16 | PI15336 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - tighten ground jumpers on all trays. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CIV-16 | CIV-16 | PI15337 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - replace rusty hardware with SS hardware. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const |  |  | 2020-02-07 | Fred Michael
CIV-16 | CIV-16 | PI15338 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - crossover tray at north end under control package needs divider. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-26 | Chris Colvin | 2020-04-29 | Mike Tabbert
CIV-16 | CIV-16 | PI15339 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - vertical tray (north-center) under control package needs heavy duty clips. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const |  |  | 2020-02-07 | Fred Michael
CIV-16 | CIV-16 | PI15340 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - the four vertical trays under the control package need dropouts. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const |  |  | 2020-02-07 | Fred Michael
CIV-16 | CIV-16 | PI15341 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - ensure all trays are labeled on both sides. | C | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-04-28 | Matt Gilmore | 2020-04-29 | Mike Tabbert
CIV-16 | CIV-16 | PI15342 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - vertical tray at crossover at the NE side under package needs heavy duty clips. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const |  |  | 2020-02-07 | Fred Michael
CIV-16 | CIV-16 | PI15343 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - all vertical trays on the west side of the control package need dropouts. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const |  |  | 2020-02-07 | Fred Michael
CIV-16 | CIV-16 | PI15344 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - any cables touching edges need edge guards. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const |  |  | 2020-02-07 | Fred Michael
CIV-16 | CIV-16 | PI15345 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - pull tight & ty-wrap cables in vertical tray at waterfall at north end of the control package. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const |  |  | 2020-02-07 | Fred Michael
CIV-16 | CIV-16 | PI15346 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - install all cable tray covers. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-12 | Chris Colvin | 2020-04-29 | Mike Tabbert
CIV-16 | CIV-16 | PI15347 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - trim ty-wraps on the 2 lower horizontal trays from control package to GT area. | C | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-04-28 | Matt Gilmore | 2020-04-29 | Mike Tabbert
CIV-16 | CIV-16 | PI15348 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - remove temp power, rope from trays. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-16 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15349 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - label trays on both sides of horizontal trays. Note: labels "1003" are incorrect. | C | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-19 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15350 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - form cables on east side of "T" to filter house & ty-wrap to tray. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-16 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15351 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - vertical riser to filter house needs divider caps. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-16 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15352 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - vertical risers to filter houose - replace light duty clamps with heavy duty clamps. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-16 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15353 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - complete ty-wrapping every 5 feet in horizontal trays. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-16 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15354 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - tray 1BTL421023/L/K - label tray on both sides - vertical riser to filter house. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-16 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15355 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - at "T" - cables not in trays, remove un-used cables. | C | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-19 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15356 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - ty-wrap cables in vertical tray to NE corner going to filter house. Note: scaffold is in place and ready to fix now. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-16 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15357 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - cables crossing divider at NE corner going to filter house. Note: scaffold is in place and ready to fix now. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-16 | Chris Colvin | 2020-03-23 | Mike Tabbert
CIV-16 | CIV-16 | PI15358 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - missing tray labels on horizontal run - both sides. | C | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-04-28 | Matt Gilmore | 2020-04-29 | Mike Tabbert
CIV-16 | CIV-16 | PI15359 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - form cables in waterfall at GT/HRSG transition area. | C | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-05-05 | Chris Colvin | 2020-05-19 | Mike Tabbert
CIV-16 | CIV-16 | PI15360 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - tray 1BTL421011/L/K - label tray on both sides. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-12 | Chris Colvin | 2020-03-16 | Mike Tabbert
CIV-16 | CIV-16 | PI15361 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - tray 1BTL421011/L/K - trim ty-wraps. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-12 | Chris Colvin | 2020-05-04 | Mike Tabbert
CIV-16 | CIV-16 | PI15362 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - tray 1BTL421011/L/K - straighten out cables. | C | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const | 2020-03-20 | Chris Colvin | 2020-05-04 | Mike Tabbert
CIV-16 | CIV-16 | PI15363 | Verified | Dwg. LK-10-323-PL-EE-CT-0002 - remove & re-install trapeze support in contact with air line at east side below duct burner skid. | B | E | Chris Colvin | McD | 2020-01-07 | Chris Colvin | Const |  |  | 2020-02-10 | Fred Michael
CIV-16 | CIV-16 | PI02741 | Verified | Cables need to be straightned out in tray feeding 1C-GCH-CP-9000, tie rap cables in a neat and consistent fashion. | C | E | Chris Colvin | McD | 2019-07-24 | Chris Colvin | Const | 2020-04-16 | Chris Colvin | 2020-04-21 | Mike Tabbert
CIV-16 | CIV-16 | PI13380 | Verified | Complete tray system in STG needs the labels installed. | C | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
CIV-16 | CIV-16 | PI15458 | Verified | Cabletray support near main PDC - Column missing second nut for two nut connection (2011-148C2) | C | S | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
CIV-16 | CIV-16 | PI15457 | Verified | Cable try support near Main PDC - Loose Anchor bolt nuts (2011-151C1, 152C1, 153C1) | C | S | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Const |  |  | 2020-02-10 | Fred Michael
CIV-16 | CIV-16 | PI17324 | Verified | Missing nuts and loose requiring tighting on column L/9. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-07 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-16 | CIV-16 | PI17325 | Verified | Missing nuts on column J/9. | C | S | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Const | 2020-05-07 | Tim Gallegos | 2020-05-27 | Dave Goldak
CIV-16 | CIV-16 | PI17698 | Verified | Cable tray support brackets not fastened/bolted to concrete. Located under Cooling Tower PDC. | C | E | Chris Colvin | McD | 2020-03-04 | Chris Colvin | Const | 2020-03-31 | Chris Colvin | 2020-06-24 | Dave Goldak
CIV-16 | CIV-16 | PI18070 | Verified | The edges of the cable trays on the Plant Northeast side of the cooling tower are sharp/potential hazard if someone trips onto them. Consider adding cap or shield. | C | E | Mike Tabbert | McD | 2020-03-18 | Mike Tabbert | Comm | 2020-03-25 | Mike Tabbert | 2021-02-01 | Dave Goldak
CNC-01 | CNC-01 | PI02362 | Verified | Replace vendor supplied plastic seal tight connectors. | A | E | Luis Cantu | McD | 2019-07-19 | Luis Cantu | Const | 2019-07-19 | Luis Cantu | 2019-07-26 | Logan Holland
CNC-01 | CNC-01 | PI02363 | Verified | Ground flex connectors on skid. | A | E | Luis Cantu | McD | 2019-07-19 | Luis Cantu | Const | 2019-07-19 | Luis Cantu | 2019-07-26 | Logan Holland
CNC-01 | CNC-01 | PI02364 | Verified | Add low point drain(s) on vendor conduit on skid. | A | E | Luis Cantu | McD | 2019-07-19 | Luis Cantu | Const | 2019-07-19 | Luis Cantu | 2019-07-26 | Logan Holland
CNC-01 | CNC-01 | PI02365 | Verified | Vents for calibration column and 1C-CNC-LSL-0101 on skid are too low. Need to be higher that tote. | A | I | Gonzalo Pena | McD | 2019-07-19 | Gonzalo Pena | Const | 2019-07-19 | Gonzalo Pena | 2019-07-25 | C_AC03
CNC-01 | CNC-01 | PI02366 | Verified | Grout Condensate Aqueous Ammonia Feed Skid 1C-CNC-SKD-0100. | C | C | Johnny Campbell | McD | 2019-07-19 | Johnny Campbell | Const | 2019-07-24 | Jack Fields | 2019-10-04 | Joshua Sturgeon
CNC-01 | CNC-01 | PI02367 | Verified | Heat shrink shields in panel 1C-CNC-CP-0100. | A | E | Luis Cantu | McD | 2019-07-19 | Luis Cantu | Const | 2019-07-19 | Luis Cantu | 2019-07-25 | C_AC03
CNC-01 | CNC-01 | PI02368 | Verified | Red line vendor P&ID to show goose-necked vent on 1C-CNC-LSL-0101. ProMinent P&ID 3018800316-101. | C | P | Charles Worthington | McD | 2019-07-19 | Charles Worthington | Const | 2020-04-28 | Charles Worthington | 2020-04-28 | Michael Law
CNC-01 | CNC-01 | PI02369 | Verified | Tighten flex connector on 1C-CNC-CP-0100. | A | E | Luis Cantu | McD | 2019-07-19 | Luis Cantu | Const | 2019-07-19 | Luis Cantu | 2019-07-22 | Mike Tabbert
CNC-01 | CNC-01 | PI02371 | Verified | Extend skid drain to sump. | C | I | Gonzalo Pena | McD | 2019-07-19 | Gonzalo Pena | Const | 2019-07-19 | Gonzalo Pena | 2019-08-08 | Kelvin Cook
CNC-01 | CNC-01 | PI02413 | Verified | Complete all completion paperwork. | A | E | Luis Cantu | McD | 2019-07-20 | Luis Cantu | Const | 2019-07-23 | Mike Tabbert | 2019-07-23 | Mike Tabbert
CNC-01 | CNC-01 | PI02414 | Verified | Verify all raceway grounding has been completed. | A | E | Luis Cantu | McD | 2019-07-20 | Luis Cantu | Const | 2019-07-20 | Ken Mundy | 2019-07-23 | Mike Tabbert
CNC-01 | CNC-01 | PI02415 | Verified | 1C-CNC-SKD-0100, Connect grounding grid to skid. | A | E | Luis Cantu | McD | 2019-07-20 | Luis Cantu | Const | 2019-07-20 | Ken Mundy | 2019-07-23 | Mike Tabbert
CNC-01 | CNC-01 | PI02447 | Verified | Grating over containment incomplete. | D | S | Tim Gallegos | McD | 2019-07-22 | Tim Gallegos | Const | 2019-07-26 | Tim Gallegos | 2019-08-08 | Dave Goldak
CNC-01 | CNC-01 | PI02448 | Verified | 1C-CNC-FXH-0100 & connection to tote (vendor piping) | B | M | William Mitchell | McD | 2019-07-22 | William Mitchell | Const | 2019-12-23 | Michael Law | 2020-01-02 | Nelson Eichelberger
CNC-01 | CNC-01 | PI02449 | Verified | Apply coating to trench & pads. | A | X | Javier Buelvas | BRA | 2019-07-22 | Javier Buelvas | Const | 2019-07-23 | Javier Buelvas | 2019-07-31 | Blake Boudreaux
CNC-01 | CNC-01 | PI12615 | Verified | Acid chemical injection line needs support. | B | P | James Beech | McD | 2019-10-29 | James Beech | Const | 2019-12-09 | James Beech | 2020-01-02 | William Mitchell
CNC-01 | CNC-01 | PI16105 | Verified | 1C-CNCPI-0106; Discharge Pressure Indicator needs to be changed, interior of lens covered with blue material, cannot read scale | B | I | William Mitchell | McD | 2020-01-16 | William Mitchell | Comm | 2020-03-07 | William Mitchell | 2020-03-09 | Dave Goldak
CNC-01 | CNC-01 | PI16106 | Verified | Calbiration Column Vent needs screen cap fitting | C | I | Gonzalo Pena | McD | 2020-01-16 | Gonzalo Pena | Comm | 2020-01-29 | Gonzalo Pena | 2020-02-05 | Blake Boudreaux
CNC-01 | CNC-01 | PI16107 | Verified | Top seal at Calbiration Column is leaking | B | I | Gonzalo Pena | McD | 2020-01-16 | Gonzalo Pena | Comm | 2020-01-31 | Gonzalo Pena | 2020-02-05 | Blake Boudreaux
CNC-01 | CNC-01 | PI16108 | Verified | Condensate Aqueous Ammonina Feed System does not match vendor P&ID | C | P | Charles Worthington | McD | 2020-01-16 | Charles Worthington | Comm | 2020-10-22 | Jason Ezell | 2021-01-25 | Dave Goldak
CNC-01 | CNC-01 | PI16109 | Verified | Clean up Condensate Aqueous Ammonia Feed System skid | C | C | Alan Huntsman | McD | 2020-01-16 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-04-08 | Bernard Stasse
CNC-01 | CNC-01 | PI16110 | Verified | Seal bush hammered surface of Condensate Ammonia Feed System concrete pad | C | C | Johnny Campbell | McD | 2020-01-16 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-04-08 | Bernard Stasse
CNC-01 | CNC-01 | PI18024 | Verified | 1C-CNC-SKD-0100 - An ammonia leak was found. Ammonia leaked into the pressure gauge on the discharge of ammonia injection pumps. The operator closed the valve to isolate gauge from pumps. | C | M | William Mitchell | McD | 2020-03-17 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2020-12-08 | Dave Goldak
CNM-01 | CNM-01 | PI04365 | Verified | 1C-CNM-V-0035 missing valve handle | A | P | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-08-28 | Damon Turner | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI04599 | Verified | On ISO 1C-CNM-PD-P41-0143-01 install eng supports per iso detail | A | P | Bobby Williams | McD | 2019-08-24 | Bobby Williams | Const | 2019-08-28 | Damon Turner | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI04600 | Verified | On ISO 1C-CNM-PD-P41-0144-01 install eng supports per iso detail | A | P | Bobby Williams | McD | 2019-08-24 | Bobby Williams | Const | 2019-08-28 | Damon Turner | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI06115 | Verified | 1ACNMC0004, Pull Cable - duplicate of 6149 | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06116 | Verified | 1ACNMK0001, Pull Cable - duplicate of 6150 | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06117 | Verified | 1ACNMX0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06118 | Verified | 1AMBSX0021, Pull Cable - duplicate of 6152 | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06119 | Verified | 1BCNMX0001, Pull Cable - duplicate of 6155 | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06120 | Verified | 1CCNMC0012, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06121 | Verified | 1CCNMC0013, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06122 | Verified | 1CCNMC0014, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06123 | Verified | 1CCNMH0001A, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06124 | Verified | 1CCNMH0001B, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06125 | Verified | 1CCNMH0001C, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06126 | Verified | 1CCNMH0001G, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06127 | Verified | 1CCNMH0003A, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06128 | Verified | 1CCNMH0003B, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06129 | Verified | 1CCNMH0003C, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06130 | Verified | 1CCNMH0003G, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06131 | Verified | 1CCNMK0004, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06132 | Verified | 1CCNMK0005, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06133 | Verified | 1CCNMK0006, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06134 | Verified | 1CCNMK0007, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-09-17 | Michael Law | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06135 | Verified | 1CCNMX0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06136 | Verified | 1CCNMX0002, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06137 | Verified | 1CCNMX0007, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06138 | Verified | 1CCNMX0008, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06139 | Verified | 1CCNMX0009, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06140 | Verified | 1CCNMX0010, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06141 | Verified | 1CCNMX0013, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06142 | Verified | 1CCNMX0017, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06143 | Verified | 1CCNMX0018, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06144 | Verified | 1CCNMX0019, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06145 | Verified | 1CCNMX0020, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06146 | Verified | 1CCNMX0021, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06147 | Verified | 1CCNMX0022, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06148 | Verified | 1CCNMX0023, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06149 | Verified | 1ACNMC0004, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06150 | Verified | 1ACNMK0001, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06151 | Verified | 1ACNMX0001, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06152 | Verified | 1AMBSX0021, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06153 | Verified | 1BCNMC0004, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06154 | Verified | 1BCNMK0001, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06155 | Verified | 1BCNMX0001, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CNM-01 | CNM-01 | PI06156 | Verified | 1CASFC0015, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
CNM-01 | CNM-01 | PI06157 | Verified | 1CCNMC0001, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
CNM-01 | CNM-01 | PI06158 | Verified | 1CCNMC0002, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CNM-01 | CNM-01 | PI06159 | Verified | 1CCNMC0003, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CNM-01 | CNM-01 | PI06160 | Verified | 1CCNMC0004, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CNM-01 | CNM-01 | PI06161 | Verified | 1CCNMC0011, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-11-11 | Mike Tabbert | 2019-11-11 | Mike Tabbert
CNM-01 | CNM-01 | PI06162 | Verified | 1CCNMC0012, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06163 | Verified | 1CCNMC0013, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06164 | Verified | 1CCNMC0014, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06165 | Verified | 1CCNMC0015, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CNM-01 | CNM-01 | PI06166 | Verified | 1CCNMC0016, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06167 | Verified | 1CCNMC0017, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CNM-01 | CNM-01 | PI06168 | Verified | 1CCNMC0018, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CNM-01 | CNM-01 | PI06169 | Verified | 1CCNMC0020, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
CNM-01 | CNM-01 | PI06170 | Verified | 1CCNMC0021, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06171 | Verified | 1CCNMC0024, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06172 | Verified | 1CCNMH0001A, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06173 | Verified | 1CCNMH0001B, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06174 | Verified | 1CCNMH0001C, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06175 | Verified | 1CCNMH0001G, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06176 | Verified | 1CCNMH0002A, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-09-24 | Michael Law | 2019-09-25 | Michael Law
CNM-01 | CNM-01 | PI06177 | Verified | 1CCNMH0002B, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-09-24 | Michael Law | 2019-09-25 | Michael Law
CNM-01 | CNM-01 | PI06178 | Verified | 1CCNMH0002C, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-09-24 | Michael Law | 2019-09-25 | Michael Law
CNM-01 | CNM-01 | PI06179 | Verified | 1CCNMH0002G, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-09-24 | Michael Law | 2019-09-25 | Michael Law
CNM-01 | CNM-01 | PI06180 | Verified | 1CCNMH0003A, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06181 | Verified | 1CCNMH0003B, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06182 | Verified | 1CCNMH0003C, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06183 | Verified | 1CCNMH0003G, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06184 | Verified | 1CCNMK0001, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06185 | Verified | 1CCNMK0002, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
CNM-01 | CNM-01 | PI06186 | Verified | 1CCNMK0003, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CNM-01 | CNM-01 | PI06187 | Verified | 1CCNMK0004, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06188 | Verified | 1CCNMK0005, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06189 | Verified | 1CCNMK0006, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06190 | Verified | 1CCNMK0007, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06191 | Verified | 1CCNMX0001, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06192 | Verified | 1CCNMX0002, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06193 | Verified | 1CCNMX0003, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
CNM-01 | CNM-01 | PI06194 | Verified | 1CCNMX0004, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
CNM-01 | CNM-01 | PI06195 | Verified | 1CCNMX0005, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
CNM-01 | CNM-01 | PI06196 | Verified | 1CCNMX0006, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
CNM-01 | CNM-01 | PI06197 | Verified | 1CCNMX0007, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06198 | Verified | 1CCNMX0008, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CNM-01 | CNM-01 | PI06199 | Verified | 1CCNMX0009, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CNM-01 | CNM-01 | PI06200 | Verified | 1CCNMX0010, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CNM-01 | CNM-01 | PI06201 | Verified | 1CCNMX0011, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CNM-01 | CNM-01 | PI06202 | Verified | 1CCNMX0012, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06203 | Verified | 1CCNMX0013, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06204 | Verified | 1CCNMX0015, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CNM-01 | CNM-01 | PI06205 | Verified | 1CCNMX0016, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CNM-01 | CNM-01 | PI06206 | Verified | 1CCNMX0017, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06207 | Verified | 1CCNMX0018, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CNM-01 | CNM-01 | PI06208 | Verified | 1CCNMX0019, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06209 | Verified | 1CCNMX0020, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06210 | Verified | 1CCNMX0021, Pull and Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CNM-01 | CNM-01 | PI06211 | Verified | 1CCNMX0022, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06212 | Verified | 1CCNMX0023, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06213 | Verified | 1CCNMX0026, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
CNM-01 | CNM-01 | PI06214 | Verified | 1CCNMX0027, Terminate Cable | A | E | Dustin Futrell | McD | 2019-09-14 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CNM-01 | CNM-01 | PI06244 | Verified | RAK-9065 install seal tight conduit | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CNM-01 | CNM-01 | PI06245 | Verified | PSL-9009A/B/C to rework conduit, install low point drain | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-24 | Brad Stanford | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06246 | Verified | PIT-0003B no conduit | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const |  |  | 2019-11-23 | Zinda Harris
CNM-01 | CNM-01 | PI06247 | Verified | PIT-0003B no tubing | A | I | Gonzalo Pena | McD | 2019-09-16 | Gonzalo Pena | Const | 2019-09-19 | Gonzalo Pena | 2019-09-28 | Mike Tabbert
CNM-01 | CNM-01 | PI06248 | Verified | PIT-0003A no tubing | A | I | Gonzalo Pena | McD | 2019-09-16 | Gonzalo Pena | Const | 2019-09-19 | Gonzalo Pena | 2019-09-28 | Mike Tabbert
CNM-01 | CNM-01 | PI06249 | Verified | PIT-0003A ground seal tight | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06250 | Verified | AOV-0205 conduit to complete | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06251 | Verified | PIT-0206 need tag on instrument | B | I | Gonzalo Pena | McD | 2019-09-16 | Gonzalo Pena | Const | 2019-09-19 | Gonzalo Pena | 2019-09-28 | Mike Tabbert
CNM-01 | CNM-01 | PI06252 | Verified | LV-0031 complete conduit, seal tight | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06253 | Verified | LV-0034 complete conduit, seal tight | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06254 | Verified | LV-0034 rework bend tubing | A | I | Gonzalo Pena | McD | 2019-09-16 | Gonzalo Pena | Const | 2019-09-20 | Gonzalo Pena | 2019-09-28 | Mike Tabbert
CNM-01 | CNM-01 | PI06255 | Verified | TE-0007 not installed - need weld on thermowell | A | P | Bobby Williams | McD | 2019-09-16 | Bobby Williams | Const | 2019-10-10 | Gonzalo Pena | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06256 | Verified | TE-0007 no conduit | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06257 | Verified | FV-0222 rework bend tubing | A | I | Gonzalo Pena | McD | 2019-09-16 | Gonzalo Pena | Const | 2019-09-20 | Gonzalo Pena | 2019-09-28 | Mike Tabbert
CNM-01 | CNM-01 | PI06258 | Verified | FV-0222 no conduit | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-28 | Albert Burge
CNM-01 | CNM-01 | PI06259 | Verified | LIT-0004A/B/C not installed | A | I | Gonzalo Pena | McD | 2019-09-16 | Gonzalo Pena | Const | 2019-10-23 | Gonzalo Pena | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06260 | Verified | LG-0005 not installed | A | P | Bobby Williams | McD | 2019-09-16 | Bobby Williams | Const | 2019-10-16 | James Beech | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06261 | Verified | PDIT-0110 missing | A | I | Gonzalo Pena | McD | 2019-09-16 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-09-28 | Mike Tabbert
CNM-01 | CNM-01 | PI06262 | Verified | TE-0107 no conduit | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06263 | Verified | MOV-0105A/B/C not wired | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
CNM-01 | CNM-01 | PI06264 | Verified | MOV-0105A/B/C ground seal tights | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-10-05 | Mike Tabbert
CNM-01 | CNM-01 | PI06265 | Verified | CNM motor pumps M-0001A/B/C ground the motor to the grid | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06266 | Verified | CNM motor pumps M-0001A/B/C ground all stub ups conduit and seal tights. | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-24 | Brad Stanford | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06267 | Verified | TP-5581 and 5582 not installed | A | I | Gonzalo Pena | McD | 2019-09-16 | Gonzalo Pena | Const | 2019-09-20 | Gonzalo Pena | 2019-09-20 | Mike Tabbert
CNM-01 | CNM-01 | PI06268 | Verified | PDIT-0050A/B/C tubing not installed | A | I | Gonzalo Pena | McD | 2019-09-16 | Gonzalo Pena | Const | 2019-10-09 | Gonzalo Pena | 2019-10-15 | Albert Burge
CNM-01 | CNM-01 | PI06269 | Verified | V-0042 A/B/C no conduit | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-11-20 | Fred Michael
CNM-01 | CNM-01 | PI06270 | Verified | V-0042 A/B/C no tubing | A | I | Gonzalo Pena | McD | 2019-09-16 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-28 | Mike Tabbert
CNM-01 | CNM-01 | PI06271 | Verified | V-0042 A/B/C no tag | B | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-11-02 | Brad Stanford | 2019-11-20 | Fred Michael
CNM-01 | CNM-01 | PI06272 | Verified | PV-0206 replace damaged tubing | A | I | Gonzalo Pena | McD | 2019-09-16 | Gonzalo Pena | Const | 2019-09-20 | Gonzalo Pena | 2019-09-28 | Mike Tabbert
CNM-01 | CNM-01 | PI06273 | Verified | PV-0206 conduit incomplete | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06274 | Verified | LV-0242 need to ground seal tight | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const |  |  | 2019-09-28 | Mike Tabbert
CNM-01 | CNM-01 | PI06275 | Verified | TP-0121 is blocked by toe plate. Clear block | A | S | Bobby Williams | McD | 2019-09-16 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06276 | Verified | MOV-0037 no conduit | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06277 | Verified | RAK-9065 needs ground | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-18 | Brad Stanford | 2019-11-23 | Michael Law
CNM-01 | CNM-01 | PI06278 | Verified | Grout all instrument and conduit stands for CNM-01 | C | C | Johnny Campbell | McD | 2019-09-16 | Johnny Campbell | Const | 2019-10-22 | Johnny Campbell | 2019-12-12 | Fred Michael
CNM-01 | CNM-01 | PI06279 | Verified | LK-1B-CNM-PD-P41-0286-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06280 | Verified | LK-1B-FWS-PD-P40-0207-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06281 | Verified | LK-1B-FWS-PD-P40-0212-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06282 | Verified | LK-1B-HRS-PD-P40-0025-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06283 | Verified | LK-1B-HRS-PD-P40-0040-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06284 | Verified | LK-1B-HRS-PD-P40-0040-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06285 | Verified | LK-1B-HRS-PD-P40-0045-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06286 | Verified | LK-1B-HRS-PD-P41-0007-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06287 | Verified | LK-1B-HRS-PD-P41-0007-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06288 | Verified | LK-1B-HRS-PD-P41-0040-04 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06289 | Verified | LK-1B-HRS-PD-P41-0040-05 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06290 | Verified | LK-1B-HRS-PD-P41-0040-06 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06291 | Verified | LK-1B-HRS-PD-P41-0040-07 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06292 | Verified | LK-1B-HRS-PD-P41-0045-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06293 | Verified | LK-1C-ASF-PD-P41-0051-06 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06294 | Verified | LK-1C-CNM-PD-P40-0097-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06295 | Verified | LK-1C-CNM-PD-P40-0100-04 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06296 | Verified | LK-1C-CNM-PD-P40-0101-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06297 | Verified | LK-1C-CNM-PD-P40-0130-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06298 | Verified | LK-1C-CNM-PD-P40-0130-03 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06299 | Verified | LK-1C-CNM-PD-P40-0140-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06300 | Verified | LK-1C-CNM-PD-P40-0260-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06301 | Verified | LK-1C-CNM-PD-P41-0002-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06302 | Verified | LK-1C-CNM-PD-P41-0002-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06303 | Verified | LK-1C-CNM-PD-P41-0003-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06304 | Verified | LK-1C-CNM-PD-P41-0003-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06305 | Verified | LK-1C-CNM-PD-P41-0005-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06306 | Verified | LK-1C-CNM-PD-P41-0005-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06307 | Verified | LK-1C-CNM-PD-P41-0065-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06308 | Verified | LK-1C-CNM-PD-P41-0100-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06309 | Verified | LK-1C-CNM-PD-P41-0100-03 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06310 | Verified | LK-1C-CNM-PD-P41-0101-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06311 | Verified | LK-1C-CNM-PD-P41-0102-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06312 | Verified | LK-1C-CNM-PD-P41-0102-04 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06313 | Verified | LK-1C-CNM-PD-P41-0130-03 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06314 | Verified | LK-1C-LPS-PD-P41-0036-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06315 | Verified | LK-1C-LPS-PD-P41-0049-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06316 | Verified | LK-1C-LPS-PD-P41-0056-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06317 | Verified | LK-1C-STE-PD-P40-0010-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06318 | Verified | LK-1C-STE-PD-P40-0016-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06319 | Verified | LK-1C-STE-PD-P40-0016-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06320 | Verified | LK-1C-STE-PD-P40-0018-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06321 | Verified | LK-1C-STE-PD-P40-0025-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06322 | Verified | LK-1C-STE-PD-P41-0012-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
CNM-01 | CNM-01 | PI06323 | Verified | On ISO 1C-CNM-PD-P40-0034-01 valve handle missing on 1C-CNM-V-0035 | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-15 | Bobby Williams | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI06324 | Verified | On ISO 1C-CNM-PD-P40-0042-01 Valve handle missing on 1C-CNM-V-0042A | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06325 | Verified | On ISO 1C-CNM-PD-P40-0045-01 Valve 1C-CNM-V-0042B is missing hardware | A | P | Damon Turner | McD | 2019-09-18 | Damon Turner | Const | 2019-09-25 | Bobby Williams | 2019-10-05 | Kelvin Cook
CNM-01 | CNM-01 | PI06326 | Verified | On ISO 1C-CNM-PD-P40-0047-01 Valve 1C-CNM-V-0047C is missing hardware | A | P | Damon Turner | McD | 2019-09-18 | Damon Turner | Const | 2019-09-25 | Bobby Williams | 2019-10-05 | Kelvin Cook
CNM-01 | CNM-01 | PI06327 | Verified | On ISO 1C-CNM-PD-P40-0050-01 adjust bolts nuts evenly at restraining rods on 1C-CNM-EJ-0001A | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06328 | Verified | On ISO 1C-CNM-PD-P40-0055-01 adjust bolts nuts evenly at restraining rods on 1C-CNM-EJ-0001B | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06329 | Verified | On ISO 1C-CNM-PD-P40-0060-01 loose nuts at restraining bar & loose nuts at bolts on 1C-CNM-EJ-0001C | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06330 | Verified | On ISO 1C-CNM-PD-P40-0100-01 rotate valve 1C-CNM-MOV-0105A to the east | A | P | Damon Turner | McD | 2019-09-18 | Damon Turner | Const | 2019-09-25 | Bobby Williams | 2019-10-05 | Kelvin Cook
CNM-01 | CNM-01 | PI06331 | Verified | On ISO 1C-CNM-PD-P40-0100-01 at flange connection to 1C-CNM-P-0001A/N2 missing hardware | A | P | Damon Turner | McD | 2019-09-18 | Damon Turner | Const | 2019-09-25 | Bobby Williams | 2019-10-05 | Kelvin Cook
CNM-01 | CNM-01 | PI06332 | Verified | On ISO 1C-CNM-PD-P40-0100-02 remove rope spool 0100-1 | C | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06333 | Verified | On ISO 1C-CNM-PD-P40-0100-02 pipe support 1C-CNM-PD-HGR-0011 is out of plumb | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-26 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06334 | Verified | On ISO 1C-CNM-PD-P40-0100-03 instrument 1C-CNM-FE-0110 is not installed | B | P | William Mitchell | McD | 2019-09-18 | William Mitchell | Const | 2019-12-15 | Michael Law | 2019-12-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06335 | Verified | On ISO 1C-CNM-PD-P40-0100-03 rotate valve 1C-CNM-V-0114 down | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-26 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06336 | Verified | On ISO 1C-CNM-PD-P40-0100-04 remove rigging from spool 0100-1 | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06337 | Verified | On ISO 1C-CNM-PD-P40-0100-04 remove lashing from spool 0100-2 | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06338 | Verified | On ISO 1C-CNM-PD-P40-0101-1 rotate valve 1C-CNM-MOV-0105B to the east | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06339 | Verified | On ISO 1C-CNM-PD-P40-0101-1 at flange connection to 1C-CNM-P-0001B/N2 missing gasket and missing hardware | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06340 | Verified | On ISO 1C-CNM-PD-P40-0102-01 rotate valve 1C-CNM-MOV-0105C to the east | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06341 | Verified | On ISO 1C-CNM-PD-P40-0116-01 pipe support 1C-CNM-PD-HGR-0107 is not intalled | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-02 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06342 | Verified | On ISO 1C-CNM-PD-P40-0130-01 specialty item 1C-CNM-QUIL-0135 is not intalled | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-16 | James Beech | 2019-11-08 | Kelvin Cook
CNM-01 | CNM-01 | PI06343 | Verified | On ISO 1C-CNM-PD-P40-0130-01 install temporary trim pipe for hydro | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-02 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06344 | Verified | On ISO 1C-CNM-PD-P40-0130-01 Reinstall pipe after hydro | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-18 | Michael Law | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI06345 | Verified | On ISO 1C-CNM-PD-P40-0130-02 pipe support 1C-CNM-PD-HGR-0032 & 0033 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06346 | Verified | On ISO 1C-CNM-PD-P40-0130-03 pipe support 1C-CNM-PD-HGR-0001 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06347 | Verified | On ISO 1C-CNM-PD-P40-0131-01 pipe support 1C-CNM-PD-HGR-0035 is not installed | B | P | James Beech | McD | 2019-09-18 | James Beech | Const |  |  | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06348 | Verified | On ISO 1C-CNM-PD-P40-0140-01 pipe support 1C-CNM-PD-HGR-0111 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-08 | Kelvin Cook
CNM-01 | CNM-01 | PI06349 | Verified | On ISO 1C-CNM-PD-P40-0140-01 pipe support 1C-CNM-PD-HGR-0109 missing ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06350 | Verified | On ISO 1C-CNM-PD-P40-0140-02 pipe support 1C-CNM-PD-HGR-0112 missing ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06351 | Verified | On ISO 1C-CNM-PD-P40-0200-01 pipe support 1C-CNM-PD-HGR-0036 & 0038 have loose ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06352 | Verified | On ISO 1C-CNM-PD-P40-0200-01 remove wood from pipe support 1C-CNM-PD-HGR-0037 and complete support | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06353 | Verified | On ISO 1C-CNM-PD-P40-0200-02 pipe support 1C-CNM-PD-HGR-0039 has loose nuts at turnbuckle | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06354 | Verified | On ISO 1C-CNM-PD-P40-0200-02 pipe support 1C-CNM-PD-HGR-0040 is not installed | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06355 | Verified | On ISO 1C-CNM-PD-P40-0205-01 pipe support 1C-CNM-PD-HGR-0049 missing ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06356 | Verified | On ISO 1C-CNM-PD-P40-0205-01 pipe support 1C-CNM-PD-HGR-0050 loose ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06357 | Verified | On ISO 1C-CNM-PD-P40-0205-02 pipe support 1C-CNM-PD-HGR-0053 loose nuts at ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06358 | Verified | On ISO 1C-CNM-PD-P40-0205-03 pipe support 1C-CNM-PD-HGR-0056 need full thread engagement at bottom of eye bolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06359 | Verified | On ISO 1C-CNM-PD-P40-0240-02 pipe support 1C-CNM-PD-HGR-0043 Incomplete weld on guides | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06360 | Verified | On ISO 1C-CNM-PD-P40-0241-01 pipe support 1C-CNM-PD-HGR-0044 Incomplete weld on guides | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06361 | Verified | On ISO 1C-CNM-PD-P40-0241-01 pipe support 1C-CNM-PD-HGR-0045 missing second set of nuts at ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06362 | Verified | On ISO 1C-CNM-PD-P40-0241-01 pipe support 1C-CNM-PD-HGR-0046 has loose ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06363 | Verified | On ISO 1C-CNM-PD-P40-0260-01 pipe support 1C-CNM-PD-HGR-0058 is not installed | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06364 | Verified | On ISO 1C-CNM-PD-P40-0260-01 Remove rigging on pipe at field weld 1 | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06365 | Verified | On ISO 1C-CNM-PD-P40-0260-02 Remove rigging on spool 0260-1 | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06366 | Verified | On ISO 1C-CNM-PD-P40-0260-02 pipe support 1C-CNM-PD-HGR-0057 is not installed | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06367 | Verified | On ISO 1C-CNM-PD-P41-0008-01 instrument 1C-CNM-PSL-9009A is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-10-11 | James Beech | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06368 | Verified | On ISO 1C-CNM-PD-P41-0031-02 pipe support 1C-CNM-PD-HGR-0243 has loose nuts at ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-26 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06369 | Verified | On ISO 1C-CNM-PD-P41-0031-03 pipe support 1C-CNM-PD-HGR-0239 & 0240 & 241 are not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-02 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06370 | Verified | On ISO 1C-CNM-PD-P41-0040-01 pipe support 1C-CNM-PD-HGR-0222 has loose ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06371 | Verified | On ISO 1C-CNM-PD-P41-0041-01 threaded cap is not intalled | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06372 | Verified | On ISO 1C-CNM-PD-P41-0041-01 rework spool 0041-1 need to level on slight slope | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06373 | Verified | On ISO 1C-CNM-PD-P41-0042-01 instrument 1C-CNM-PP-0040A is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-19 | Gonzalo Pena | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06374 | Verified | On ISO 1C-CNM-PD-P41-0042-02 at flange connection to 1C-CNM-SRV-0045A bolts too short | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06375 | Verified | On ISO 1C-CNM-PD-P41-0045-01 instrument 1C-CNM-PP-0040B is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-19 | Gonzalo Pena | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06376 | Verified | On ISO 1C-CNM-PD-P41-0045-02 at flange connection to 1C-CNM-SRV-0045B bolts too short | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06377 | Verified | On ISO 1C-CNM-PD-P41-0047-01 instrument 1C-CNM-PP-0040C is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-19 | Gonzalo Pena | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06378 | Verified | On ISO 1C-CNM-PD-P41-0047-02 at flange connection to 1C-CNM-SRV-0045C bolts too short | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06379 | Verified | On ISO 1C-CNM-PD-P41-0051-01 bent valve handle or valve shaft for 1C-CNM-V-0051A | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-04 | Damon Turner | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI06380 | Verified | On ISO 1C-CNM-PD-P41-0052-01 instrument 1C-CNM-PDIT-0050A is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Kelvin Cook
CNM-01 | CNM-01 | PI06381 | Verified | On ISO 1C-CNM-PD-P41-0052-01 at connection to 1C-CNM-STN-0050A/DIFF Press no pipe dope 2nos | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06382 | Verified | On ISO 1C-CNM-PD-P41-0052-02 pipe support 1C-CNM-PD-HGR-0198 is not installed | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06383 | Verified | On ISO 1C-CNM-PD-P41-0052-03 pipe support 1C-CNM-PD-HGR-0205 has no ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06384 | Verified | On ISO 1C-CNM-PD-P41-0057-01 at connection to 1C-CNM-STN-0050B/DIFF Press no pipe dope 2nos | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06385 | Verified | On ISO 1C-CNM-PD-P41-0057-01 instrument 1C-CNM-PDIT-0050B is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Kelvin Cook
CNM-01 | CNM-01 | PI06386 | Verified | On ISO 1C-CNM-PD-P41-0057-02 pipe support 1C-CNM-PD-HGR-0168 is not installed | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06387 | Verified | On ISO 1C-CNM-PD-P41-0057-03 pipe support 1C-CNM-PD-HGR-0175 has no ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06388 | Verified | On ISO 1C-CNM-PD-P41-0062-01 pipe support 1C-CNM-PD-HGR-0176 Is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-02 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06389 | Verified | On ISO 1C-CNM-PD-P41-0062-02 pipe support 1C-CNM-PD-HGR-0183 Is not installed | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06390 | Verified | On ISO 1C-CNM-PD-P41-0062-02 pipe support 1C-CNM-PD-HGR-0189 & 0190 has loose ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-11 | Kelvin Cook
CNM-01 | CNM-01 | PI06391 | Verified | On ISO 1C-CNM-PD-P41-0063-01 pipe support 1C-CNM-PD-HGR-0145 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-02 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06392 | Verified | On ISO 1C-CNM-PD-P41-0063-02 pipe support 1C-CNM-PD-HGR-0152 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06393 | Verified | On ISO 1C-CNM-PD-P41-0063-02 pipe support 1C-CNM-PD-HGR-0158 has loose ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06394 | Verified | On ISO 1C-CNM-PD-P41-0063-02 pipe support 1C-CNM-PD-HGR-0159 has no ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06395 | Verified | On ISO 1C-CNM-PD-P41-0064-01 pipe support 1C-CNM-PD-HGR-0113 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-02 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06396 | Verified | On ISO 1C-CNM-PD-P41-0064-02 pipe support 1C-CNM-PD-HGR-0122 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-08 | Kelvin Cook
CNM-01 | CNM-01 | PI06397 | Verified | On ISO 1C-CNM-PD-P41-0064-02 pipe support 1C-CNM-PD-HGR-0127 has loose ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06398 | Verified | On ISO 1C-CNM-PD-P41-0064-02 pipe support 1C-CNM-PD-HGR-0128 loose and crooked ubolt | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06399 | Verified | On ISO 1C-CNM-PD-P41-0088-01 pipe support 1C-CNM-PD-HGR-0129 & 0130 loose ubolt too much gap | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06400 | Verified | On ISO 1C-CNM-PD-P41-0088-01 at connection to 1C-CNM-STN-0050C/DIFF Press no pipe dope 2nos | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06401 | Verified | On ISO 1C-CNM-PD-P41-0088-01 instrument 1C-CNM-PDIT-0050C is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Kelvin Cook
CNM-01 | CNM-01 | PI06402 | Verified | On ISO 1C-CNM-PD-P41-0088-01 pipe support 1C-CNM-PD-HGR-0137 is not installed | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06403 | Verified | On ISO 1C-CNM-PD-P41-0088-02 pipe support 1C-CNM-PD-HGR-0144 crooked ubolt | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06404 | Verified | On ISO 1C-CNM-PD-P41-0100-07 instrument 1C-CNM-PP-0120 is not installed | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06405 | Verified | On ISO 1C-CNM-PD-P41-0100-08 pipe support 1C-CNM-PD-HGR-0246 missing pipe clamp | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06406 | Verified | On ISO 1C-CNM-PD-P41-0100-08 missing gasket and hardware at flange | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06407 | Verified | On ISO 1C-CNM-PD-P41-0100-08 remove teflon tape at threaded cap and at y strainer | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06408 | Verified | ISO 1C-CNM-PD-P41-0100-09 is not installed | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06409 | Verified | ISO 1C-CNM-PD-P41-0101-03 pipe support 1C-CNM-PD-HGR-0248 missing pipe clamp | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06410 | Verified | ISO 1C-CNM-PD-P41-0101-03 pipe support 1C-CNM-PD-HGR-0249 change out ubolt too much gap | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06411 | Verified | ISO 1C-CNM-PD-P41-0101-03 missing gasket and hardware at flange | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06412 | Verified | On ISO 1C-CNM-PD-P41-0101-03 remove teflon tape at threaded cop and near by as well | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06413 | Verified | ISO 1C-CNM-PD-P41-0101-04 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-16 | James Beech | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06414 | Verified | ISO 1C-CNM-PD-P41-0102-03 pipe support 1C-CNM-PD-HGR-0250 has loose ubolt and missing hose clamp | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06415 | Verified | ISO 1C-CNM-PD-P41-0102-03 missing gasket and proper bolts at flange | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-16 | James Beech | 2019-11-08 | Kelvin Cook
CNM-01 | CNM-01 | PI06416 | Verified | ISO 1C-CNM-PD-P41-0102-03 remove teflon tape at threaded cap | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06417 | Verified | ISO 1C-CNM-PD-P41-0102-04 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-16 | James Beech | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06418 | Verified | ISO 1C-CNM-PD-P41-0130-01 instrument 1C-CNM-PP-0131 is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-19 | Gonzalo Pena | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06419 | Verified | ISO 1C-CNM-PD-P41-0130-03 is not installed | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06420 | Verified | ISO 1C-CNM-PD-P41-0140-01 threaded cap is loose | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06421 | Verified | ISO 1C-CNM-PD-P41-0141-01 pipe support 1C-CNM-PD-HGR-0084 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06422 | Verified | ISO 1C-CNM-PD-P41-0141-02 threaded cap not installed at valve 1C-CNM-V-0147 | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-26 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06423 | Verified | ISO 1C-CNM-PD-P41-0141-02 pipe support 1C-CNM-PD-HGR-0094 replace bent all threaded rods | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-26 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06424 | Verified | ISO 1C-CNM-PD-P41-0141-04 pipe support 1C-CNM-PD-HGR-0079 missing nuts at pipe clamp | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06425 | Verified | ISO 1C-CNM-PD-P41-0141-04 pipe support 1C-CNM-PD-HGR-0080 is out of plumb | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06426 | Verified | ISO 1C-CNM-PD-P41-0141-04 pipe support 1C-CNM-PD-HGR-0069 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06427 | Verified | ISO 1C-CNM-PD-P41-0141-04 pipe support 1C-CNM-PD-HGR-0082 remove rope | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06428 | Verified | ISO 1C-CNM-PD-P41-0141-05 remove rope from pipe just off pipe support 1C-CNM-PD-HGR-0072 | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06429 | Verified | ISO 1C-CNM-PD-P41-0200-01 threaded cap not installed at valve 1C-CNM-V-0224 | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06430 | Verified | ISO 1C-CNM-PD-P41-0205-01 threaded cap not installed at valve 1C-CNM-V-0204 | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06431 | Verified | ISO 1C-CNM-PD-P41-0210-01 pipe support 1C-CNM-PD-HGR-0097 is not installed | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06432 | Verified | ISO 1C-CNM-PD-P41-0240-01 threaded cap not installed at valve 1C-CNM-V-0241 | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06433 | Verified | valve 1C-CNM-V-0071C Is not installed at 1C-CNM-P-0001C | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-02 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06434 | Verified | valve 1C-CNM-V-0071B Is not installed at 1C-CNM-P-0001B | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-02 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06435 | Verified | valve 1C-CNM-V-0071A Is not installed at 1C-CNM-P-0001A | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-02 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06436 | Verified | On ISO 1A-CNM-PD-P40-0280-03 valve 1A-CNM-V-0280 for commissioning to restore after hydro | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-12-04 | Bobby Williams | 2019-12-14 | Kelvin Cook
CNM-01 | CNM-01 | PI06437 | Verified | On ISO 1A-CNM-PD-P40-0280-04 pipe support 1A-CNM-PD-HGR-0206 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const |  |  | 2019-11-12 | Bobby Williams
CNM-01 | CNM-01 | PI06438 | Verified | On ISO 1A-CNM-PD-P40-0280-04 pipe support 1A-CNM-PD-HGR-0204 & 0205 install per detail | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06439 | Verified | On ISO 1A-CNM-PD-P40-0291-01 pipe support 1A-CNM-PD-HGR-0207 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06440 | Verified | ISO 1A-CNM-PD-P41-0280-01 is not installed | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06441 | Verified | ISO 1A-CNM-PD-P41-0280-02 is not installed | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06442 | Verified | ISO 1A-CNM-PD-P41-0280-05 to be installed after hydro degrease | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-12-04 | Bobby Williams | 2019-12-14 | Kelvin Cook
CNM-01 | CNM-01 | PI06443 | Verified | ISO 1A-CNM-PD-P41-0280-06 to be installed after hydro degrease | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-12-04 | Bobby Williams | 2019-12-14 | Kelvin Cook
CNM-01 | CNM-01 | PI06444 | Verified | ISO 1A-CNM-PD-P41-0285-01 pipe spool 0285-2 is not installed | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06445 | Verified | ISO 1A-CNM-PD-P41-0285-01 pipe supports 1A-CNM-PD-HGR-0229 & 0230 & 0228 & 0227 are not installed | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06446 | Verified | ISO 1A-CNM-PD-P41-0285-02 is not intalled | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06447 | Verified | ISO 1A-CNM-PD-P41-0286-01 is not intalled | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06448 | Verified | On ISO 1B-CNM-PD-P40-0280-01 pipe support 1B-CNM-PD-HGR-0030 loose nut at eyebolt tighten bolts at 66 lug | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06449 | Verified | On ISO 1B-CNM-PD-P40-0280-01 pipe support 1B-CNM-PD-HGR-0213 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06450 | Verified | On ISO 1B-CNM-PD-P40-0280-04 remove rigging from spool 0280-1 | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06451 | Verified | On ISO 1B-CNM-PD-P40-0280-04 pipe support 1B-CNM-PD-HGR-0216 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-15 | Bobby Williams | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI06452 | Verified | On ISO 1B-CNM-PD-P40-0280-04 pipe support 1B-CNM-PD-HGR-0215 verify out of plumb | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06453 | Verified | On ISO 1B-CNM-PD-P40-0280-04 pipe support 1B-CNM-PD-HGR-0217 has loose nut, needs full thread engagement at eyebolt and has loose clamp | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06454 | Verified | On ISO 1B-CNM-PD-P40-0280-01 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06455 | Verified | On ISO 1B-CNM-PD-P40-0280-02 missing threaded cap | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06456 | Verified | On ISO 1B-CNM-PD-P41-0280-05 install after hydro degrease | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-12-04 | Bobby Williams | 2019-12-14 | Kelvin Cook
CNM-01 | CNM-01 | PI06457 | Verified | On ISO 1B-CNM-PD-P41-0280-04 install after hydro degrease | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-15 | Bobby Williams | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI06458 | Verified | On ISO 1B-CNM-PD-P41-0285-01 pipe support 1B-CNM-PD-HGR-0235 is not installed | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06459 | Verified | On ISO 1B-CNM-PD-P40-0285-02 is not installed | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06460 | Verified | On ISO 1B-CNM-PD-P40-0286-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06461 | Verified | On ISO 1C-CNM-PD-P40-0240-03, 6" 300# isolation kit at the UG is not installed. Has the wrong bolts, remove PTFE and install proper bolts. | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-15 | Bobby Williams | 2019-12-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06462 | Verified | On ISO 1C-CNM-PD-P40-0240-03 remove plastic at UG flange | C | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06463 | Verified | On ISO 1C-CNM-PD-P41-0002-01 instrument 1C-CNM-LIT-0004A is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Kelvin Cook
CNM-01 | CNM-01 | PI06464 | Verified | On ISO 1C-CNM-PD-P41-0002-02 instrument 1C-CNM-LIT-0004A is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Kelvin Cook
CNM-01 | CNM-01 | PI06465 | Verified | On ISO 1C-CNM-PD-P41-0003-01 instrument 1C-CNM-LIT-0004B is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Kelvin Cook
CNM-01 | CNM-01 | PI06466 | Verified | On ISO 1C-CNM-PD-P41-0003-02 instrument 1C-CNM-LIT-0004B is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Kelvin Cook
CNM-01 | CNM-01 | PI06467 | Verified | On ISO 1C-CNM-PD-P41-0005-01 instrument 1C-CNM-LG-0005 is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Kelvin Cook
CNM-01 | CNM-01 | PI06468 | Verified | On ISO 1C-CNM-PD-P41-0005-02 instrument 1C-CNM-LG-0005 is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Kelvin Cook
CNM-01 | CNM-01 | PI06469 | Verified | On ISO 1C-CNM-PD-P41-0007-01 is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Kelvin Cook
CNM-01 | CNM-01 | PI06470 | Verified | On ISO 1C-CNM-PD-P41-0038-01 pipe support 1C-CNM-PD-HGR-0103 missing ubolt | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06471 | Verified | On ISO 1C-CNM-PD-P41-0038-01 rework the 90. field weld is incomplete. Just off support 0100 | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06472 | Verified | On ISO 1C-CNM-PD-P41-0065-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const |  |  | 2019-11-12 | Bobby Williams
CNM-01 | CNM-01 | PI06473 | Verified | On ISO 1C-CNM-PD-P41-0100-03 Is not installed | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06474 | Verified | On ISO 1C-CNM-PD-P41-0100-04 Is not installed | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06475 | Verified | On ISO 1C-CNM-PD-P41-0100-05 Is not installed | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06476 | Verified | On ISO 1C-CNM-PD-P41-0250-01 Is not installed | A | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06477 | Verified | On ISO 1A-FWS-PD-P40-0540-01 pipe support 1A-FWS-PD-HGR-0060 is incomplete | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06478 | Verified | On ISO 1B-FWS-PD-P40-0540-01 pipe support 1B-FWS-PD-HGR-0119 is incomplete | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06479 | Verified | On ISO 1A-HRS-PD-P40-0025-01 pipe support 1A-HRS-PD-HGR-0517 has loose nut at turnbuckle. Remove rigging for thermal growth | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-04 | Bobby Williams | 2019-11-08 | Kelvin Cook
CNM-01 | CNM-01 | PI06480 | Verified | On ISO 1A-HRS-PD-P40-0025-01 pipe support 1A-HRS-PD-HGR-0535 loose nut at turnbuckle. Out of plumb. No thermal growth. | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const |  |  | 2019-11-12 | Bobby Williams
CNM-01 | CNM-01 | PI06481 | Verified | On ISO 1A-HRS-PD-P40-0025-02 pipe support 1A-HRS-PD-HGR-0540 has loose nut | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-12 | Kelvin Cook
CNM-01 | CNM-01 | PI06482 | Verified | On ISO 1A-HRS-PD-P40-0025-03 pipe support 1A-HRS-PD-HGR-0523 has loose bolts at shoe | B | P | James Beech | McD | 2019-09-18 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-10-19 | Kelvin Cook
CNM-01 | CNM-01 | PI06483 | Verified | On ISO 1A-HRS-PD-P41-0025-02 instrument 1A-HRS-PIT-0025 is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-08 | Kelvin Cook
CNM-01 | CNM-01 | PI06484 | Verified | ISO 1A-HRS-PD-P40-0040-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-23 | James Beech | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI06485 | Verified | On ISO 1A-HRS-PD-P40-0040-02 pipe support 1A-HRS-PD-HGR-0037 set shoe proper on support | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const |  |  | 2019-11-12 | Bobby Williams
CNM-01 | CNM-01 | PI06486 | Verified | On ISO 1A-HRS-PD-P40-0040-02 instrument 1A-HRS-FE-0081/oulet to be installed after steam blows | B | P | Billy Williams | McD | 2019-09-18 | Billy Williams | Const |  |  | 2019-12-06 | Kelvin Cook
CNM-01 | CNM-01 | PI06487 | Verified | ISO 1A-HRS-PD-P41-0040-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-16 | James Beech | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06488 | Verified | On ISO 1B-HRS-PD-P40-0025-01 pipe support 1B-HRS-PD-HGR-0532 loose nut at turn buckle | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-25 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06489 | Verified | On ISO 1B-HRS-PD-P40-0025-01 pipe support 1B-HRS-PD-HGR-0518 loose nut at turn buckle. 2 thread min at 3 bolt clamp. | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-22 | Bobby Williams | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI06490 | Verified | ISO 1B-HRS-PD-P40-0040-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-16 | James Beech | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI06491 | Verified | On ISO 1B-HRS-PD-P40-0040-02 pipe suppport 1B-HRS-PD-HGR-0039 set shoe proper on support | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const |  |  | 2019-11-12 | Bobby Williams
CNM-01 | CNM-01 | PI06492 | Verified | ISO 1B-HRS-PD-P41-0040-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-16 | James Beech | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06493 | Verified | On ISO 1B-HRS-PD-P41-00025-02 instrument 1B-HRS-PIT-0025 is not installed | A | I | Gonzalo Pena | McD | 2019-09-18 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06494 | Verified | On ISO 1C-ASF-PD-P40-0080-01 pipe support pipe support 1C-ASF-PD-HGR-0016 & 0017 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const |  |  | 2019-11-12 | Bobby Williams
CNM-01 | CNM-01 | PI06495 | Verified | On ISO 1C-ASF-PD-P40-0080-03 remove rigging from spool 0080-1 | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-26 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06496 | Verified | On ISO 1C-ASF-PD-P40-0080-02 pipe support 1C-ASF-PD-HGR-0011 fall thread at nut required on both clamp at shoe | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-26 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06497 | Verified | On ISO 1C-ASF-PD-P41-0050-01 bolts missing at both flanges | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-09 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06498 | Verified | On ISO 1C-ASF-PD-P41-0051-01 1 bolt too long at flanges closes to AOV-0050 | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-25 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06499 | Verified | On ISO 1C-ASF-PD-P41-0051-09 threaded cap is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-25 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06500 | Verified | On ISO 1C-ASF-PD-P41-0051-10 pipe support 1C-ASF-PD-HGR-0059 is loose | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const |  |  | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06501 | Verified | On ISO 1C-ASF-PD-P41-0051-10 pipe support 1C-ASF-PD-HGR-0058 missing second set of nuts on top of ubolt | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-27 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06502 | Verified | On ISO 1C-ASF-PD-P41-0051-10 spool 0051-1 out of plumb needs to be rolled north to square up | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-04 | Bobby Williams | 2019-11-08 | Kelvin Cook
CNM-01 | CNM-01 | PI06503 | Verified | On ISO 1C-ASF-PD-P41-0051-10 spool 0051-1 need to add length to square up | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-04 | Bobby Williams | 2019-11-08 | Kelvin Cook
CNM-01 | CNM-01 | PI06504 | Verified | On ISO 1C-CRS-PD-P41-0016-01 pipe supports 1C-CRS-PD-HGR-0012 & 0013 & 0014 & 0015 are not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-04 | Bobby Williams | 2019-11-08 | Kelvin Cook
CNM-01 | CNM-01 | PI06505 | Verified | ON ISO 1C-LPS-PD-P40-0025-01 pipe support 1C-LPS-PD-HGR-0537 missing anchor bolts. Loose clamp | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06506 | Verified | ON ISO 1C-LPS-PD-P40-0025-01 pipe support 1C-LPS-PD-HGR-0534 missing bottom of the support | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06507 | Verified | ISO 1C-LPS-PD-P41-0040-02 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06508 | Verified | On ISO 1C-LPS-PD-P41-0040-03 pipe support 1C-LPS-PD-HGR-0080 is not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-04 | Damon Turner | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06509 | Verified | ISO 1C-LPS-PD-P41-0041-04 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06510 | Verified | ISO 1C-LPS-PD-P41-0049-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-10 | James Beech | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06511 | Verified | ISO 1C-LPS-PD-P41-0049-02 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-10 | James Beech | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06512 | Verified | ISO 1C-LPS-PD-P41-0056-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06513 | Verified | ISO 1C-LPS-PD-P41-0056-02 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06514 | Verified | On ISO 1C-SDS-PD-P40-0058-01 pipe support 1C-SDS-PD-HGR-0008 | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const |  |  | 2019-11-12 | Bobby Williams
CNM-01 | CNM-01 | PI06515 | Verified | On ISO 1C-SDS-PD-P40-0058-01 missing cap screws at flanges connecting to valve 1C-SDS-V-0103 | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const |  |  | 2019-11-12 | Bobby Williams
CNM-01 | CNM-01 | PI06516 | Verified | On ISO 1C-SDS-PD-P40-0058-01 bolts too short south flange of valve 1C-SDS-LV-0100 | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-09 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06517 | Verified | On ISO 1C-SDS-PD-P41-0012-01 spool 0012-3 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06518 | Verified | ISO 1C-SDS-PD-P41-0012-02 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-09 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06519 | Verified | On ISO 1C-SDS-PD-P41-0013-01 spool 0013-3 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06520 | Verified | ISO 1C-SDS-PD-P41-0013-02 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-09 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06521 | Verified | ISO 1C-SDS-PD-P41-0033-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-09 | Damon Turner | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06522 | Verified | ISO 1C-SDS-PD-P41-0034-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-10 | James Beech | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06523 | Verified | On ISO 1C-SDS-PD-P41-0051-01 spool 0051-3 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-26 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06524 | Verified | ISO 1C-SDS-PD-P41-0051-02 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-09 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06525 | Verified | ISO 1C-SDS-PD-P41-0052-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06526 | Verified | ISO 1C-SDS-PD-P41-0052-02 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-09 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06527 | Verified | ISO 1C-SDS-PD-P41-0190-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-26 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06528 | Verified | ISO 1C-SDS-PD-P41-0190-02 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-26 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06529 | Verified | ISO 1C-SDS-PD-P41-0190-03 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-26 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06530 | Verified | ISO 1C-SDS-PD-P41-0190-04 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-09 | Damon Turner | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06531 | Verified | ISO 1C-SDS-PD-P41-0191-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-26 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06532 | Verified | ISO 1C-SDS-PD-P41-0191-02 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-09 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06533 | Verified | ISO 1C-SDS-PD-P41-0191-03 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-09 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06534 | Verified | ISO 1C-SDS-PD-P41-0191-04 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-09 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06535 | Verified | On ISO 1C-STE-PD-P40-0010-01 incomplete field weld 1 | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-11-01 | Bobby Williams | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI06536 | Verified | On ISO 1C-STE-PD-P40-0010-01 incomplete field weld 2 | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-16 | James Beech | 2019-11-08 | Kelvin Cook
CNM-01 | CNM-01 | PI06537 | Verified | On ISO 1C-STE-PD-P40-0016-01 pipe support 1C-STE-PD-HGR-0038 & 0039 & 0040 are not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-25 | Damon Turner | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI06538 | Verified | On ISO 1C-STE-PD-P40-0016-02 pipe support 1C-STE-PD-HGR-0041 & 0042 & 0043 are not installed | B | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-10-10 | James Beech | 2019-11-08 | Kelvin Cook
CNM-01 | CNM-01 | PI06539 | Verified | On ISO 1C-STE-PD-P40-0016-02 incomplete field weld 2 | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-25 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06540 | Verified | On ISO 1C-STE-PD-P40-0025-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-25 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06541 | Verified | On ISO 1C-STE-PD-P41-0012-01 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-25 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06542 | Verified | On ISO 1C-STE-PD-P41-0012-02 is not installed | A | P | Bobby Williams | McD | 2019-09-18 | Bobby Williams | Const | 2019-09-25 | Damon Turner | 2019-10-28 | Kelvin Cook
CNM-01 | CNM-01 | PI06899 | Verified | 1A-HRS-FE-0081 to be installed after steam blows | B | P | Bobby Williams | McD | 2019-09-23 | Bobby Williams | Const | 2019-12-09 | Bobby Williams | 2019-12-15 | Kelvin Cook
CNM-01 | CNM-01 | PI06900 | Verified | ISO 1A-HRS-PD-P41-0007-01 to be installed with 1A-HRS-FE-0081 after steam blows | B | P | Bobby Williams | McD | 2019-09-23 | Bobby Williams | Const |  |  | 2019-12-06 | Kelvin Cook
CNM-01 | CNM-01 | PI06901 | Verified | ISO 1A-HRS-PD-P41-0007-02 to be installed with 1A-HRS-FE-0081 after steam blows | B | P | Bobby Williams | McD | 2019-09-23 | Bobby Williams | Const |  |  | 2019-12-06 | Kelvin Cook
CNM-01 | CNM-01 | PI06904 | Verified | ISO 1A-HRS-PD-P41-0040-06 to be installed with HRS-FE-0081 | B | P | Bobby Williams | McD | 2019-09-23 | Bobby Williams | Const | 2019-12-09 | Bobby Williams | 2019-12-15 | Kelvin Cook
CNM-01 | CNM-01 | PI06905 | Verified | ISO 1A-HRS-PD-P41-0040-07 to be installed with HRS-FE-0081 | B | P | Bobby Williams | McD | 2019-09-23 | Bobby Williams | Const | 2019-12-09 | Bobby Williams | 2019-12-14 | Kelvin Cook
CNM-01 | CNM-01 | PI06917 | Verified | ISO 1B-HRS-PD-P40-0040-02 1B-HRS-FE-0081 to be installed | B | P | Bobby Williams | McD | 2019-09-23 | Bobby Williams | Const | 2019-12-09 | Bobby Williams | 2019-12-14 | Kelvin Cook
CNM-01 | CNM-01 | PI06924 | Verified | ISO 1B-HRS-PD-P41-0007-01 to be installed with FE-0081 after Steam Blows | B | P | Bobby Williams | McD | 2019-09-23 | Bobby Williams | Const |  |  | 2019-12-06 | Kelvin Cook
CNM-01 | CNM-01 | PI06925 | Verified | ISO 1B-HRS-PD-P41-0007-02 to be installed with FE-0081 after Steam Blows | B | P | Bobby Williams | McD | 2019-09-23 | Bobby Williams | Const |  |  | 2019-12-06 | Kelvin Cook
CNM-01 | CNM-01 | PI06932 | Verified | ISO 1B-HRS-PD-P41-0040-06 to be installed with FE-0081 | B | P | Bobby Williams | McD | 2019-09-23 | Bobby Williams | Const | 2020-01-06 | Bobby Williams | 2020-01-08 | Ethan Byrd
CNM-01 | CNM-01 | PI06933 | Verified | ISO 1B-HRS-PD-P41-0040-07 to be installed with FE-0081 | B | P | Bobby Williams | McD | 2019-09-23 | Bobby Williams | Const | 2020-01-06 | Bobby Williams | 2020-01-08 | Fred Michael
CNM-01 | CNM-01 | PI08203 | Verified | Rotate actuator 180° on valve 1C-LPS-AOV-0081 (INSULATION CONFLICT). | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-23 | Alex Isaac
CNM-01 | CNM-01 | PI09779 | Verified | Test Package CNM-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI09780 | Verified | Test Package CNM-T-02 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const | 2019-11-18 | Michael Law | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI09781 | Verified | Test Package CNM-T-03 need to be tested (I/S). | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const | 2019-11-15 | James Beech | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI09782 | Verified | Test Package CNM-T-04 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI09783 | Verified | Test Package HRS-T-04 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI09784 | Verified | Test Package LPS-T-05 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
CNM-01 | CNM-01 | PI10250 | Verified | 1A-CNM-V-0280 & 1B-CNM-V-0280 pressure equalization lines are different, please confirm the correct valves are installed. | C | P | Kelvin Cook | McD | 2019-10-23 | Kelvin Cook | Const | 2020-02-28 | Kelvin Cook | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI10251 | Verified | 1B-CNM-V-0280 pressure equalization line has no clearance between structural steel column. | C | P | James Beech | McD | 2019-10-23 | James Beech | Const | 2020-05-20 | James Beech | 2020-07-10 | Nelson Eichelberger
CNM-01 | CNM-01 | PI12627 | Verified | Pump seals - 2 pumps seals sent to manufacturer for modification. When they come back the 3rd seal will be sent as well. | B | M | William Mitchell | McD | 2019-10-29 | William Mitchell | Const | 2020-01-09 | J.L. Bickham | 2020-01-09 | William Mitchell
CNM-01 | CNM-01 | PI12631 | Verified | LK-1C-STE-PD-P40-0010-01 - Welds 3 & 4 Need Repairs. | A | P | Bobby Williams | McD | 2019-10-30 | Bobby Williams | Const |  |  | 2019-11-01 | Tom Noble
CNM-01 | CNM-01 | PI12804 | Verified | Remove plate from 3 nozzles on the west side of the Condenser "ground level" and install proper plugs. | A | P | Bobby Williams | McD | 2019-11-06 | Bobby Williams | Const |  |  | 2019-11-12 | Bobby Williams
CNM-01 | CNM-01 | PI12805 | Verified | Remove plate from 1 nozzle on the south side of the Condenser "mez level" and install proper plug | A | P | Bobby Williams | McD | 2019-11-06 | Bobby Williams | Const |  |  | 2019-11-12 | Bobby Williams
CNM-01 | CNM-01 | PI12806 | Verified | Remove plate from 3 nozzles on the east side of the Condenser "ground level" and install proper plugs. | A | P | Bobby Williams | McD | 2019-11-06 | Bobby Williams | Const |  |  | 2019-11-12 | Bobby Williams
CNM-01 | CNM-01 | PI12807 | Verified | Remove plug from 1 nozzle on the east side of the Condenser "mez level" and connect 1C-STE-P41-0053-01 | A | P | Bobby Williams | McD | 2019-11-06 | Bobby Williams | Const | 2019-11-15 | Bobby Williams | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI12808 | Verified | 1C-CMN-PD-P41-0009 install a cap | A | P | Bobby Williams | McD | 2019-11-06 | Bobby Williams | Const | 2019-11-15 | Bobby Williams | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI12809 | Verified | 1C-CMN-PD-P41-0078 install a cap | A | P | Bobby Williams | McD | 2019-11-06 | Bobby Williams | Const | 2019-11-15 | Bobby Williams | 2019-11-23 | Kelvin Cook
CNM-01 | CNM-01 | PI13073 | Verified | Remove start-up trim and install final trim on valve 1C-CNM-FV-0222 (AFTER DEGREASE) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const |  |  | 2019-12-09 | James Beech
CNM-01 | CNM-01 | PI13074 | Verified | Remove start-up trim and install final trim on valve 1C-CNM-LV-0242 (AFTER DEGREASE) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const |  |  | 2019-12-09 | James Beech
CNM-01 | CNM-01 | PI13075 | Verified | Remove start-up trim and install final trim on valve 1C-CNM-PV-0206 (AFTER DEGREASE) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const |  |  | 2019-12-09 | James Beech
CNM-01 | CNM-01 | PI13139 | Verified | Perform final "clean and close" on condenser after steam blows. | A | M | Bobby Williams | McD | 2019-11-18 | Bobby Williams | Const |  |  | 2019-12-14 | Kelvin Cook
CNM-01 | CNM-01 | PI13385 | Verified | 1B-CNM-PD-P41-0280-04 Install 1B-CNM-FE-8500 after degreasing | B | P | Bobby Williams | McD | 2019-11-23 | Bobby Williams | Const | 2019-12-09 | Bobby Williams | 2019-12-19 | Kelvin Cook
CNM-01 | CNM-01 | PI13386 | Verified | 1B-CNM-PD-P41-0280-06 to be installed after degreasing | B | P | Bobby Williams | McD | 2019-11-23 | Bobby Williams | Const | 2019-12-17 | Bobby Williams | 2019-12-19 | Kelvin Cook
CNM-01 | CNM-01 | PI13387 | Verified | 1B-CNM-PD-P41-0280-05 to be installed after degreasing | B | P | Bobby Williams | McD | 2019-11-23 | Bobby Williams | Const | 2019-12-17 | Bobby Williams | 2019-12-19 | Kelvin Cook
CNM-01 | CNM-01 | PI13388 | Verified | 1B-CNM-PD-P41-0280-06: 1B-CNM-FIT-8500 to be installed after degreasing | B | I | Gonzalo Pena | McD | 2019-11-23 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-19 | Kelvin Cook
CNM-01 | CNM-01 | PI13389 | Verified | 1B-CNM-PD-P41-0280-05: 1B-CNM-FIT-8500 to be installed after degreasing | B | I | Gonzalo Pena | McD | 2019-11-23 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-19 | Kelvin Cook
CNM-01 | CNM-01 | PI13390 | Verified | 1A-CNM-PD-P41-0280-04 Install 1A-CNM-FE-8500 after degreasing | B | P | Bobby Williams | McD | 2019-11-23 | Bobby Williams | Const | 2019-12-04 | Bobby Williams | 2019-12-06 | Kelvin Cook
CNM-01 | CNM-01 | PI13391 | Verified | 1A-CNM-PD-P41-0280-06 to be installed after degreasing | B | P | Bobby Williams | McD | 2019-11-23 | Bobby Williams | Const | 2019-12-04 | Bobby Williams | 2019-12-06 | Kelvin Cook
CNM-01 | CNM-01 | PI13392 | Verified | 1A-CNM-PD-P41-0280-05 to be installed after degreasing | B | P | Bobby Williams | McD | 2019-11-23 | Bobby Williams | Const | 2019-12-04 | Bobby Williams | 2019-12-06 | Kelvin Cook
CNM-01 | CNM-01 | PI13393 | Verified | 1A-CNM-PD-P41-0280-06: 1A-CNM-FIT-8500 to be installed after degreasing | B | I | Gonzalo Pena | McD | 2019-11-23 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-19 | Kelvin Cook
CNM-01 | CNM-01 | PI13394 | Verified | 1A-CNM-PD-P41-0280-05: 1A-CNM-FIT-8500 to be installed after degreasing | B | I | Gonzalo Pena | McD | 2019-11-23 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-19 | Kelvin Cook
CNM-01 | CNM-01 | PI14688 | Verified | 1C-HTS-CAB-0301-FLEX CONNECTOR LOOSE ON BACK OF BOX. | C | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const | 2020-04-16 | Chris Colvin | 2020-04-20 | Michael Law
CNM-01 | CNM-01 | PI14689 | Verified | 1C-HTS-CAB-0200-NEEDS TO BE CLEANED OUT GOOD. WET INSIDE OF BOX. | B | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-13 | John Sullivan
CNM-01 | CNM-01 | PI14722 | Verified | 1C-SDS-PD-P41-0033-01: 1C-SDS-HGR-0227 was located on 12/7/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-15 | Bobby Williams | 2019-12-15 | Kelvin Cook
CNM-01 | CNM-01 | PI14724 | Verified | 1C-CNM-PD-P41-0141-04: 1C-STE-PD-P41-0018-01: 1C-STE-HGR-0023 was located on 12/7/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-17 | Bobby Williams | 2019-12-19 | Kelvin Cook
CNM-01 | CNM-01 | PI14725 | Verified | 1C-CNM-PD-P41-0141-04: 1C-CNM-HGR-0078 and 0079 was located on 12/7/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-13 | Bobby Williams | 2019-12-14 | Kelvin Cook
CNM-01 | CNM-01 | PI14728 | Verified | 1C-STE-PD-P41-0012-01: 1C-STE-HGR-0063 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-15 | Bobby Williams | 2019-12-15 | Kelvin Cook
CNM-01 | CNM-01 | PI14731 | Verified | 1C-CNM-PD-P40-0037-02: 1C-CNM-HGR-0028 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-13 | Bobby Williams | 2019-12-15 | Kelvin Cook
CNM-01 | CNM-01 | PI14738 | Verified | 1A-HRS-PD-P40-0040-02: 1C-HRS-HGR-0037 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-13 | Bobby Williams | 2019-12-15 | Kelvin Cook
CNM-01 | CNM-01 | PI14740 | Verified | 1C-CNM-PD-P40-0010-01: 1C-CNM-HGR-0062 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const |  |  | 2019-12-14 | Kelvin Cook
CNM-01 | CNM-01 | PI14741 | Verified | 1C-CNM-PD-P40-0011-01: 1C-CNM-HGR-0064 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const |  |  | 2019-12-14 | Kelvin Cook
CNM-01 | CNM-01 | PI14742 | Verified | 1C-CNM-PD-P41-0141-04: 1C-CNM-HGR-0069 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-13 | Bobby Williams | 2019-12-15 | Kelvin Cook
CNM-01 | CNM-01 | PI14743 | Verified | 1C-CNM-PD-P41-0141-01: 1C-CNM-HGR-0084 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-17 | Bobby Williams | 2019-12-19 | Kelvin Cook
CNM-01 | CNM-01 | PI14804 | Verified | 1C-HTS-CAB-0201- NEED TO SHRINK BOOT ON TUBE BUNDLE. | B | I | James Tanner | McD | 2019-12-15 | James Tanner | Const | 2019-12-19 | Gonzalo Pena | 2019-12-21 | John Sullivan
CNM-01 | CNM-01 | PI14805 | Verified | 1C-HTS-CAB-0201- NEED TO COMPLETE TUBE BUNDLE ON FIELD END. (NEED PIPE TO WELD ROOT VALVE) - 1C-CNM-PSL-9815A | A | I | James Tanner | McD | 2019-12-15 | James Tanner | Const | 2019-12-19 | Gonzalo Pena | 2019-12-21 | John Sullivan
CNM-01 | CNM-01 | PI14806 | Verified | 1C-HTS-CAB-0201- NEED TO PLUG CONDUIT IF NOT BEING USED. | C | I | Gonzalo Pena | McD | 2019-12-15 | Gonzalo Pena | Const | 2020-01-20 | Gonzalo Pena | 2020-01-28 | John Sullivan
CNM-01 | CNM-01 | PI14807 | Verified | 1C-HTS-CAB-0201- NEED TO CLEAN BOX INSIDE AND OUT. | B | I | James Tanner | McD | 2019-12-15 | James Tanner | Const |  |  | 2019-12-17 | John Sullivan
CNM-01 | CNM-01 | PI15577 | Verified | 1C-CNM-PDIT-0050B Lower tube/tray elevation below condenser operating level | B | I | Gonzalo Pena | McD | 2020-01-08 | Gonzalo Pena | Const | 2020-01-15 | Gonzalo Pena | 2020-01-27 | Fred Michael
CNM-01 | CNM-01 | PI15578 | Verified | 1C-CNM-PDIT-0050C Lower tube/tray elevation below condenser operating level | B | I | Gonzalo Pena | McD | 2020-01-08 | Gonzalo Pena | Const | 2020-01-15 | Gonzalo Pena | 2020-01-27 | Fred Michael
CNM-01 | CNM-01 | PI16733 | Verified | Construct bridge over suction line from Hotwell, Line No.24-1C-CNM-0041, ground floor STG Bldg | D | C | Charles Worthington | McD | 2020-02-13 | Charles Worthington | Comm | 2020-04-28 | Charles Worthington | 2020-07-10 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16734 | Verified | Clean and paint suction line from Hotwell, Line No.24-1C-CNM-0041, ground floor STG Bldg | C | X | Johnny Campbell | McD | 2020-02-13 | Johnny Campbell | Comm | 2020-04-06 | Johnny Campbell | 2020-04-07 | Bernard Stasse
CNM-01 | CNM-01 | PI16735 | Verified | Check all flex conduit connections to 1C-HTS-CAB-0301, located at North side of Condensate Pump A | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16736 | Verified | Flex conduit ground cable is disconnected at 1C-HTS-CAB-0301 | B | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-03-04 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16737 | Verified | Tighten all flex conduit connections to 1C Condensate Pump A Motor termination box | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16738 | Verified | Tighten all flex conduit connections to 1C Condensate Pump B Motor termination box | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16739 | Verified | Tighten all flex conduit connections to 1C Condensate Pump C Motor termination box | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16740 | Verified | Jacking bolt missing at base of 1C Condensate Pump B, East side | C | M | Tim Green | McD | 2020-02-13 | Tim Green | Comm | 2020-08-06 | Tim Green | 2020-08-14 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16741 | Verified | Vertical support base plate anchor bolts too long at 1C Condensate Pump Suction Strainer A Drain Valve; 1C-CNM-V-0053A, Line No. 2-1C-CNM-0053 | C | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-04-03 | Tim Green | 2020-04-07 | Bernard Stasse
CNM-01 | CNM-01 | PI16742 | Verified | Missing screen in bottom of 1C Condensate Pump A Motor termination box, West side of pump | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CNM-01 | CNM-01 | PI16743 | Verified | Flex conduit ground cable is disconnected on the West side of 1C Condensate Pump A | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16744 | Verified | Flex conduit ground cable is disconnected on the West side of 1C Condensate Pump B | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16745 | Verified | Flex conduit ground cable is disconnected on the West side of 1C Condensate Pump C | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16746 | Verified | Need additional support for 1C-CNM-PDI-0050B; Pressure Differential Indicator tubing | C | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-04-22 | James Beech | 2020-07-16 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16747 | Verified | Vertical support base plate anchor bolts too long at East side of 1C Condensate Pump Suction Strainer B | C | I | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-03-20 | Tim Green | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16748 | Verified | Tighten vertical support base plate anchor nuts at 1C Condensate Pump Suction Strainer B 2" drain line, Line No. 2-1C-CNM-0058 | C | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-03-27 | James Beech | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16749 | Verified | 1C Condensate Pump Suction Strainer C lid hold down bolt missing | C | P | William Mitchell | McD | 2020-02-13 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2020-07-29 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16750 | Verified | Tighten 1C Condensate Pump A base hold down anchor nuts, top nuts are loose | C | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-03-20 | Tim Green | 2020-07-29 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16751 | Verified | Tighten 1C Condensate Pump B base hold down anchor nuts, top nuts are loose | C | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-03-20 | Tim Green | 2020-07-29 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16752 | Verified | Tighten 1C Condensate Pump C base hold down anchor nuts, top nuts are loose | C | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-03-20 | Tim Green | 2020-07-29 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16753 | Verified | Coupling guard loose at 1C Condensate Pump C, use standard fasteners, currently fastened with screws and wing nuts | C | M | Shane Crowe | McD | 2020-02-13 | Shane Crowe | Comm | 2020-05-04 | Shane Crowe | 2020-06-08 | John Watts
CNM-01 | CNM-01 | PI16754 | Verified | Strainer drain valve cap missing at 1C-CNM-STN-0073C, 1C Condensate Pump C, .75 inch balancing line | C | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-03-20 | Tim Green | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16755 | Verified | 0.5 inch pump casing vent as shown on LK-IC-CNM-ME-PID-0002 is incomplete at 1C Condensate Pump A | B | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-03-09 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16756 | Verified | 0.5 inch pump casing vent as shown on LK-IC-CNM-ME-PID-0002 is incomplete at 1C Condensate Pump B | B | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-03-09 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16757 | Verified | 0.5 inch pump casing vent as shown on LK-IC-CNM-ME-PID-0002 is incomplete at 1C Condensate Pump C | B | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-03-09 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16758 | Verified | Replace teflon tape with pipe thread compound at 1C-CNM-PI-0076C; .75" Pressure Indicator, 1C Condensate Pump C balancing line | C | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-03-04 | Tim Green | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16759 | Verified | Strainer drain valve cap missing at 1C-CNM-STN-0073B, 1C Condensate Pump B, .75 inch balancing line | C | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-03-20 | Tim Green | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16760 | Verified | Strainer drain valve cap missing at 1C-CNM-STN-0073A, 1C Condensate Pump B, .75 inch balancing line | C | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-03-20 | Tim Green | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16761 | Verified | RTD flex connection needs to be tightened at West side of 1C Condensate Pump A Motor | C | E | Jonathan Donham | McD | 2020-02-13 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16762 | Verified | Conduit strap needs to be tightened at 1C-HTS-CAB-0301 | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2020-06-08 | John Watts
CNM-01 | CNM-01 | PI16763 | Verified | Conduit supports need to be welded and strapped at 1C-HTS-CAB-0301 | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2020-06-08 | John Watts
CNM-01 | CNM-01 | PI16764 | Verified | Jacking bolt missing at pump to motor connection, West side of 1C Condensate Pump A | C | M | Tim Green | McD | 2020-02-13 | Tim Green | Comm | 2020-08-06 | Tim Green | 2020-08-14 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16765 | Verified | Cap screw missing at pump to motor connection, West side of 1C Condensate Pump A | C | M | William Mitchell | McD | 2020-02-13 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2020-07-29 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16766 | Verified | Missing screws at 1C Condensate Pump B Motor cable termination box cover | C | E | Jonathan Donham | McD | 2020-02-13 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16767 | Verified | 1C-CNM-PDIT-0050B tubing bundle needs seal at 1C-HTS-CAB-0301, STG bldg ground floor | B | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-02-18 | James Tanner | 2020-02-24 | Keith Pollock
CNM-01 | CNM-01 | PI16768 | Verified | Clean inside of 1C-HTS-CAB-0301, STG bldg ground floor | C | I | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-05-07 | James Beech | 2020-06-08 | John Watts
CNM-01 | CNM-01 | PI16769 | Verified | End of cable tray is cutting into tubing bundle behind 1C-HTS-CAB-0301, STG bldg ground floor | C | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-02-18 | James Tanner | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16770 | Verified | Name plate data tag is loose on 1C Condensate Pump B discharge check valve; 1C-CNM-CHK-0100B | C | M | Shane Crowe | McD | 2020-02-13 | Shane Crowe | Comm | 2020-03-19 | Shane Crowe | 2020-07-29 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16771 | Verified | Tag all system components | C | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-04-29 | James Beech | 2021-01-22 | Eric Policarpio
CNM-01 | CNM-01 | PI16772 | Verified | 1C Condensate Pump C Motor cable termination box missing screw in cover | C | E | Jonathan Donham | McD | 2020-02-13 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16773 | Verified | Cable conduit to 1C Condensate Pump C Motor termination box missing condolet cover, West side of pump | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CNM-01 | CNM-01 | PI16774 | Verified | Tighten 1C Condensate Pump C Motor flex conduit connectors, W side of pump | C | E | Jonathan Donham | McD | 2020-02-13 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16775 | Verified | Ground cable not tie wrapped to flex conduit at 1C Condensate Pump C | C | E | Jonathan Donham | McD | 2020-02-13 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16776 | Verified | Remove green tape from 1C Condensate Pump C Motor RTD | C | C | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CNM-01 | CNM-01 | PI16777 | Verified | Conduit missing condolet cover at 1C-HTS-CAB-0203, STG mezzanine | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2020-05-26 | Randy Carpenter
CNM-01 | CNM-01 | PI16778 | Verified | Need OTQ approval for mounting vertical instrument tubing supports to grating | D | I | Michael Law | McD | 2020-02-13 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
CNM-01 | CNM-01 | PI16779 | Verified | 1C-CNM-PIT-0106 is leaking inside 1C-HTS-CAB-0200 filling cab with water, STG ground floor near condensate pumps. Leaking from threaded fitting. | B | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-02-18 | James Tanner | 2020-02-24 | Keith Pollock
CNM-01 | CNM-01 | PI16780 | Verified | Tubing bundle not sealed at 1C-CNM-HTS-CAB-0200, STG mezzanine | B | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-02-18 | James Tanner | 2020-02-25 | John Watts
CNM-01 | CNM-01 | PI16781 | Verified | Cold gal rod hanger support at Condensate Discharge Header piping, Line No. 16-1C-CNM-0100, North West corner STG mezzanine | C | X | Johnny Campbell | McD | 2020-02-13 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-07 | Bernard Stasse
CNM-01 | CNM-01 | PI16782 | Verified | Clean Condensate Discharge Header piping upstream of 1C Gland Seal Steam Condenser | C | C | Johnny Campbell | McD | 2020-02-13 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-07 | Bernard Stasse
CNM-01 | CNM-01 | PI16784 | Verified | Broken cover latch at 1C-HTS-CAB-0300, STG mezzanine | C | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-02-19 | James Tanner | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16785 | Verified | Seal all tubing bundles at 1C-HTS-CAB-0300, STG mezzanine | B | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-02-19 | James Tanner | 2020-02-25 | John Watts
CNM-01 | CNM-01 | PI16786 | Verified | Clean out 1C-HTS-CAB-0300 | C | I | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-26 | Randy Carpenter
CNM-01 | CNM-01 | PI16787 | Verified | Paint 1C Gland Seal Steam Condenser | C | X | Jerry Smith | McD | 2020-02-13 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16788 | Verified | Rework kinked tubing to 1C-CNM-PI-9815 inside 1C-HTS-CAB-0201, STG mezzanine | C | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-03-07 | Tim Green | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16789 | Verified | Conduit to 1C-CNM-TI-0236; Condensate Discharge Header Temperature Indicator broken, STG mezzanine | B | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
CNM-01 | CNM-01 | PI16790 | Verified | Conduit to 1C-CNM-TI-0236; Condensate Discharge Header Temperature Indicator missing condolet covers | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CNM-01 | CNM-01 | PI16791 | Verified | Instrument tubing bundle lock nuts loose inside 1A-HTS-CAB-0200, HRSG A FW Pump platform | C | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-02-18 | James Tanner | 2020-02-21 | Keith Pollock
CNM-01 | CNM-01 | PI16792 | Verified | Instrument tubing bundle sheath needs heat shrink at 1A-HTS-CAB-0200, HRSG A FW Pump platform | C | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-02-18 | James Tanner | 2020-02-21 | Keith Pollock
CNM-01 | CNM-01 | PI16793 | Verified | Instrumentation leak inside 1B-HTS-CAB-0200, HRSG B FW Pump platform | B | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-03-07 | Tim Green | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16794 | Verified | Tube bundle lock nuts loose inside 1B-HTS-CAB-0200, HRSG B FW Pump platform | C | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-02-19 | James Tanner | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16795 | Verified | Tubing bundle sheath needs heat shrink at 1B-HTS-CAB-0200, HRSG A FW Pump platform | C | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-02-19 | James Tanner | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16796 | Verified | End of cable tray is cutting into tubing bundle behind 1B-HTS-CAB-0200, HRSG B FW Pump platform | C | I | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-02-19 | James Tanner | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16797 | Verified | Power cable conduit condolet cover is loose at 1B-HTS-CAB-0200, HRSG B FW Pump platform | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2020-05-26 | Randy Carpenter
CNM-01 | CNM-01 | PI16798 | Verified | 1B-FWS-CHK-0272; Feedwater Check Valve nameplate painted over, located in FW return piping from 1B GT Fuel Heater A, upstream of tie-in to Condensate Header, HRSG B FW Pump platform | C | X | Tim Green | McD | 2020-02-13 | Tim Green | Comm | 2021-01-15 | Eric Policarpio | 2021-01-15 | Dave Goldak
CNM-01 | CNM-01 | PI16799 | Verified | Missing U-Bolt upstream of 1C-CNM-V-0202; Curtain Spray Isolation Valve, Line No. 4-1C-CNM-0205, W side of Condenser, STG mezzanine | C | P | Tim Green | McD | 2020-02-13 | Tim Green | Comm | 2020-08-06 | Tim Green | 2020-08-14 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16800 | Verified | Flex conduit rubbing hard against 1C-CNM-PV-0206; Curtain Spray Pressure Control Valve, Line No. 4-1C-CNM-0205, W side of Condenser, STG mezzanine | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-05-13 | Chris Colvin | 2020-07-10 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16801 | Verified | Condensate Discharge Header sample tubing tray needs additional support, Line No. 1-1C-CNM-0130, Northeast corner, STG mezzanine | C | I | James Tanner | McD | 2020-02-13 | James Tanner | Comm | 2020-02-19 | James Tanner | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16802 | Verified | Instrument tubing to 1C-LPS-AOV-0081; Condensate Spray Control Valve needs to be routed around I-Beam with clearance, currently tight against I-Beam, Line No. 1.5-1C-LPS-0400, STG operating deck | C | I | James Tanner | McD | 2020-02-13 | James Tanner | Comm | 2020-02-17 | James Tanner | 2020-02-21 | Keith Pollock
CNM-01 | CNM-01 | PI16803 | Verified | 1C-LPS-AOV-0081; Condensate Spray Control Valve posiiton indicator cover has loose bolts, Line No. 1.5-1C-LPS-0400, STG operating deck | C | I | Albert Burge | McD | 2020-02-13 | Albert Burge | Comm | 2020-02-13 | Albert Burge | 2020-02-15 | Shannon Scott
CNM-01 | CNM-01 | PI16804 | Verified | Tubing from solenoid to 1C-LPS-AOV-0081; Condensate Spray Control Valve is not connected Line No. 1.5-1C-LPS-0400, STG operating deck | B | I | Albert Burge | McD | 2020-02-13 | Albert Burge | Comm | 2020-02-13 | Albert Burge | 2020-02-15 | Shannon Scott
CNM-01 | CNM-01 | PI16805 | Verified | One 3/4" elec. plug missing at 1C-LPS-AOV-0081; Condensate Spray Control Valve, Line No. 1.5-1C-LPS-0400, STG operating deck | C | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-04-07 | Bernard Stasse
CNM-01 | CNM-01 | PI16806 | Verified | Replace carbon steel flange bolts with teflon coated B7 bolts at 1C-LPS-FE-0080; Condensate Spray Flow Element, Line No. 1.5-1C-LPS-0400, STG operating deck | D | P | Michael Law | McD | 2020-02-13 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-04-26 | Keith Pollock
CNM-01 | CNM-01 | PI16807 | Verified | Power cable conduit condolet covers not screwed down at 1C-LPS-AOV-0081; Condensate Spray Control Valve, Line No. 1.5-1C-LPS-0400, STG operating deck | C | E | Jonathan Donham | McD | 2020-02-13 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16808 | Verified | One cable is not terminated at 1C-LPS-AOV-0081; Condensate Spray Control Valve, Line No. 1.5-1C-LPS-0400, STG operating deck | B | E | Chris Colvin | McD | 2020-02-13 | Chris Colvin | Comm | 2020-03-26 | Chris Colvin | 2020-04-07 | Bernard Stasse
CNM-01 | CNM-01 | PI16809 | Verified | Instrument Air tubing is not connected to 1C-LPS-TV-0083; Condensate Spray Temperature Control Valve, Line No. 1.5-1C-LPS-0400, STG operating deck | B | I | Albert Burge | McD | 2020-02-13 | Albert Burge | Comm | 2020-02-13 | Albert Burge | 2020-02-15 | Shannon Scott
CNM-01 | CNM-01 | PI16810 | Verified | Moisture inside STE-MOV-9612A; Main Stop Valve B Drain to Condenser, STG mezzanine, East side | C | E | Jonathan Donham | McD | 2020-02-13 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16811 | Verified | Paint Condensate Header in HRSG A pipe rack where spool piece was welded in | C | X | Jerry Smith | McD | 2020-02-13 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-07-29 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16812 | Verified | Paint Condensate Header in HRSG B pipe rack where spool piece was welded in | C | X | Jerry Smith | McD | 2020-02-13 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-07-28 | Nelson Eichelberger
CNM-01 | CNM-01 | PI16813 | Verified | Tubing tray vertical support base plate J-Hook bolts too short, no threads showing at 1C-CNM-AOV-0205; Curtain Spray Control Valve, STG mezzanine | C | P | Gonzalo Pena | McD | 2020-02-13 | Gonzalo Pena | Comm | 2020-02-19 | James Tanner | 2020-04-03 | Bernard Stasse
CNM-01 | CNM-01 | PI16814 | Verified | Remove chain wheel from 1C-SDS-V-0103; STG Steam Drains Tank Drain Line Isolation Valve, Line No. 8-1C-SDS-0058, STG ground level, E side of Condenser | C | P | James Beech | McD | 2020-02-13 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-08 | John Watts
CNM-01 | CNM-01 | PI17201 | Verified | 1C-CNM-V-0042B – Valve leaks through and cannot isolate the strainer. | B | P | William Mitchell | McD | 2020-02-25 | William Mitchell | Comm | 2020-03-09 | Michael Law | 2020-03-26 | Keith Pollock
CNM-01 | CNM-01 | PI17229 | Verified | Condensate pumps - tighten down / add missing lock nuts on pumps A/B/C. | C | M | Shane Crowe | McD | 2020-02-25 | Shane Crowe | Const | 2020-03-19 | Shane Crowe | 2020-06-24 | Dave Goldak
CNM-01 | CNM-01 | PI18019 | Verified | 1C-CNM-CND-0100 - Inspect the condenser tubes and clean, if necessary. Inspect the equipment on the circulating water system for iron after the Jan 21, 2020 upset to the system. Clean equipment for full efficiency. | D | I | Michael Law | McD | 2020-03-17 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-07-10 | Nelson Eichelberger
CNM-01 | CNM-01 | PI18119 | Verified | Condensate Thermal Shut-Off Valve (TSV) will need to be updgraded to a 140F unit. The sample runs hotter than 120F. | D | P | Charles Worthington | McD | 2020-03-20 | Charles Worthington | Comm | 2020-07-22 | Bryan Sturgies | 2021-05-07 | John Watts
CNM-01 | CNM-01 | PI18190 | Verified | Ensure the suction strainers have been pulled on Condensate Pumps | C | P | William Mitchell | McD | 2020-03-26 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2020-04-17 | John Watts
CRS-01 | CRS-01 | PI07035 | Verified | 1C-CRS-PP-0009 not installed. STG mezz. | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
CRS-01 | CRS-01 | PI07036 | Verified | 1C-CRS-PI-0011 not installed. STG mezz. | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI07037 | Verified | Set all spring cans to cold settings. | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-21 | Michael Law
CRS-01 | CRS-01 | PI07038 | Verified | HGR-0503 not installed per design. STG mezz. | A | P | Damon Turner | McD | 2019-09-24 | Damon Turner | Const |  |  | 2019-10-08 | Alex Isaac
CRS-01 | CRS-01 | PI07039 | Verified | Tag all valves. | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const |  |  | 2020-02-10 | Kelvin Cook
CRS-01 | CRS-01 | PI07040 | Verified | Pipe off center at concrete penetration - 1C-ASF-0065. Insulation issue. Turbine deck. | B | C | Alan Huntsman | McD | 2019-09-24 | Alan Huntsman | Const |  |  | 2020-02-19 | Michael Law
CRS-01 | CRS-01 | PI07041 | Verified | Rotate head 180 deg. On 1C-ASF-V-0010. Turbine deck. | A | P | Damon Turner | McD | 2019-09-24 | Damon Turner | Const |  |  | 2019-10-08 | Alex Isaac
CRS-01 | CRS-01 | PI07042 | Verified | Support 1C-CRS-PD-HGR-0902 not set per design, should be centered on beam. Turbine deck, under silencers. | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-08 | Alex Isaac | 2020-01-21 | Michael Law
CRS-01 | CRS-01 | PI07043 | Verified | Pneumatic cylinders not installed on NRV 1C-CRS-AOV-9720. STG ground level. | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2020-02-03 | Bobby Williams | 2020-03-03 | Michael Law
CRS-01 | CRS-01 | PI07044 | Verified | Support 1C-CRS-PD-HGR-0502 not installed per design. STG ground level. | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-20 | Charlie English | 2019-11-21 | Alex Isaac
CRS-01 | CRS-01 | PI09174 | Verified | Support 1A-CRS-PD-HGR-0508 not in per design (MOVE CLAMP EAST) | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09175 | Verified | Install 1A-CRS-FE-0030 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-10-08 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
CRS-01 | CRS-01 | PI09176 | Verified | Install spool PS-1A-CRS-P41-0010-02-152-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-10-08 | James Beech | Const | 2020-02-07 | James Beech | 2020-02-07 | Kelvin Cook
CRS-01 | CRS-01 | PI09177 | Verified | Install spool PS-1A-CRS-P41-0010-01-152-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-10-08 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
CRS-01 | CRS-01 | PI09178 | Verified | Remove rigging from pipe (2 PLACES) | B | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2019-12-08 | Shane Copeland
CRS-01 | CRS-01 | PI09179 | Verified | Line not installed (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-10-08 | James Beech | Const | 2020-02-07 | James Beech | 2020-02-07 | Kelvin Cook
CRS-01 | CRS-01 | PI09180 | Verified | Install spool PS-1B-CRS-P41-0010-02-152-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-10-08 | James Beech | Const | 2020-02-07 | James Beech | 2020-02-07 | Kelvin Cook
CRS-01 | CRS-01 | PI09181 | Verified | Remove tie-wire from support 1B-MSS-PD-HGR-0530 | C | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-09 | Kelvin Cook
CRS-01 | CRS-01 | PI09182 | Verified | Support 1C-ASF-PD-HGR-0018 not installed per design (NOT PLUMB) | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-20 | Charlie English | 2019-11-21 | Alex Isaac
CRS-01 | CRS-01 | PI09183 | Verified | Lisega clamp not installed on support 1C-ASF-PD-HGR-0010 | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-20 | Charlie English | 2019-11-21 | Alex Isaac
CRS-01 | CRS-01 | PI09184 | Verified | Support 1C-CRS-PD-HGR-0500 Missing Dowel Pin | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-20 | Charlie English | 2019-11-24 | Kelvin Cook
CRS-01 | CRS-01 | PI09185 | Verified | Hydro support should be installed at support 1C-CRS-PD-HGR-0501 (SEE DETAIL) | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-11-21 | Alex Isaac
CRS-01 | CRS-01 | PI09186 | Verified | Support 1C-CRS-PD-HGR-0503 not set per design | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-11-21 | Alex Isaac
CRS-01 | CRS-01 | PI09187 | Verified | IC-CRS-SRV-0075 not installed (REMOVED FOR HYDROLAZE) | B | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-13 | Alex Isaac
CRS-01 | CRS-01 | PI09188 | Verified | Rotate operator on valve 1C-ASF-V-0010 | B | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-22 | Bobby Williams | 2019-11-26 | Alex Isaac
CRS-01 | CRS-01 | PI09189 | Verified | Support 1C-CRS-PD-HGR-0009 not set per design | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-11-21 | Alex Isaac
CRS-01 | CRS-01 | PI09190 | Verified | Support 1C-CRS-PD-HGR-0010 not set per design | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-11-21 | Alex Isaac
CRS-01 | CRS-01 | PI09191 | Verified | U-bolts not installed on support 1C-CRS-PD-HGR-0551 | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-11-26 | Alex Isaac
CRS-01 | CRS-01 | PI09192 | Verified | Support 1C-CRS-PD-HGR-0536 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-11-26 | Alex Isaac
CRS-01 | CRS-01 | PI09193 | Verified | U-bolts not installed on support 1C-CRS-PD-HGR-0552 | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-11-26 | Alex Isaac
CRS-01 | CRS-01 | PI09194 | Verified | Support 1C-CRS-PD-HGR-0537 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-11-26 | Alex Isaac
CRS-01 | CRS-01 | PI09195 | Verified | U-bolts not installed on support 1C-CRS-PD-HGR-0553 | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-11-26 | Alex Isaac
CRS-01 | CRS-01 | PI09196 | Verified | Support 1C-CRS-PD-HGR-0538 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-11-26 | Alex Isaac
CRS-01 | CRS-01 | PI09197 | Verified | Line not complete | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-11-26 | Alex Isaac
CRS-01 | CRS-01 | PI09198 | Verified | U-bolts not installed on support 1C-CRS-PD-HGR-0554 | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-11-26 | Alex Isaac
CRS-01 | CRS-01 | PI09199 | Verified | Support 1C-CRS-PD-HGR-0539 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-11-26 | Alex Isaac
CRS-01 | CRS-01 | PI09200 | Verified | Line not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09201 | Verified | Line not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09202 | Verified | Support 1C-CRS-PD-HGR-0011 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09203 | Verified | Line not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09204 | Verified | Line not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09205 | Verified | Support 1C-CRS-PD-HGR-0021 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-04 | James Beech | 2019-11-06 | Alex Isaac
CRS-01 | CRS-01 | PI09206 | Verified | Support 1C-CRS-PD-HGR-0022 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-13 | Alex Isaac
CRS-01 | CRS-01 | PI09207 | Verified | Support 1C-CRS-PD-HGR-0023 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-13 | Alex Isaac
CRS-01 | CRS-01 | PI09208 | Verified | Support 1C-CRS-PD-HGR-0024 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-13 | Alex Isaac
CRS-01 | CRS-01 | PI09209 | Verified | Support 1C-CRS-PD-HGR-0025 not complete | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-04 | James Beech | 2019-11-06 | Alex Isaac
CRS-01 | CRS-01 | PI09210 | Verified | Support 1C-CRS-PD-HGR-0028 not complete | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-13 | Alex Isaac
CRS-01 | CRS-01 | PI09211 | Verified | Line not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-13 | Alex Isaac
CRS-01 | CRS-01 | PI09212 | Verified | Line not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09213 | Verified | Line not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-13 | Alex Isaac
CRS-01 | CRS-01 | PI09214 | Verified | Line not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09215 | Verified | Line not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09216 | Verified | Cotter Pins not installed - Support 1C-SDS-PD-HGR-0112 | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09217 | Verified | Support 1C-SDS-PD-HGR-0111 not set per design | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-20 | Charlie English | 2019-11-24 | Kelvin Cook
CRS-01 | CRS-01 | PI09218 | Verified | Support 1C-SDS-PD-HGR-0109 not set per design | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-20 | Charlie English | 2019-11-24 | Kelvin Cook
CRS-01 | CRS-01 | PI09219 | Verified | Stops Not Installed - Support 1C-SDS-PD-HGR-0108 | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09220 | Verified | Support 1C-SDS-PD-HGR-0107 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09221 | Verified | Support Not Complete - 1C-SDS-PD-HGR-0106 | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09222 | Verified | Support Not Complete - 1C-SDS-PD-HGR-0105 | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09223 | Verified | Support 1C-SDS-PD-HGR-0113 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-13 | Alex Isaac
CRS-01 | CRS-01 | PI09224 | Verified | Support 1C-SDS-PD-HGR-0114 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-13 | Alex Isaac
CRS-01 | CRS-01 | PI09225 | Verified | Support 1C-SDS-PD-HGR-0115 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-06 | Shane Copeland
CRS-01 | CRS-01 | PI09226 | Verified | Support 1C-SDS-PD-HGR-0116 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-08 | Shane Copeland
CRS-01 | CRS-01 | PI09227 | Verified | Support 1C-SDS-PD-HGR-0120 not set per design | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-13 | Alex Isaac
CRS-01 | CRS-01 | PI09228 | Verified | Support 1C-SDS-PD-HGR-0121 Loose Nuts on Strut | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-08 | Shane Copeland
CRS-01 | CRS-01 | PI09229 | Verified | Support 1C-SDS-PD-HGR-0118 Stops not Installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-08 | Shane Copeland
CRS-01 | CRS-01 | PI09230 | Verified | Support 1C-SDS-PD-HGR-0117 not complete | B | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const |  |  | 2019-12-20 | Bobby Williams
CRS-01 | CRS-01 | PI09231 | Verified | Support 1C-SDS-PD-HGR-0122 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-20 | Charlie English | 2019-11-24 | Kelvin Cook
CRS-01 | CRS-01 | PI09232 | Verified | Support 1C-SDS-PD-HGR-0123 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-20 | Charlie English | 2019-11-24 | Kelvin Cook
CRS-01 | CRS-01 | PI09233 | Verified | Support 1C-SDS-PD-HGR-0124 not set per design | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-18 | Bobby Williams | 2019-12-08 | Shane Copeland
CRS-01 | CRS-01 | PI09234 | Verified | Support 1C-SDS-PD-HGR-0125 not installed | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-13 | Alex Isaac
CRS-01 | CRS-01 | PI09785 | Verified | Test Package CRS-T-04 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const | 2019-11-26 | Bobby Williams | 2019-12-04 | Kelvin Cook
CRS-01 | CRS-01 | PI09841 | Verified | 1ACRSC0001 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09842 | Verified | 1ACRSX0006 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09843 | Verified | 1ACRSX0008 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09844 | Verified | 1ACRSX0009 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09845 | Verified | 1ACRSX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09846 | Verified | 1ACRSX0012 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09847 | Verified | 1ACRSX0013 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09848 | Verified | 1ACRSX0019 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09849 | Verified | 1AIPSX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09850 | Verified | 1BCRSK0001 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09851 | Verified | 1BCRSX0001 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09852 | Verified | 1BCRSX0002 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09853 | Verified | 1BCRSX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09854 | Verified | 1BCRSX0004 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09855 | Verified | 1BCRSX0005 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09856 | Verified | 1BCRSX0018 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09857 | Verified | 1BCRSX0019 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09858 | Verified | 1BIPSX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09859 | Verified | 1ACRSX0021 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09860 | Verified | 1ACRSX0022 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CRS-01 | CRS-01 | PI09861 | Verified | 1ACRSX0023 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CRS-01 | CRS-01 | PI09862 | Verified | 1ACRSX0025 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09863 | Verified | 1AIPSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09864 | Verified | 1BCRSC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09865 | Verified | 1BCRSC0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09866 | Verified | 1BCRSK0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09867 | Verified | 1BCRSX0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09868 | Verified | 1BCRSX0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09869 | Verified | 1BCRSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09870 | Verified | 1BCRSX0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09871 | Verified | 1BCRSX0005 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09872 | Verified | 1BCRSX0008 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09873 | Verified | 1BCRSX0018 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09874 | Verified | 1BCRSX0019 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09875 | Verified | 1BIPSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09914 | Verified | 1ACRSC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09915 | Verified | 1ACRSX0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09916 | Verified | 1ACRSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09917 | Verified | 1ACRSX0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09918 | Verified | 1ACRSX0005 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09919 | Verified | 1ACRSX0006 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09920 | Verified | 1ACRSX0008 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09921 | Verified | 1ACRSX0009 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09922 | Verified | 1ACRSX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09923 | Verified | 1ACRSX0012 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09924 | Verified | 1ACRSX0013 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09925 | Verified | 1ACRSX0014 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09926 | Verified | 1ACRSX0015 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09927 | Verified | 1ACRSX0016 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09928 | Verified | 1ACRSX0017 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09929 | Verified | 1ACRSX0018 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09930 | Verified | 1ACRSX0019 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI09931 | Verified | 1ACRSX0020 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CRS-01 | CRS-01 | PI10846 | Verified | 10CRSX0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI10869 | Verified | 1ACRSK0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI10871 | Verified | 1ACRSX0026 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11084 | Verified | 1BCRSX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11085 | Verified | 1BCRSX0012 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11086 | Verified | 1BCRSX0013 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11087 | Verified | 1BCRSX0014 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11088 | Verified | 1BCRSX0015 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11089 | Verified | 1BCRSX0016 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11090 | Verified | 1BCRSX0017 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11091 | Verified | 1BCRSX0020 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11092 | Verified | 1BCRSX0021 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11093 | Verified | 1BCRSX0022 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11094 | Verified | 1BCRSX0023 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11095 | Verified | 1BCRSX0025 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11096 | Verified | 1BCRSX0026 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11323 | Verified | 1CCRSC0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11324 | Verified | 1CCRSC0002 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11325 | Verified | 1CCRSC0003 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11326 | Verified | 1CCRSC0004 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11327 | Verified | 1CCRSC0013 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11742 | Verified | 1BCRSX0025 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11743 | Verified | 1BCRSX0026 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11741 | Verified | 1BCRSX0023 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11740 | Verified | 1BCRSX0022 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11739 | Verified | 1BCRSX0021 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11738 | Verified | 1BCRSX0020 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11737 | Verified | 1BCRSX0017 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11736 | Verified | 1BCRSX0016 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11735 | Verified | 1BCRSX0015 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11734 | Verified | 1BCRSX0014 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11733 | Verified | 1BCRSX0013 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11732 | Verified | 1BCRSX0012 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11731 | Verified | 1BCRSX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11506 | Verified | 1ACRSX0026 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11503 | Verified | 1ACRSK0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11480 | Verified | 10CRSX0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11338 | Verified | 1CCRSX0006 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11336 | Verified | 1CCRSX0004 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11335 | Verified | 1CCRSX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11334 | Verified | 1CCRSX0002 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11333 | Verified | 1CCRSX0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11332 | Verified | 1CCRSC0018 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11331 | Verified | 1CCRSC0017 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11330 | Verified | 1CCRSC0016 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11329 | Verified | 1CCRSC0015 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11328 | Verified | 1CCRSC0014 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11970 | Verified | 1CCRSC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12181 | Verified | 1BCRSX0005 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CRS-01 | CRS-01 | PI12182 | Verified | 1BCRSX0018 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12183 | Verified | 1BCRSX0019 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12194 | Verified | 1BIPSX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12246 | Verified | 1ACRSC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12247 | Verified | 1ACRSX0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12248 | Verified | 1ACRSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CRS-01 | CRS-01 | PI12249 | Verified | 1ACRSX0004 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CRS-01 | CRS-01 | PI12250 | Verified | 1ACRSX0005 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CRS-01 | CRS-01 | PI12251 | Verified | 1ACRSX0006 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CRS-01 | CRS-01 | PI12252 | Verified | 1ACRSX0008 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12253 | Verified | 1ACRSX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11971 | Verified | 1CCRSC0002 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11972 | Verified | 1CCRSC0003 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11973 | Verified | 1CCRSC0004 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11974 | Verified | 1CCRSC0013 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11975 | Verified | 1CCRSC0014 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11976 | Verified | 1CCRSC0015 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11977 | Verified | 1CCRSC0016 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11978 | Verified | 1CCRSC0017 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11979 | Verified | 1CCRSC0018 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11980 | Verified | 1CCRSX0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11981 | Verified | 1CCRSX0002 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11982 | Verified | 1CCRSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11983 | Verified | 1CCRSX0004 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI11985 | Verified | 1CCRSX0006 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12128 | Verified | 1ACRSC0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12129 | Verified | 1ACRSX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12130 | Verified | 1ACRSX0012 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12131 | Verified | 1ACRSX0013 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CRS-01 | CRS-01 | PI12139 | Verified | 1AIPSX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12176 | Verified | 1BCRSK0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12177 | Verified | 1BCRSX0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12178 | Verified | 1BCRSX0002 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CRS-01 | CRS-01 | PI12179 | Verified | 1BCRSX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CRS-01 | CRS-01 | PI12180 | Verified | 1BCRSX0004 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CRS-01 | CRS-01 | PI13510 | Verified | Support conduit at 1B-CRS-TE-8406G/H. 1B HRSG first landing. | B | E | Chris Colvin | McD | 2019-11-25 | Chris Colvin | Const | 2019-12-05 | Brad Stanford | 2019-12-11 | Shannon Scott
CRS-01 | CRS-01 | PI13511 | Verified | Pour all seals. After commissioning. | B | E | Chris Colvin | McD | 2019-11-25 | Chris Colvin | Const | 2019-12-23 | Michael Law | 2020-01-13 | Fred Michael
CRS-01 | CRS-01 | PI13512 | Verified | 1B-CRS-TE-8410 - not installed. HP lower south level. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-07 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13513 | Verified | Condulet covers missing. HP lower south level. | B | E | Chris Colvin | McD | 2019-11-25 | Chris Colvin | Const | 2019-12-05 | Brad Stanford | 2019-12-11 | Shannon Scott
CRS-01 | CRS-01 | PI13514 | Verified | 1B-CRS-TE-8412 - check flex length for growth. HP lower south level. | A | E | Chris Colvin | McD | 2019-11-25 | Chris Colvin | Const | 2019-12-05 | Brad Stanford | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13515 | Verified | 1A-CRS-TP-8411 - not installed. HP lower south level. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-07 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13516 | Verified | 1A-CRS-PIT-0025 - complete tubing. STG operating deck east. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-14 | Fred Michael | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13517 | Verified | 1B-CRS-PIT-0025 - complete tubing. STG operating deck east. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-07 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13518 | Verified | Heat shring all boots at instrument cabs. | B | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-12 | James Tanner | 2019-12-18 | Shannon Scott
CRS-01 | CRS-01 | PI13519 | Verified | 1C-HTS-CAB-0204 needs brace / support. STG operating deck east. | B | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2020-02-10 | Gonzalo Pena | 2020-02-15 | Shannon Scott
CRS-01 | CRS-01 | PI13520 | Verified | Clean all HTS cabinets inside and outside. | C | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2020-02-07 | Fred Michael | 2020-02-15 | Shannon Scott
CRS-01 | CRS-01 | PI13521 | Verified | Install 1A-CRS-FIT-0030. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-07 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13522 | Verified | Install 1B-CRS-FIT-0030. Tubing tie in. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2020-02-10 | James Tanner | 2020-02-19 | Albert Burge
CRS-01 | CRS-01 | PI13523 | Verified | Install 1A-CRS-TE-0030. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13524 | Verified | Install 1B-CRS-TE-0030. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13525 | Verified | 1C-CRS-AOV-0009 missing tag. STG operating deck north. Place in visible location. | C | P | Bobby Williams | McD | 2019-11-25 | Bobby Williams | Const | 2019-12-05 | James Tanner | 2019-12-11 | Shannon Scott
CRS-01 | CRS-01 | PI13526 | Verified | 1C-CRS-LSH-0090 - cover missing strap. STG operating deck north. | B | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13527 | Verified | 1C-CRS-AOV-0090 - missing air supply. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-06 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13528 | Verified | 1C-CRS-TE-0042 - flex too short. STG mezz north. | A | E | Chris Colvin | McD | 2019-11-25 | Chris Colvin | Const | 2019-12-05 | Brad Stanford | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13529 | Verified | 1C-CRS-TE-0042 - rework support. | B | E | Chris Colvin | McD | 2019-11-25 | Chris Colvin | Const | 2019-12-05 | Brad Stanford | 2019-12-08 | John Sullivan
CRS-01 | CRS-01 | PI13530 | Verified | 1C-CRS-PIT-9700B - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-16 | Gonzalo Pena | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13531 | Verified | 1C-CRS-AOV-9720 - complete tubing. Non-return valve. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2020-02-10 | James Tanner | 2020-02-19 | Albert Burge
CRS-01 | CRS-01 | PI13532 | Verified | 1C-CRS-AOV-0040 - missing air supply. STG ground level. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13533 | Verified | 1C-CRS-LSH-0040 - cover missing clamp. STG ground level. | B | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13534 | Verified | 1C-CRS-LSHH-0040 - cover missing clamp. STG ground level. | B | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13535 | Verified | 1C-CRS-PI-0041 - complete tubing. STG ground level. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-10 | Gonzalo Pena | 2019-12-10 | Fred Michael
CRS-01 | CRS-01 | PI13536 | Verified | 1C-CRS-LSH-0020 - missing cover. STG ground level. | B | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13537 | Verified | 1C-CRS-AOV-0020 - complete instrument air. STG ground level. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-06 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13538 | Verified | 1C-CRS-AOV-0020 - rework flex. Too close to process line. | A | E | Chris Colvin | McD | 2019-11-25 | Chris Colvin | Const | 2019-12-05 | Brad Stanford | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13539 | Verified | 1C-CRS-FY-0020 - Terminate cable. | A | E | Chris Colvin | McD | 2019-11-25 | Chris Colvin | Const | 2019-12-05 | Brad Stanford | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13540 | Verified | 1C-CRS-PI-0011 - complete tubing. STG mezz. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-07 | James Tanner | 2020-01-01 | Albert Burge
CRS-01 | CRS-01 | PI13541 | Verified | 1C-HTS-CAB-0101 - move east away from pipe & allow for pipe insulation. STG mezz. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2019-12-13 | Albert Burge
CRS-01 | CRS-01 | PI12254 | Verified | 1ACRSX0012 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12255 | Verified | 1ACRSX0013 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CRS-01 | CRS-01 | PI12256 | Verified | 1ACRSX0014 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CRS-01 | CRS-01 | PI12257 | Verified | 1ACRSX0015 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12258 | Verified | 1ACRSX0016 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12259 | Verified | 1ACRSX0017 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12260 | Verified | 1ACRSX0020 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12261 | Verified | 1ACRSX0021 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12262 | Verified | 1ACRSX0025 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12279 | Verified | 1AIPSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12357 | Verified | 1BCRSC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12358 | Verified | 1BCRSC0002 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12359 | Verified | 1BCRSK0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12360 | Verified | 1BCRSX0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12361 | Verified | 1BCRSX0002 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12362 | Verified | 1BCRSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12363 | Verified | 1BCRSX0004 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12364 | Verified | 1BCRSX0005 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12365 | Verified | 1BCRSX0008 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12366 | Verified | 1BCRSX0018 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12367 | Verified | 1BCRSX0019 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI12380 | Verified | 1BIPSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
CRS-01 | CRS-01 | PI13258 | Verified | Pipe Support Number: 1B-CRS-PD-HGR-0509: Ref. Iso. LK-1B-CRS-PD-P40-0010-01: Loose Jam Nut above the Turnbuckle on the South Side. | A | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-11-26 | Bobby Williams | 2019-12-05 | Gary Pickeral
CRS-01 | CRS-01 | PI13259 | Verified | Pipe Support Number: 1C-CRS-PD-HGR-0531: Ref. Iso. LK-1C-CRS-PD-P40-0010-06: The Column Bolt (Item 1; 2" Hvy Hex Bolt) is not snug against Elbow Trunion (1C-CRS-PD-HGR-0941) above. | A | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-11-26 | Bobby Williams | 2019-12-05 | Gary Pickeral
CRS-01 | CRS-01 | PI13542 | Verified | 1A-CRS-PIT-8401 missing plug. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const | 2019-12-07 | James Tanner | 2019-12-13 | Albert Burge
CRS-01 | CRS-01 | PI13543 | Verified | 1A-CRS-TE-8400 - plumb up conduit. | B | E | Chris Colvin | McD | 2019-11-25 | Chris Colvin | Const | 2019-12-05 | Brad Stanford | 2019-12-08 | John Sullivan
CRS-01 | CRS-01 | PI13544 | Verified | 1A-CRS-PV-8303 - install after steam blows. | A | I | Gonzalo Pena | McD | 2019-11-25 | Gonzalo Pena | Const |  |  | 2020-02-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13706 | Verified | 1A-CRS-MOV-0100 - handwheel is broken off. | A | P | James Beech | McD | 2019-11-27 | James Beech | Const | 2019-12-31 | James Beech | 2020-01-16 | Michael Law
CRS-01 | CRS-01 | PI13973 | Verified | 1ACRSK0001, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13974 | Verified | 1ACRSX0026, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-09 | Mike Tabbert
CRS-01 | CRS-01 | PI13975 | Verified | 1BCRSX0016, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13976 | Verified | 1BCRSX0017, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13977 | Verified | 1BCRSX0020, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13978 | Verified | 1BCRSX0021, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13979 | Verified | 1BCRSX0022, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13980 | Verified | 1BCRSX0023, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13981 | Verified | 1BCRSX0025, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13982 | Verified | 1BCRSX0026, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13983 | Verified | 1CCRSC0004, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13984 | Verified | 1ACRSK0001, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
CRS-01 | CRS-01 | PI13985 | Verified | 1ACRSX0026, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-12 | Mike Tabbert
CRS-01 | CRS-01 | PI13986 | Verified | 1BCRSK0001, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
CRS-01 | CRS-01 | PI13987 | Verified | 1BCRSX0016, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13988 | Verified | 1BCRSX0017, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13989 | Verified | 1BCRSX0020, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13990 | Verified | 1BCRSX0021, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13991 | Verified | 1BCRSX0022, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13992 | Verified | 1BCRSX0023, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI13993 | Verified | 1BCRSX0025, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-12 | Mike Tabbert
CRS-01 | CRS-01 | PI13994 | Verified | 1BCRSX0026, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-12 | Mike Tabbert
CRS-01 | CRS-01 | PI13995 | Verified | 1CCRSC0004, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-12 | Mike Tabbert
CRS-01 | CRS-01 | PI13996 | Verified | 1ACRSC0001, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
CRS-01 | CRS-01 | PI13997 | Verified | 1ACRSK0001, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
CRS-01 | CRS-01 | PI13998 | Verified | 1ACRSX0001, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
CRS-01 | CRS-01 | PI13999 | Verified | 1ACRSX0026, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-12 | Mike Tabbert
CRS-01 | CRS-01 | PI14000 | Verified | 1BCRSC0001, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
CRS-01 | CRS-01 | PI14001 | Verified | 1BCRSK0001, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
CRS-01 | CRS-01 | PI14002 | Verified | 1BCRSX0002, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-12 | Mike Tabbert
CRS-01 | CRS-01 | PI14003 | Verified | 1BCRSX0016, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI14004 | Verified | 1BCRSX0020, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI14005 | Verified | 1BCRSX0021, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI14006 | Verified | 1BCRSX0022, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI14007 | Verified | 1BCRSX0023, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
CRS-01 | CRS-01 | PI14008 | Verified | 1BCRSX0025, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-12 | Mike Tabbert
CRS-01 | CRS-01 | PI14009 | Verified | 1BCRSX0026, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-12 | Mike Tabbert
CRS-01 | CRS-01 | PI14010 | Verified | 1CCRSC0004, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-12 | Mike Tabbert
CRS-01 | CRS-01 | PI14666 | Verified | Complete tubing connection to 1C-CRS-PIT-9700B | A | I | James Tanner | McD | 2019-12-10 | James Tanner | Const | 2019-12-11 | James Tanner | 2019-12-12 | Michael Law
CRS-01 | CRS-01 | PI14667 | Verified | Complete tubing connection to 1C-CRS-PIT-0041 | A | I | James Tanner | McD | 2019-12-10 | James Tanner | Const |  |  | 2019-12-12 | Michael Law
CRS-01 | CRS-01 | PI14668 | Verified | Complete tubing connection to 1C-CRS-FIT-0056 | A | I | James Tanner | McD | 2019-12-10 | James Tanner | Const |  |  | 2019-12-11 | Jack White
CRS-01 | CRS-01 | PI14669 | Verified | Complete tubing connection to 1A-IPS-PIT-8312 | A | I | Gonzalo Pena | McD | 2019-12-10 | Gonzalo Pena | Const | 2020-02-03 | James Tanner | 2020-02-04 | Michael Law
CRS-01 | CRS-01 | PI14670 | Verified | Complete tubing connection to 1B-IPS-PIT-8312 | A | I | Gonzalo Pena | McD | 2019-12-10 | Gonzalo Pena | Const | 2020-02-10 | James Tanner | 2020-02-10 | Fred Michael
CRS-01 | CRS-01 | PI14686 | Verified | 1AIPSX0003, To Termination | A | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
CRS-01 | CRS-01 | PI14690 | Verified | 1C-CRS-PIT-0041-NEED TO INSTALL TUBE BUNDLE. | A | I | James Tanner | McD | 2019-12-11 | James Tanner | Const | 2019-12-12 | Michael Law | 2019-12-13 | John Sullivan
CRS-01 | CRS-01 | PI14691 | Verified | 1C-CRS-PIT-0011-NEED TO SHRINK BOOT ON TUBE BUNDLE. | B | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-14 | John Sullivan
CRS-01 | CRS-01 | PI14692 | Verified | 1C-CRS-PIT-0041-NEED TO INSTALL INSTRUMENT I.D. TAG | C | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-14 | John Sullivan
CRS-01 | CRS-01 | PI14693 | Verified | 1C-CRS-PIT-0011-NEED TO INSTALL I.D. TAG ON INSTRUMENT. | C | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-13 | John Sullivan
CRS-01 | CRS-01 | PI14815 | Verified | 1C-CRS-PIT-9700B-NEED TO SHRINK BOOT ON TUBE BUNDLE(1C-HTS-CAB-0103) - DUPLICATE PUNCH ITEM - JOHN S. | B | I | James Tanner | McD | 2019-12-15 | James Tanner | Const |  |  | 2019-12-15 | Eric Policarpio
CRS-01 | CRS-01 | PI14816 | Verified | 1C-HTS-CAB-0103-NEED TO CLEAN BOX INSIDE AND OUT. | B | I | James Tanner | McD | 2019-12-15 | James Tanner | Const | 2019-12-17 | Gonzalo Pena | 2019-12-18 | John Sullivan
CRS-01 | CRS-01 | PI14823 | Verified | NEED TO INSTALL TUBE BUNDLE FOR 1A-CRS-FIT-0030.(1A-HTS-CAB-0313) | B | I | Gonzalo Pena | McD | 2019-12-15 | Gonzalo Pena | Const | 2020-02-10 | James Tanner | 2020-02-10 | Fred Michael
CRS-01 | CRS-01 | PI14824 | Verified | NEED TO INSTALL I.D. TAG ON 1A-CRS-FIT-0030.(1A-HTS-CAB-0313) | C | I | James Tanner | McD | 2019-12-15 | James Tanner | Const | 2019-12-30 | Gonzalo Pena | 2020-01-14 | John Sullivan
CRS-01 | CRS-01 | PI14863 | Verified | 1A-CRS-TE-8406C, Replace TE because of water Damage | A | I | Gonzalo Pena | McD | 2019-12-23 | Gonzalo Pena | Comm | 2020-01-29 | Gonzalo Pena | 2020-01-29 | Mike Tabbert
CRS-01 | CRS-01 | PI15832 | Verified | Install Condensing Pot (2 each) 1A-CRS-FIT-0030 | B | P | James Beech | McD | 2020-01-09 | James Beech | Const | 2020-02-07 | James Beech | 2020-02-07 | Kelvin Cook
CRS-01 | CRS-01 | PI15833 | Verified | Install Condensing Pot (2 each) 1B-CRS-FIT-0030 | B | P | James Beech | McD | 2020-01-09 | James Beech | Const | 2020-02-07 | James Beech | 2020-02-07 | Kelvin Cook
CRS-01 | CRS-01 | PI15891 | Verified | Pipe leading to 1B-CRS-AOV-0020 needs additional support, located under HRSGB | D | P | Michael Law | McD | 2020-01-13 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
CRS-01 | CRS-01 | PI16034 | Verified | Install Final Trim on valve 1C-CRS-AOV-9720 | A | P | Shane Crowe | McD | 2020-01-14 | Shane Crowe | Const | 2020-02-06 | Shane Crowe | 2020-02-07 | Kelvin Cook
CRS-01 | CRS-01 | PI16035 | Verified | Install Final Trim on valve 1C-STS-CRV-9000A | A | P | Shane Crowe | McD | 2020-01-14 | Shane Crowe | Const | 2020-02-03 | Shane Crowe | 2020-02-03 | Kelvin Cook
CRS-01 | CRS-01 | PI16036 | Verified | Install Final Trim on valve 1C-STS-CRV-9000B | A | P | Shane Crowe | McD | 2020-01-14 | Shane Crowe | Const | 2020-02-03 | Shane Crowe | 2020-02-03 | Kelvin Cook
CRS-01 | CRS-01 | PI17572 | Verified | Missing Vent Hole, Hgr 531 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-27 | James Beech | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17573 | Verified | Missing Shim Plate, Hanger 908 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-27 | James Beech | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17574 | Verified | Missing Vent Hole, Hanger 908 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-27 | James Beech | 2021-07-06 | John Watts
CRS-01 | CRS-01 | PI17575 | Verified | Missing washers -- has loose nuts, hanger 524 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-27 | James Beech | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17576 | Verified | Installed not per dwg (hanger 508) -- different design type support. | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17577 | Verified | Missing tag (thermal well w/temp element) | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-22 | James Beech | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17578 | Verified | Not installed to design dwg, clam & turnbuckle (different type), 1B-CRS-HGR-0519 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17579 | Verified | Incomplete installation (cotter pin), 1A-CRS-HGR-0507 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-29 | James Beech | 2020-12-16 | Dave Goldak
CRS-01 | CRS-01 | PI17580 | Verified | Incomplete installation wiring and conduit cover, 1A-CRS-TE-0030 | C | E | Chris Colvin | McD | 2020-03-03 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2021-05-24 | Keith Pollock
CRS-01 | CRS-01 | PI17581 | Verified | Not installed per dwg (1A-CRS HGR-0507), different type installed | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17582 | Verified | Missing tag, 1A-CRS-FE-0030 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-23 | James Beech | 2020-10-06 | Dave Goldak
CRS-01 | CRS-01 | PI17583 | Verified | Missing tag, 1A-CRS-TE-0030 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-23 | James Beech | 2020-10-06 | Dave Goldak
CRS-01 | CRS-01 | PI17584 | Verified | Incomplete wiring and conduit cover, 1A-CRS-TE-0030 | C | E | Chris Colvin | McD | 2020-03-03 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2021-05-24 | Keith Pollock
CRS-01 | CRS-01 | PI17585 | Verified | Missing vent hole, 1A-CRS-HGR-0903 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-30 | James Beech | 2021-07-06 | John Watts
CRS-01 | CRS-01 | PI17586 | Verified | Missing patch paint, 1A-CRS-HGR-0903 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2021-07-22 | Eric Policarpio | 2021-07-22 | John Watts
CRS-01 | CRS-01 | PI17587 | Verified | Separating insulation lagging above hanger 0507 | C | Q | Josh Koerner | PCI | 2020-03-03 | Josh Koerner | Comm | 2020-06-19 | Jason Ezell | 2020-06-19 | Jason Ezell
CRS-01 | CRS-01 | PI17588 | Verified | Missing adjusting rod lock nut, 1A-CRS-HGR-0507 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-22 | James Beech | 2020-12-16 | Dave Goldak
CRS-01 | CRS-01 | PI17589 | Verified | Not installed per design dwg, different type, 1C-CRS-HGR-0503 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17590 | Verified | Installed not per dwg. Different type of spring can supports, 1C-CRS-HGR-0503 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17591 | Verified | Hanger support plates were not installed parallel and bolts are loose, 1C-CRS-HGR-0503 | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm | 2020-09-15 | Jason Ezell | 2021-02-01 | Dave Goldak
CRS-01 | CRS-01 | PI17592 | Verified | Hanger shear lug position and contact not accessable under insulation, 1C-CRS-HGR-0901 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-09 | James Beech | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17593 | Verified | Missing tag 1C-CRS-V-0041. | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-30 | James Beech | 2020-11-11 | Dave Goldak
CRS-01 | CRS-01 | PI17594 | Verified | Un-readable tag 1C-CRS-V-0010 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-30 | James Beech | 2020-07-10 | Dave Goldak
CRS-01 | CRS-01 | PI17595 | Verified | Pipe hanger not installed plumb, 1C-CRS-HGR-0009 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-22 | James Beech | 2020-07-10 | Dave Goldak
CRS-01 | CRS-01 | PI17596 | Verified | Pipe union installed backwards, line 1C-CRS-P41-0064-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-29 | James Beech | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17597 | Verified | Hanger installation not per design, 0" cold gap required, 1/2" cold gap as installed, 1C-HRG-0025 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17598 | Verified | Pipe union installed backwards, line 1C-CRS-P41-005-01 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-29 | James Beech | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17599 | Verified | Missing hardware, anchor bolt washers all four (4) anchors, 1C-CRS-HGR-0021 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-22 | James Beech | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17600 | Verified | Not installed per design, hanger attachment angle not square to cantilever arm, 1C-CRS-HGR-0021 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17601 | Verified | Missing hardware, six (6) pipe attachment U-bolt nuts | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-22 | James Beech | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17602 | Verified | Missing hardware, U-bolt double nuts, 1C-CRS-HGR-023 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-22 | James Beech | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17603 | Verified | Missing hardware, U-bolt double nuts, 1C-CRS-HGR-024 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-22 | James Beech | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17604 | Verified | Installation not complete, adjustment not at cold setting, 1C-CRS-HGR-503 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17605 | Verified | SRV operating arm restrained, 1C-CRV-SRV-0045 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-20 | Tim Green | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17606 | Verified | SRV operating arm restrained, 1C-CRV-SRV-0055 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-20 | Tim Green | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17607 | Verified | SRV operating arm restrained, 1C-CRV-SRV-0075 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-20 | Tim Green | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17608 | Verified | Not per design, turnbuckle installed in hanger rod, 1C-CRS-HGR-0502 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17609 | Verified | Permanent tag missing, 1C-CRS-TW-9705 and TE-9705 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-29 | James Beech | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17610 | Verified | Hanger rod bent, 1C-CRS-HGR-0011 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-23 | James Beech | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17611 | Verified | Installation not complete, hanger rod lock nut not drawn to hanger clamp, 1C-CRS-HGR-0011 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-23 | James Beech | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17612 | Verified | Hanger rod bent, 1C-CRS-HGR-0012 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-23 | James Beech | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17613 | Verified | Hanger not per design type, 1C-CRS-HGR-500 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17614 | Verified | See attached photo DSCN1873; iICRS-HGR-500 | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm | 2020-05-29 | James Beech | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17615 | Verified | Installation not complete, adjustment not at cold setting, 1C-CRS-HGR-501 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17616 | Verified | Hanger not per design type,1C-CRS-HGR-501 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17617 | Verified | Hanger not installed per design, 1C-CRS-HGR-003 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-10 | Dave Goldak
CRS-01 | CRS-01 | PI17618 | Verified | Hanger not in per design location, 1C-CRS-HGR-002 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-07-10 | Eric Policarpio | 2020-07-10 | Dave Goldak
CRS-01 | CRS-01 | PI17619 | Verified | Installation not complete, hanger not adjusted to perpendicular to pipe, 1C-CRS-HGR-003 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-07-10 | James Beech | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17620 | Verified | Missing hardware, hanger rod lock nut to spring support, 1C-CRS-HGR-004 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-23 | James Beech | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17621 | Verified | Missing hardware, restraint pipe clamp bolt and nut, 1C-CRS-HGR-0018 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-23 | James Beech | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17622 | Verified | Installation not complete, restraint pipe clamp nut not fully engaged on bolt, 1C-CRS-HGR-0018 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-23 | James Beech | 2020-07-07 | Dave Goldak
CRS-01 | CRS-01 | PI17623 | Verified | Hanger not per design type, 1C-CRS-HGR-007 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17624 | Verified | Installation not complete, missing hardware, conduit covers, 1A-CRS-TW/TE-0087A, B & C | C | E | Chris Colvin | McD | 2020-03-03 | Chris Colvin | Comm | 2020-04-01 | Chris Colvin | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17625 | Verified | Unistrut conduit not per design standard, not anchored to structure (on conduit for 1A-CRS-TE-0087A, B & C) | C | E | Chris Colvin | McD | 2020-03-03 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17626 | Verified | Hanger not per design type, 1B-CRS-HGR-0522 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17627 | Verified | Installation not complete, conduit covers loose or missing, to 1B-CRS-TW/TE-0087A, B & C, line 1B-CRS-P40-0025-02 | C | E | Chris Colvin | McD | 2020-03-03 | Chris Colvin | Comm | 2020-04-01 | Chris Colvin | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17628 | Verified | Hanger not per design type, 1B-CRS-HGR-0521 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17629 | Verified | Hanger installation alignment not complete, anchor clamp not square to pipe at setting dimension, 1B-CRS-HRG-0521 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-27 | Dave Goldak
CRS-01 | CRS-01 | PI17630 | Verified | Installation not complete, vent hole not found, 1B-CRS-HGR-0907 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-30 | James Beech | 2021-07-06 | John Watts
CRS-01 | CRS-01 | PI17631 | Verified | Hanger not per design type, 1B-CRS-HGR-0523 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17632 | Verified | Hanger not per design location, weld on bracket position not to dimension , 1B-CRS-HGR-0523 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-27 | Dave Goldak
CRS-01 | CRS-01 | PI17633 | Verified | Hanger installation not complete, hardened washers under cotter pins missing, 1B-CRS-HGR-0523 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-08 | James Beech | 2021-07-06 | John Watts
CRS-01 | CRS-01 | PI17634 | Verified | Hanger not per design type, 1B-CRS-HGR-0520 | C | P | Gary Pickeral | McD | 2020-03-03 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
CRS-01 | CRS-01 | PI17635 | Verified | Hanger installation not complete, bolts too short and not torqued, 1B-CRS-HGR-0511 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-08 | James Beech | 2020-11-25 | Dave Goldak
CRS-01 | CRS-01 | PI17636 | Verified | Hanger installation not complete, vent hole not found in locations indicated, 1B-CRS-HGR-0511 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-30 | James Beech | 2020-11-25 | Dave Goldak
CRS-01 | CRS-01 | PI17637 | Verified | Hanger installation not complete, welds not painted with cold galvanizing paint, 1B-CRS-HGR-0511 | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-30 | James Beech | 2020-11-25 | Dave Goldak
CRS-01 | CRS-01 | PI17657 | Verified | 1A-CRS-FV-0015 - The ASCO filter regulator supply gauge is broken. The gauge needs to be replaced before operating the valve. | B | P | James Beech | McD | 2020-03-04 | James Beech | Comm | 2020-03-09 | Tim Green | 2020-06-03 | John Watts
CRS-01 | CRS-01 | PI17857 | Verified | 1B-CRS-TI-8406C 1B Reheater #1 Metal Temp reads 200 degs F lower than other TE's | B | E | Albert Burge | McD | 2020-03-16 | Albert Burge | Comm | 2020-03-19 | Albert Burge | 2020-03-26 | Keith Pollock
CRS-01 | CRS-01 | PI17858 | Verified | 1B-CRS-TI-8406H 1B Reheater #1 Metal Temp reads 75 degs F lower than other TE's | B | E | Albert Burge | McD | 2020-03-16 | Albert Burge | Comm | 2020-03-19 | Albert Burge | 2020-03-26 | Keith Pollock
CTS-01 | CTS-01 | PI01402 | Verified | 1ACTSK0060, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-07 | Mike Tabbert | 2019-06-07 | Mike Tabbert
CTS-01 | CTS-01 | PI02579 | Verified | LK-1A-CTS-PD-P40-0120-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-16 | Tom Noble
CTS-01 | CTS-01 | PI02580 | Verified | LK-1A-CTS-PD-P40-0120-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-15 | Terry Deaton | 2019-08-15 | Tom Noble
CTS-01 | CTS-01 | PI02581 | Verified | LK-1A-CTS-PD-P40-0140-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-23 | Terry Deaton | 2019-08-23 | Tom Noble
CTS-01 | CTS-01 | PI02582 | Verified | LK-1A-CTS-PD-P40-0140-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-15 | Terry Deaton | 2019-08-15 | Tom Noble
CTS-01 | CTS-01 | PI02583 | Verified | LK-1A-CTS-PD-P40-0141-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-20 | Tom Noble
CTS-01 | CTS-01 | PI02584 | Verified | LK-1A-CTS-PD-P40-0141-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-20 | Tom Noble
CTS-01 | CTS-01 | PI02585 | Verified | LK-1A-CTS-PD-P40-0141-03 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-20 | Tom Noble
CTS-01 | CTS-01 | PI02586 | Verified | LK-1A-CTS-PD-P40-0206-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-12 | Tom Noble
CTS-01 | CTS-01 | PI02587 | Verified | LK-1A-CTS-PD-P40-0206-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-12 | Tom Noble
CTS-01 | CTS-01 | PI02588 | Verified | LK-1A-CTS-PD-P41-0101-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-14 | Tom Noble
CTS-01 | CTS-01 | PI02589 | Verified | LK-1A-CTS-PD-P41-0110-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-26 | Terry Deaton | 2019-08-26 | Tom Noble
CTS-01 | CTS-01 | PI02590 | Verified | LK-1A-CTS-PD-P41-0114-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-12 | Tom Noble
CTS-01 | CTS-01 | PI02591 | Verified | LK-1A-CTS-PD-P41-0116-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-26 | Terry Deaton | 2019-08-27 | Tom Noble
CTS-01 | CTS-01 | PI02592 | Verified | LK-1A-CTS-PD-P41-0255-03 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-31 | Terry Deaton | 2019-07-31 | Tom Noble
CTS-01 | CTS-01 | PI02593 | Verified | LK-1A-CTS-PD-P41-0255-04 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-31 | Terry Deaton | 2019-07-31 | Tom Noble
CTS-01 | CTS-01 | PI02594 | Verified | LM-01357 (155126-110100-01-SD-000212) - MBP03BR201 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-07 | Terry Deaton | 2019-08-07 | Tom Noble
CTS-01 | CTS-01 | PI02595 | Verified | LM-01357 (155126-110100-01-SD-000212) - QJA05BR203 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-12 | Tom Noble
CTS-01 | CTS-01 | PI02596 | Verified | LM-01377 (155126-110100-01-SD-000234) - MBR01BR802 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-07 | Tom Noble | 2019-08-07 | Tom Noble
CTS-01 | CTS-01 | PI02597 | Verified | LM-01377 (155126-110100-01-SD-000234) - MBR01BR803 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-16 | Tom Noble
CTS-01 | CTS-01 | PI02598 | Verified | LM-01377 (155126-110100-01-SD-000234) - MBR01BR805 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-16 | Albert Burge | 2019-08-16 | Tom Noble
CTS-01 | CTS-01 | PI02599 | Verified | LM-01377 (155126-110100-01-SD-000234) - MBR01BR806 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-20 | Tom Noble
CTS-01 | CTS-01 | PI02600 | Verified | LM-01377 (155126-110100-01-SD-000234) - MBR01BR807 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-12 | Tom Noble
CTS-01 | CTS-01 | PI02601 | Verified | LM-01380 (155126-110100-01-SD-000236) - QFF11BR114 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-12 | Tom Noble
CTS-01 | CTS-01 | PI03348 | Verified | LM-1380 - Restore piping after pressure test. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-01 | CTS-01 | PI03349 | Verified | LM-1380 - PS2 not installed. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-01 | CTS-01 | PI03350 | Verified | LM-1380 - 24A0A-PS1 not installed. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-01 | CTS-01 | PI03351 | Verified | Southeast corner of GT enclosure - wall penetration - 4x4 steel needs to be set proper & install bolts. | A | M | Sheri Fritz | PCI | 2019-08-07 | Sheri Fritz | Const | 2019-08-09 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-01 | CTS-01 | PI03352 | Verified | LM-1380 - Torque all flanges & bend tabs. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-01 | CTS-01 | PI03353 | Verified | LM-1380 - All u-bolts need top & bottom nuts. | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-01 | CTS-01 | PI03354 | Verified | Pressure gauge is loose on the instrument air tank in the gas turbine enclosure. | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-14 | Gonzalo Pena | 2019-08-15 | Kelvin Cook
CTS-01 | CTS-01 | PI03355 | Verified | Instrument air receiver tank supply line bronze valve missing handle. | A | P | Eddie Vannoy | McD | 2019-08-07 | Eddie Vannoy | Const | 2019-10-01 | Michael Law | 2019-10-03 | Kelvin Cook
CTS-01 | CTS-01 | PI03356 | Verified | Tag all Instrument Air skid components in the GT enclosure. | C | M | James Strange | MHI | 2019-08-07 | James Strange | Const | 2020-04-01 | James Strange | 2020-04-01 | Eric Policarpio
CTS-01 | CTS-01 | PI03357 | Verified | Tag all Seal Air skid components in the GT enclosure. | C | M | James Strange | MHI | 2019-08-07 | James Strange | Const | 2020-04-01 | James Strange | 2020-04-01 | Eric Policarpio
CTS-01 | CTS-01 | PI03358 | Verified | Install orifice plate at A4A0A-09 & 24A0A-08. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-16 | Kelvin Cook
CTS-01 | CTS-01 | PI03359 | Verified | Remove rope from 1-1/2" instrument air header. | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-01 | CTS-01 | PI03360 | Verified | LM-1362 - Install flex hoses. | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-14 | Kelvin Cook
CTS-01 | CTS-01 | PI03361 | Verified | LM-1364 - Install flex hoses. | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-14 | Kelvin Cook
CTS-01 | CTS-01 | PI03362 | Verified | LM-1365 - Install flex hoses. | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-14 | Kelvin Cook
CTS-01 | CTS-01 | PI03363 | Verified | LM-1357 - 21A0D-PS-34 - Missing u-bolt. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Gonzalo Pena | 2019-08-16 | Kelvin Cook
CTS-01 | CTS-01 | PI03364 | Verified | LM-1355 - 21A0A-PS-28 - Install u-bolt properly (top & bottom nuts). | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-01 | CTS-01 | PI03365 | Verified | LM-1355 - 21A0B-PS-31 - Install per detail. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-19 | Kelvin Cook
CTS-01 | CTS-01 | PI03366 | Verified | LM-1357 - 21A0D-PS-01 - Loose u-bolt. | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-01 | CTS-01 | PI03367 | Verified | LM-1359-21A0D-PS-02 - Missing u-bolt. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-16 | Kelvin Cook
CTS-01 | CTS-01 | PI03368 | Verified | LM-1353-21A0D-PS-04 - Missing u-bolt & SS plate. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-16 | Kelvin Cook
CTS-01 | CTS-01 | PI03369 | Verified | LM-1355-21A0D-PS-02 - Loose u-bolt. | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-01 | CTS-01 | PI03370 | Verified | Clamp on Instrument air tubing on south end of GT enclosure missing bolt. LM-1379-23A0K-PS-20. | B | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-15 | Kelvin Cook
CTS-01 | CTS-01 | PI03371 | Verified | LM-1379-23A0K-PS-19 missing. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-01 | CTS-01 | PI03372 | Verified | LM-1379 - Tee branch between PS-18 & PS-17 damaged. Replace. | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-15 | Kelvin Cook
CTS-01 | CTS-01 | PI03373 | Verified | LM-1386 - Loose u-bolts - 27A0K-PS-01 & 02. | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-01 | CTS-01 | PI03374 | Verified | FGPA unit pipe - Restore all after pressure test. Bolts, bend tabs & ground - gasket on order K.Cook 18-Sep | A | P | James Beech | McD | 2019-08-07 | James Beech | Const | 2019-08-19 | Terry Deaton | 2019-10-19 | Kelvin Cook
CTS-01 | CTS-01 | PI03375 | Verified | LM-1359 (1A-MBP03AA823 & 824) - flex hose not installed. | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-14 | Kelvin Cook
CTS-01 | CTS-01 | PI03376 | Verified | LM-1359 - 21A0C-14 - install proper bolts & grounding. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-01 | CTS-01 | PI03413 | Verified | Install missing hardware for the LP bleed air manifold connection LC-01596-23OA-5. Torque and bend washers. | B | P | James Beech | McD | 2019-08-09 | James Beech | Const | 2019-11-04 | Kelvin Cook | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI03414 | Verified | Complete EB-01 insulation per LC-01577 | B | M | Sheri Fritz | PCI | 2019-08-09 | Sheri Fritz | Const | 2019-12-06 | Michael Law | 2020-01-15 | Ron McMurtry
CTS-01 | CTS-01 | PI03415 | Verified | Seal EB-01 penetration into the GT enclosure per LC-01587-GB00248673-items 19/20/21/22 | B | M | Bobby Williams | McD | 2019-08-09 | Bobby Williams | Const | 2019-12-02 | Bobby Williams | 2020-01-15 | Ron McMurtry
CTS-01 | CTS-01 | PI03416 | Verified | Install pipe penetration plates and closure plates for the GT enclosure. Install pipe insulation in areas required prior to fitting plate. Install plates per LC-01587 pages 84 and 85 | B | P | Bobby Williams | McD | 2019-08-09 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI03531 | Verified | Complete grout of the GT enclosure | C | C | Johnny Campbell | McD | 2019-08-09 | Johnny Campbell | Const | 2019-10-08 | Johnny Campbell | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI03532 | Verified | Complete grout of all instrumentation stanchions | B | C | Johnny Campbell | McD | 2019-08-09 | Johnny Campbell | Const | 2019-11-12 | Johnny Campbell | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI03534 | Verified | Complete pressure test and remove blind plate for the No. 1 bearing vibration probe cooling air line. Restore flange with orifice plate per LC-01624-24AOA-4, with items 7, G2, B3/4/5 | A | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-23 | Terry Deaton | 2019-08-28 | Brian Ballard
CTS-01 | CTS-01 | PI03536 | Verified | Confirm torque for the blade path thermocouples and complete tire-wire | A | M | Shane Crowe | McD | 2019-08-09 | Shane Crowe | Const | 2019-08-13 | Shane Crowe | 2019-08-22 | Brian Ballard
CTS-01 | CTS-01 | PI03537 | Verified | Remove FME cover and restore IGMT plate per LC-01818-GQ-03370 | A | M | Shane Crowe | McD | 2019-08-09 | Shane Crowe | Const | 2019-08-16 | Shane Crowe | 2019-08-28 | Brian Ballard
CTS-01 | CTS-01 | PI03538 | Verified | Grease the turbine end support per LC-00374 QTY 4 locations | B | M | Shane Crowe | McD | 2019-08-09 | Shane Crowe | Const | 2019-12-02 | Shane Crowe | 2019-12-06 | Ron McMurtry
CTS-01 | CTS-01 | PI03540 | Verified | Complete the casing metal thermocouple installation per LC-01818-G1-CO694 | A | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI03541 | Verified | Complete the CPFM installation per LC-01818-G1-CO946 | B | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-11-13 | James Tanner | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI03542 | Verified | Replace ignitor air supply regulator gauge and complete the instrument air supply per LI-01236 | A | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-08-23 | Gonzalo Pena | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI03543 | Verified | Confirm torque for the ignitor hardware (232 ft-lbs) and complete tie-wire. | A | M | Shane Crowe | McD | 2019-08-09 | Shane Crowe | Const | 2019-08-09 | Shane Crowe | 2019-08-22 | Brian Ballard
CTS-01 | CTS-01 | PI03544 | Verified | Ensure conduit can be positioned away from the filter bleed pipe. This pipe requires 3" thick insulation. | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-22 | Brian Ballard
CTS-01 | CTS-01 | PI03545 | Verified | Repair damaged enclosure wall section. | B | M | Shane Crowe | McD | 2019-08-09 | Shane Crowe | Const | 2019-08-14 | Shane Crowe | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI03547 | Verified | Repair the GT enclosure gasket and restore enclosure wall support. | B | M | Shane Crowe | McD | 2019-08-09 | Shane Crowe | Const | 2019-08-09 | Shane Crowe | 2019-08-28 | Brian Ballard
CTS-01 | CTS-01 | PI03550 | Verified | Tie-wire the inlet maifold drain union | B | M | Shane Crowe | McD | 2019-08-09 | Shane Crowe | Const | 2019-08-14 | Shane Crowe | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI03551 | Verified | Remove excess gasket material and caulk/seal enclosure wall to the generator foundation. | B | M | Shane Crowe | McD | 2019-08-09 | Shane Crowe | Const | 2019-08-13 | Shane Crowe | 2019-08-28 | Brian Ballard
CTS-01 | CTS-01 | PI03552 | Verified | Complete the fuel gas system pressure test and remove blind plates. Install missing hardware and torque and bend lock washers with new gaskets. | A | P | Dillion Starkey | McD | 2019-08-09 | Dillion Starkey | Const | 2019-08-19 | Terry Deaton | 2019-08-28 | Brian Ballard
CTS-01 | CTS-01 | PI03553 | Verified | Complete the instrument air supply to the flame ddetectors and ignitors per LI-01236 | A | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI03554 | Verified | Clean the compressor inlet area | B | M | Shane Crowe | McD | 2019-08-09 | Shane Crowe | Const | 2019-08-13 | Shane Crowe | 2019-08-28 | Brian Ballard
CTS-01 | CTS-01 | PI03555 | Verified | Set IGV angles and record clearances, comlete water was air blow, and BSI the compressor inlet. | B | M | Dillion Starkey | McD | 2019-08-09 | Dillion Starkey | Const |  |  | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI03557 | Verified | Replace gasket per LC-01818-GI-CO853-E0, gasket is 10R-600-80. Retorque and bend lock washers after gasket is replaced. | B | M | Brian Ballard | MHI | 2019-08-09 | Brian Ballard | Const |  |  | 2019-11-23 | Brian Ballard
CTS-01 | CTS-01 | PI03558 | Verified | Install SS shin to separate dissimiliar materials for the ipe support, located right side of unit. | A | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-22 | Brian Ballard
CTS-01 | CTS-01 | PI03559 | Verified | Secure pipe support in correct location for the No. 1 bearing seal air line per LC-01623-23AOH-PS-13 | A | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-22 | Brian Ballard
CTS-01 | CTS-01 | PI03560 | Verified | Remove garlock gasket for the GT drain blade wash pipe connection to the compressor case, install permanent gasket per LC-01626-45AOA-15, gasket G5 is the required gasket. | A | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-22 | Brian Ballard
CTS-01 | CTS-01 | PI03561 | Verified | Remove garlock gasket for the GT drain blade wash pipe connection to the compressor case, install permanent gasket per LC-01626-45AOA-9, gasket G5 is the required gasket. | A | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-22 | Brian Ballard
CTS-01 | CTS-01 | PI03562 | Verified | Remove garlock gasket for the GT drain blade wash pipe connection to the compressor case, install permanent gasket per LC-01626-45AOA-12, gasket G5 is the required gasket. | A | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-12 | Terry Deaton | 2019-08-22 | Brian Ballard
CTS-01 | CTS-01 | PI03563 | Verified | Install support and secure the Row 4 D/C downstream thermocouple per LC-01818-G1-A9058. | A | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-08-23 | Gonzalo Pena | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI03564 | Verified | Repair tie-wire for the EE-00 connection the FWD exhaust manifold, located on the bottom area. | B | M | Shane Crowe | McD | 2019-08-09 | Shane Crowe | Const | 2019-08-09 | Shane Crowe | 2019-08-28 | Brian Ballard
CTS-01 | CTS-01 | PI03565 | Verified | Remove garlock gaskets and restore with permanent gaskets for the GT drain blade wash pipe. Restore flange per LC-01626-45AOA-27/29. Gaskets G3 and G#3are required at this location | A | P | James Beech | McD | 2019-08-09 | James Beech | Const | 2019-09-05 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI03566 | Verified | Remove garlock gaskets for the GT drain blade wash pipe and restore per LC-01626-45AOA-35/37. Gaskets G3 and G3 are required at this location | A | P | James Beech | McD | 2019-08-09 | James Beech | Const | 2019-09-05 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI03819 | Verified | Complete pipe test & submit CCFs to turnover. | A | P | James Beech | McD | 2019-08-13 | James Beech | Const | 2019-08-14 | Kelvin Cook | 2019-10-28 | Ed Gober
CTS-01 | CTS-01 | PI03827 | Verified | Ground all 7 JBs on east side mezz to ground grid. | A | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03828 | Verified | Ground all JB conduit bushings on east side mezz. | A | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03829 | Verified | Seal all conduits in JBs on east side mezz. | B | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI03830 | Verified | Install toe plate under the Junction Boxes on the gas turbine east side mezz. | C | S | Bobby Williams | McD | 2019-08-13 | Bobby Williams | Const | 2020-01-16 | Tim Gallegos | 2020-01-21 | Michael Law
CTS-01 | CTS-01 | PI03831 | Verified | Ground seal tite on JBs on east side mezz. | A | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03832 | Verified | Tighten all seal tite connectors. | A | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03833 | Verified | Straighten up cables in tray under the east side mezz going back to the main cable tray. | B | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-11-13 | Brad Stanford | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI03834 | Verified | Ground cable tray 1ATL411011 and add ground jumper to lower cable tray on the east side. | A | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03837 | Verified | Flex for Disc Cavity TE #5 is too short, east side. | A | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03838 | Verified | Tie-wire all TCs in the gas turbine enclosure. | A | I | Gonzalo Pena | McD | 2019-08-13 | Gonzalo Pena | Const | 2019-08-20 | Gonzalo Pena | 2019-12-18 | Keith Mahoney
CTS-01 | CTS-01 | PI03839 | Verified | Torque all TC flanges. | A | M | Shane Crowe | McD | 2019-08-13 | Shane Crowe | Const | 2019-08-16 | Shane Crowe | 2019-12-18 | Keith Mahoney
CTS-01 | CTS-01 | PI03840 | Verified | Pour all seal-offs. | B | E | Chris Colvin | McD | 2019-08-13 | Chris Colvin | Const | 2019-12-23 | Michael Law | 2020-01-08 | Mike Tabbert
CTS-01 | CTS-01 | PI03841 | Verified | Tighten flex on blade path TE box. | A | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-08-20 | Dustin Futrell | 2019-08-28 | Shannon Scott
CTS-01 | CTS-01 | PI03842 | Verified | Add support for flex on blade path TE. | B | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-29 | Shannon Scott
CTS-01 | CTS-01 | PI03843 | Verified | Install thrust probes for bearing #2 area. | A | I | Gonzalo Pena | McD | 2019-08-13 | Gonzalo Pena | Const | 2019-08-23 | Gonzalo Pena | 2019-12-18 | Keith Mahoney
CTS-01 | CTS-01 | PI03844 | Verified | Ground bearing #2 rotor grounding brush. | A | E | Chris Colvin | McD | 2019-08-13 | Chris Colvin | Const | 2019-08-16 | Gonzalo Pena | 2019-12-18 | Keith Mahoney
CTS-01 | CTS-01 | PI03845 | Verified | Need plug on combustor sheel pressure header, east side. | A | I | Gonzalo Pena | McD | 2019-08-13 | Gonzalo Pena | Const | 2019-08-20 | Gonzalo Pena | 2019-08-21 | Fred Michael
CTS-01 | CTS-01 | PI03846 | Verified | Instrument tubing at south end of turbine needs to be moved out of the center and should not slope up. | A | I | Gonzalo Pena | McD | 2019-08-13 | Gonzalo Pena | Const | 2019-08-20 | Gonzalo Pena | 2019-08-21 | Albert Burge
CTS-01 | CTS-01 | PI03847 | Verified | MBA01CT023 - need slack in flex. | A | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-28 | Albert Burge
CTS-01 | CTS-01 | PI03848 | Verified | Case cooling flex needs ground - west mezz. | A | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-09-26 | Logan Holland
CTS-01 | CTS-01 | PI03849 | Verified | Instrument air accumulator regulator needs a SS plug, east side ground level. | A | I | Gonzalo Pena | McD | 2019-08-13 | Gonzalo Pena | Const | 2019-08-15 | Gonzalo Pena | 2019-08-19 | Albert Burge
CTS-01 | CTS-01 | PI03850 | Verified | 1AMBM01AA201 needs bug screen. | B | I | Gonzalo Pena | McD | 2019-08-13 | Gonzalo Pena | Const | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Fred Michael
CTS-01 | CTS-01 | PI03851 | Verified | Complete the instrument air tubing to 1AMBM01AA201. | A | I | Gonzalo Pena | McD | 2019-08-13 | Gonzalo Pena | Const | 2019-08-15 | Gonzalo Pena | 2019-08-21 | Fred Michael
CTS-01 | CTS-01 | PI03852 | Verified | Complete the instrument air tubing to all valves. | A | I | Gonzalo Pena | McD | 2019-08-13 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-10-28 | Albert Burge
CTS-01 | CTS-01 | PI03853 | Verified | Stand for 1A-MBY91GZ006 needs securing, west side ground level. | B | I | Gonzalo Pena | McD | 2019-08-13 | Gonzalo Pena | Const | 2019-08-20 | Gonzalo Pena | 2019-08-21 | Fred Michael
CTS-01 | CTS-01 | PI03854 | Verified | Four valves in the FGPA Unit need bug screens. | B | I | Gonzalo Pena | McD | 2019-08-13 | Gonzalo Pena | Const | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Fred Michael
CTS-01 | CTS-01 | PI03855 | Verified | Ground the cable tray on the west side, at FGPA Unit. | A | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-09-04 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI03856 | Verified | Cable tray on the west side needs hold down clamps & labels. | B | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-11-13 | Brad Stanford | 2019-11-20 | Fred Michael
CTS-01 | CTS-01 | PI03867 | Verified | 1ACTSK0095, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-10-02 | Mike Tabbert
CTS-01 | CTS-01 | PI03868 | Verified | 1ACTSK0096, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-10-02 | Mike Tabbert
CTS-01 | CTS-01 | PI03869 | Verified | 1ACTSK0124, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-20 | Dustin Futrell | 2019-08-21 | Mike Tabbert
CTS-01 | CTS-01 | PI03870 | Verified | 1ACTS-MBY01GH013-DC001-K0006, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03871 | Verified | 1ACTS-MKA01CY501-AS001-X0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03872 | Verified | 1ACTS-MKA01CY502-AS001-X0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03873 | Verified | 1ACTS-MKA01CY503-AS001-X0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03874 | Verified | 1ACTS-MKA01CY504-AS001-X0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03875 | Verified | 1ACTS-MKC01CY501-AS001-X0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03876 | Verified | 1ACTS-MKC01CY502-AS001-X0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03877 | Verified | 1ACTSX0115, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-20 | Dustin Futrell | 2019-08-21 | Mike Tabbert
CTS-01 | CTS-01 | PI03878 | Verified | 1ACTSX0116, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-20 | Dustin Futrell | 2019-08-21 | Mike Tabbert
CTS-01 | CTS-01 | PI03879 | Verified | 1ACTSX0184, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03880 | Verified | 1ACTSX0186, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Mike Tabbert | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03881 | Verified | 1ACTSX0320, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03882 | Verified | 1ACTSX0322, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03883 | Verified | 1ACTSX0329, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03884 | Verified | 1ACTSX0330, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03885 | Verified | 1ACTSX0334, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03886 | Verified | 1ACTSX0335, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03887 | Verified | 1ACTSX0369, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-04 | Mike Tabbert
CTS-01 | CTS-01 | PI03890 | Verified | 1ACTSX0440, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-04 | Mike Tabbert
CTS-01 | CTS-01 | PI03891 | Verified | 1ACTS-BVR01-DS005-C0001, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03892 | Verified | 1ACTSC0013, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03893 | Verified | 1ACTSC0019, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03894 | Verified | 1ACTSC0020, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03895 | Verified | 1ACTSC0021, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03896 | Verified | 1ACTSC0022, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03897 | Verified | 1ACTSC0023, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03898 | Verified | 1ACTSC0024, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03899 | Verified | 1ACTSC0026, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03900 | Verified | 1ACTSC0044, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03901 | Verified | 1ACTSC0156, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03902 | Verified | 1ACTSC0158, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03903 | Verified | 1ACTSC0172, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03904 | Verified | 1ACTSC0173, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03905 | Verified | 1ACTSC0193, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI03906 | Verified | 1ACTSC0198, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI03907 | Verified | 1ACTSC0200, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI03908 | Verified | 1ACTSC0204, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-20 | Dustin Futrell | 2019-08-21 | Mike Tabbert
CTS-01 | CTS-01 | PI03909 | Verified | 1ACTSC0208, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI03910 | Verified | 1ACTSC0210, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03911 | Verified | 1ACTSC0258, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03912 | Verified | 1ACTSC0259, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CTS-01 | CTS-01 | PI03913 | Verified | 1ACTSC0260, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03914 | Verified | 1ACTSC0261, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03915 | Verified | 1ACTSC0262, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03916 | Verified | 1ACTSC0263, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03917 | Verified | 1ACTSC0264, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03918 | Verified | 1ACTSC0265, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03919 | Verified | 1ACTSC0266, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03920 | Verified | 1ACTSC0267, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03921 | Verified | 1ACTSC0268, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03922 | Verified | 1ACTSC0269, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CTS-01 | CTS-01 | PI03923 | Verified | 1ACTSC0270, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03924 | Verified | 1ACTSC0271, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-11 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI03925 | Verified | 1ACTSC0272, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI03926 | Verified | 1ACTSC0273, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03927 | Verified | 1ACTSC0274, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI03938 | Verified | 1ACTSC0302, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03939 | Verified | 1ACTSC0303, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03940 | Verified | 1ACTSC0325, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03941 | Verified | 1ACTSC0326, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-04 | Mike Tabbert
CTS-01 | CTS-01 | PI03942 | Verified | 1ACTSC0329, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03943 | Verified | 1ACTSC0336, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI03944 | Verified | 1ACTSC0340, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03945 | Verified | 1ACTSC0345, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-04 | Mike Tabbert
CTS-01 | CTS-01 | PI03946 | Verified | 1ACTSC0346, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CTS-01 | CTS-01 | PI03947 | Verified | 1ACTSC0356, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03948 | Verified | 1ACTS-CHC00GH001-DS120-C0001, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03949 | Verified | 1ACTSK0023, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03950 | Verified | 1ACTSK0024, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03951 | Verified | 1ACTSK0038, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03952 | Verified | 1ACTSK0040, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03953 | Verified | 1ACTSK0054, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03954 | Verified | 1ACTSK0056, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03955 | Verified | 1ACTSK0057, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03956 | Verified | 1ACTSK0068, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03957 | Verified | 1ACTSK0072, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03958 | Verified | 1ACTSK0095, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CTS-01 | CTS-01 | PI03959 | Verified | 1ACTSK0096, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CTS-01 | CTS-01 | PI03960 | Verified | 1ACTSK0097, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03961 | Verified | 1ACTSK0098, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03962 | Verified | 1ACTS-MBY01GH013-DC001-K0006, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03963 | Verified | 1ACTS-MKA01CY501-AS001-X0001, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03964 | Verified | 1ACTS-MKA01CY502-AS001-X0001, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-01 | CTS-01 | PI03965 | Verified | 1ACTS-MKA01CY503-AS001-X0001, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03966 | Verified | 1ACTS-MKA01CY504-AS001-X0001, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03967 | Verified | 1ACTS-MKC01CY501-AS001-X0001, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03968 | Verified | 1ACTS-MKC01CY502-AS001-X0001, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI03969 | Verified | 1ACTSX0001, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI03970 | Verified | 1ACTSX0104, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03971 | Verified | 1ACTSX0105, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-08-21 | Fred Michael
CTS-01 | CTS-01 | PI03972 | Verified | 1ACTSX0106, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03973 | Verified | 1ACTSX0107, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03974 | Verified | 1ACTSX0108, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03975 | Verified | 1ACTSX0115, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03976 | Verified | 1ACTSX0118, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03977 | Verified | 1ACTSX0139, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03978 | Verified | 1ACTSX0144, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03979 | Verified | 1ACTSX0160, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CTS-01 | CTS-01 | PI03980 | Verified | 1ACTSX0162, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CTS-01 | CTS-01 | PI03981 | Verified | 1ACTSX0164, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CTS-01 | CTS-01 | PI03982 | Verified | 1ACTSX0166, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CTS-01 | CTS-01 | PI03983 | Verified | 1ACTSX0168, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CTS-01 | CTS-01 | PI03984 | Verified | 1ACTSX0170, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03985 | Verified | 1ACTSX0171, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03986 | Verified | 1ACTSX0180, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CTS-01 | CTS-01 | PI03987 | Verified | 1ACTSX0182, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CTS-01 | CTS-01 | PI03988 | Verified | 1ACTSX0184, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03989 | Verified | 1ACTSX0185, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03990 | Verified | 1ACTSX0186, From Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03991 | Verified | 1ACTSX0187, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI03992 | Verified | 1ACTSX0188, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI03993 | Verified | 1ACTSX0190, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03994 | Verified | 1ACTSX0198, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI03995 | Verified | 1ACTSX0200, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03996 | Verified | 1ACTSX0201, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03997 | Verified | 1ACTSX0203, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI03998 | Verified | 1ACTSX0251, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI03999 | Verified | 1ACTSX0252, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI04000 | Verified | 1ACTSX0253, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI04001 | Verified | 1ACTSX0254, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI04002 | Verified | 1ACTSX0255, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI04003 | Verified | 1ACTSX0268, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-05 | Mike Tabbert
CTS-01 | CTS-01 | PI04004 | Verified | 1ACTSX0269, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04005 | Verified | 1ACTSX0278, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04006 | Verified | 1ACTSX0279, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04007 | Verified | 1ACTSX0280, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04008 | Verified | 1ACTSX0281, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04009 | Verified | 1ACTSX0285, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04010 | Verified | 1ACTSX0286, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04011 | Verified | 1ACTSX0288, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04012 | Verified | 1ACTSX0289, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI04013 | Verified | 1ACTSX0292, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04014 | Verified | 1ACTSX0295, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI04015 | Verified | 1ACTSX0296, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI04016 | Verified | 1ACTSX0297, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04017 | Verified | 1ACTSX0298, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04018 | Verified | 1ACTSX0307, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI04019 | Verified | 1ACTSX0315, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04020 | Verified | 1ACTSX0316, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04021 | Verified | 1ACTSX0320, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04022 | Verified | 1ACTSX0322, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04023 | Verified | 1ACTSX0324, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04024 | Verified | 1ACTSX0325, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04025 | Verified | 1ACTSX0326, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04026 | Verified | 1ACTSX0327, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04027 | Verified | 1ACTSX0328, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04028 | Verified | 1ACTSX0329, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04029 | Verified | 1ACTSX0330, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04030 | Verified | 1ACTSX0331, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI04031 | Verified | 1ACTSX0332, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04032 | Verified | 1ACTSX0333, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04033 | Verified | 1ACTSX0334, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04034 | Verified | 1ACTSX0335, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04035 | Verified | 1ACTSX0336, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI04036 | Verified | 1ACTSX0337, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI04037 | Verified | 1ACTSX0338, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-01 | CTS-01 | PI04038 | Verified | 1ACTSX0358, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04039 | Verified | 1ACTSX0364, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-05 | Mike Tabbert
CTS-01 | CTS-01 | PI04040 | Verified | 1ACTSX0365, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04041 | Verified | 1ACTSX0366, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-05 | Mike Tabbert
CTS-01 | CTS-01 | PI04042 | Verified | 1ACTSX0367, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04043 | Verified | 1ACTSX0368, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04044 | Verified | 1ACTSX0369, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04045 | Verified | 1ACTSX0370, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04046 | Verified | 1ACTSX0371, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04047 | Verified | 1ACTSX0372, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04048 | Verified | 1ACTSX0375, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04049 | Verified | 1ACTSX0376, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04050 | Verified | 1ACTSX0377, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04051 | Verified | 1ACTSX0378, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04052 | Verified | 1ACTSX0379, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04053 | Verified | 1ACTSX0380, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04054 | Verified | 1ACTSX0381, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04055 | Verified | 1ACTSX0382, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04068 | Verified | 1ACTSX0416, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04069 | Verified | 1ACTSX0419, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04070 | Verified | 1ACTSX0422, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-01 | CTS-01 | PI04071 | Verified | 1ACTSX0423, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-01 | CTS-01 | PI04072 | Verified | 1ACTSX0424, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04073 | Verified | 1ACTSX0425, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04074 | Verified | 1ACTSX0430, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04075 | Verified | 1ACTSX0431, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04083 | Verified | 1ACTSX0440, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-24 | Mike Tabbert
CTS-01 | CTS-01 | PI04084 | Verified | 1ACTS-BVR01-DS005-C0001, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04085 | Verified | 1ACTSC0025, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04086 | Verified | 1ACTSC0044, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04087 | Verified | 1ACTSC0149, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04088 | Verified | 1ACTSC0153, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04089 | Verified | 1ACTSC0154, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04090 | Verified | 1ACTSC0157, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04091 | Verified | 1ACTSC0160, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04092 | Verified | 1ACTSC0162, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04093 | Verified | 1ACTSC0193, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04094 | Verified | 1ACTSC0200, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04095 | Verified | 1ACTSC0204, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04096 | Verified | 1ACTSC0208, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04097 | Verified | 1ACTSC0210, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04098 | Verified | 1ACTSC0258, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04099 | Verified | 1ACTSC0259, To Termination | A | E | Mike Tabbert | McD | 2019-08-14 | Mike Tabbert | Const | 2019-10-09 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CTS-01 | CTS-01 | PI04100 | Verified | 1ACTSC0260, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04101 | Verified | 1ACTSC0263, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-05 | Mike Tabbert
CTS-01 | CTS-01 | PI04102 | Verified | 1ACTSC0264, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04103 | Verified | 1ACTSC0269, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CTS-01 | CTS-01 | PI04104 | Verified | 1ACTSC0281, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04105 | Verified | 1ACTSC0282, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04106 | Verified | 1ACTSC0283, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04107 | Verified | 1ACTSC0284, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04108 | Verified | 1ACTSC0329, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-05 | Mike Tabbert
CTS-01 | CTS-01 | PI04109 | Verified | 1ACTSC0336, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04110 | Verified | 1ACTSC0346, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CTS-01 | CTS-01 | PI04111 | Verified | 1ACTSC0352, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04112 | Verified | 1ACTS-CHC00GH001-DS120-C0001, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04113 | Verified | 1ACTSK0024, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04114 | Verified | 1ACTSK0038, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04115 | Verified | 1ACTSK0040, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04116 | Verified | 1ACTSK0054, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04117 | Verified | 1ACTSK0056, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04118 | Verified | 1ACTSK0057, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04119 | Verified | 1ACTSK0068, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04120 | Verified | 1ACTSK0072, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04121 | Verified | 1ACTSK0095, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CTS-01 | CTS-01 | PI04122 | Verified | 1ACTSK0096, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CTS-01 | CTS-01 | PI04123 | Verified | 1ACTSK0097, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-01 | CTS-01 | PI04124 | Verified | 1ACTSK0098, To Termination | B | E | Chris Colvin | McD | 2019-08-14 | Chris Colvin | Const |  |  | 2020-01-06 | Mike Tabbert
CTS-01 | CTS-01 | PI04125 | Verified | 1ACTS-MBY01GH013-DC001-K0006, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04126 | Verified | 1ACTS-MKA01CY501-AS001-X0001, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04127 | Verified | 1ACTS-MKA01CY502-AS001-X0001, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04128 | Verified | 1ACTS-MKA01CY503-AS001-X0001, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04129 | Verified | 1ACTS-MKA01CY504-AS001-X0001, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04130 | Verified | 1ACTS-MKC01CY501-AS001-X0001, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04131 | Verified | 1ACTS-MKC01CY502-AS001-X0001, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04132 | Verified | 1ACTSX0001, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04133 | Verified | 1ACTSX0104, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04134 | Verified | 1ACTSX0105, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04135 | Verified | 1ACTSX0106, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04136 | Verified | 1ACTSX0107, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04137 | Verified | 1ACTSX0108, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04138 | Verified | 1ACTSX0109, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04139 | Verified | 1ACTSX0110, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04140 | Verified | 1ACTSX0111, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04141 | Verified | 1ACTSX0112, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04142 | Verified | 1ACTSX0113, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04143 | Verified | 1ACTSX0114, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04144 | Verified | 1ACTSX0115, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-26 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04145 | Verified | 1ACTSX0116, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04146 | Verified | 1ACTSX0118, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04147 | Verified | 1ACTSX0157, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04148 | Verified | 1ACTSX0160, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04149 | Verified | 1ACTSX0162, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04150 | Verified | 1ACTSX0164, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Ayda Chaves
CTS-01 | CTS-01 | PI04151 | Verified | 1ACTSX0166, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04152 | Verified | 1ACTSX0168, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04153 | Verified | 1ACTSX0180, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04154 | Verified | 1ACTSX0182, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04155 | Verified | 1ACTSX0184, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04156 | Verified | 1ACTSX0185, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04157 | Verified | 1ACTSX0186, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04158 | Verified | 1ACTSX0187, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04159 | Verified | 1ACTSX0188, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04160 | Verified | 1ACTSX0190, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04161 | Verified | 1ACTSX0194, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-01 | CTS-01 | PI04162 | Verified | 1ACTSX0198, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04163 | Verified | 1ACTSX0201, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04164 | Verified | 1ACTSX0203, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04165 | Verified | 1ACTSX0206, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04166 | Verified | 1ACTSX0207, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-01 | CTS-01 | PI04167 | Verified | 1ACTSX0208, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-01 | CTS-01 | PI04168 | Verified | 1ACTSX0209, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-01 | CTS-01 | PI04169 | Verified | 1ACTSX0210, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04170 | Verified | 1ACTSX0211, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-01 | CTS-01 | PI04171 | Verified | 1ACTSX0219, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04172 | Verified | 1ACTSX0244, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04173 | Verified | 1ACTSX0246, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04174 | Verified | 1ACTSX0251, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04175 | Verified | 1ACTSX0252, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04176 | Verified | 1ACTSX0253, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04177 | Verified | 1ACTSX0254, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04178 | Verified | 1ACTSX0255, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04179 | Verified | 1ACTSX0256, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04180 | Verified | 1ACTSX0257, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04181 | Verified | 1ACTSX0258, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04182 | Verified | 1ACTSX0260, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04183 | Verified | 1ACTSX0261, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04184 | Verified | 1ACTSX0262, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04185 | Verified | 1ACTSX0263, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04186 | Verified | 1ACTSX0264, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04187 | Verified | 1ACTSX0265, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04188 | Verified | 1ACTSX0266, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04189 | Verified | 1ACTSX0267, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04190 | Verified | 1ACTSX0269, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04191 | Verified | 1ACTSX0270, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04192 | Verified | 1ACTSX0271, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04193 | Verified | 1ACTSX0272, To Termination | B | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI04194 | Verified | 1ACTSX0274, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04195 | Verified | 1ACTSX0275, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04196 | Verified | 1ACTSX0276, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04197 | Verified | 1ACTSX0281, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04198 | Verified | 1ACTSX0283, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04199 | Verified | 1ACTSX0284, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04200 | Verified | 1ACTSX0287, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04201 | Verified | 1ACTSX0315, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04202 | Verified | 1ACTSX0316, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04203 | Verified | 1ACTSX0320, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04204 | Verified | 1ACTSX0322, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04205 | Verified | 1ACTSX0326, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04206 | Verified | 1ACTSX0329, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04207 | Verified | 1ACTSX0330, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04208 | Verified | 1ACTSX0334, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04209 | Verified | 1ACTSX0335, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04210 | Verified | 1ACTSX0355, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04211 | Verified | 1ACTSX0356, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04212 | Verified | 1ACTSX0357, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CTS-01 | CTS-01 | PI04213 | Verified | 1ACTSX0359, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04214 | Verified | 1ACTSX0360, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04215 | Verified | 1ACTSX0361, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04216 | Verified | 1ACTSX0362, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04217 | Verified | 1ACTSX0363, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-01 | CTS-01 | PI04218 | Verified | 1ACTSX0364, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04219 | Verified | 1ACTSX0367, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04220 | Verified | 1ACTSX0368, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04221 | Verified | 1ACTSX0369, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04222 | Verified | 1ACTSX0370, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04223 | Verified | 1ACTSX0375, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04224 | Verified | 1ACTSX0376, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04234 | Verified | 1ACTSX0408, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04235 | Verified | 1ACTSX0411, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04236 | Verified | 1ACTSX0412, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04237 | Verified | 1ACTSX0416, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
CTS-01 | CTS-01 | PI04238 | Verified | 1ACTSX0421, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-01 | CTS-01 | PI04239 | Verified | 1ACTSX0425, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-01 | CTS-01 | PI04242 | Verified | 1ACTSX0440, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-24 | Mike Tabbert
CTS-01 | CTS-01 | PI04375 | Verified | Complete the coupling thrust probe installation per G1-C7707. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-29 | Gonzalo Pena | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04376 | Verified | Complete the coupling cover hardware installation per LC-01583. | A | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-08-23 | Shane Crowe | 2019-08-28 | Brian Ballard
CTS-01 | CTS-01 | PI04378 | Verified | Complete the No2 bearing seal air blow per LC-01644. Restore system with new gaskets and bend lock washers. | B | M | Dillion Starkey | McD | 2019-08-21 | Dillion Starkey | Comm |  |  | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04386 | Verified | Complete the coupling speed probe installation | B | I | Brian Ballard | MHI | 2019-08-21 | Brian Ballard | Const |  |  | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04387 | Verified | Install cap for un used air inlet pressure piping port | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-08-28 | Brian Ballard
CTS-01 | CTS-01 | PI04388 | Verified | Remove gasket for the filter bleed pipe connection to case and assemble per LC-01607-23AOG-10 per detail GT connection. Silkolene 762 should be applied as shown in detail. MHPS TFA to witness this activity. Torque and bend lock washers when complete. | A | P | Terry Deaton | McD | 2019-08-21 | Terry Deaton | Const | 2019-08-23 | Terry Deaton | 2019-08-28 | Brian Ballard
CTS-01 | CTS-01 | PI04389 | Verified | Torque and tie-wire the UV detector hardware to 116 Ft-Lbs. | A | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-11-04 | Joshua Sturgeon | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04390 | Verified | Torque and bend lock washers for all LP, MP, HP bleed air pipe . Except for the HP bleed air pipe connection to the GT case. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-04 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04392 | Verified | Terminate and install the casing metal thermocouple installation per LC-01818-G1-C0694. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04395 | Verified | Secure the No1 bearing area access ladder | B | M | Ron McMurtry | MHI | 2019-08-21 | Ron McMurtry | Const | 2020-02-07 | Bobby Williams | 2020-03-03 | Michael Law
CTS-01 | CTS-01 | PI04396 | Verified | Complete pipe tie-wire | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-05 | Damon Turner | 2020-01-15 | Ron McMurtry
CTS-01 | CTS-01 | PI04397 | Verified | Restore cover plate. | B | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-12-24 | Shane Crowe | 2020-01-15 | Ron McMurtry
CTS-01 | CTS-01 | PI04398 | Verified | Complete the BSI of the LP, MP, HP compressor blade rings. | B | P | Lonnie Peters | McD | 2019-08-21 | Lonnie Peters | Const | 2019-12-07 | Jack White | 2020-01-15 | Ron McMurtry
CTS-01 | CTS-01 | PI04399 | Verified | Install missing bolt for the platform support. | A | P | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04400 | Verified | Remove excess enclosure gasket material. | A | P | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-09-04 | Tim Gallegos | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04401 | Verified | Finish platform safety gate part number LC-01591-GB00392309-DOOR/1. Install per drawing LC-01591-GB00392309. | A | P | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-09-11 | Tim Gallegos | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04402 | Verified | Repair the EE-00 connection to the FWD exhaust manifold tie-wire. | A | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-08-23 | Shane Crowe | 2019-08-28 | Brian Ballard
CTS-01 | CTS-01 | PI04404 | Verified | Complete the GT case insulation. | B | Q | Sheri Fritz | PCI | 2019-08-21 | Sheri Fritz | Const | 2020-02-18 | Michael Law | 2020-03-03 | John Watts
CTS-01 | CTS-01 | PI04433 | Verified | Tighten all thermocouple unions & add tie wires. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04434 | Verified | Remove spring support stops and set to cold position. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-08-28 | Terry Deaton | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04435 | Verified | Install missing hardware for the 2C external piping per LC-01633-23BOB-9, items B11/12 are required.. | A | P | Terry Deaton | McD | 2019-08-21 | Terry Deaton | Const | 2019-08-26 | Terry Deaton | 2019-08-28 | Brian Ballard
CTS-01 | CTS-01 | PI04436 | Verified | Complete pressure test for the TCA piping and install spool per LC-01620-23BOD-5. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-13 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04437 | Verified | Complete pressure test and restore flange per LC-01620-23BOE-2, items Gb, B10/11/12 are required. Torque and bend lockwashers when complete. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-13 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04438 | Verified | Complete torque and bend lock washers for all external pipe flanges. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-26 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04439 | Verified | Release purge on the TCA cooler feed water cooling tubes and complete the feed water supply pipe installation. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-10-02 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04440 | Verified | Open TCA cooler and remove shipping hardware per LC-01582 page 27. Perform inspection after removal of shipping hardware. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-09 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04441 | Verified | "Replace shipping gaskets for the TCA cooler manway door and ventilation hole flange and restore with permanent gaskets per LC-01582 page 34, items 1 and 2 are required." | B | P | Lonnie Peters | McD | 2019-08-21 | Lonnie Peters | Const | 2019-12-07 | Jack White | 2020-01-15 | Ron McMurtry
CTS-01 | CTS-01 | PI04442 | Verified | Replace missing bolts for flange LC-01620-23BOE-10, items B9/10/11 are required. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-08-28 | Terry Deaton | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04443 | Verified | Install missing lock washers, torque and bend washers for flanges LC-01620-23BOD- 09/11, items G6, B7/8/9 are required.. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04446 | Verified | Remove GT enclosure excess gasket material and caulk seams. | B | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const |  |  | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04447 | Verified | Complete the GT enclosure closing plate installation. | B | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04474 | Verified | Confirm / adjust the EB-01 center guide clearance to 1mm – 2.5mm and complete welding of the baseplates per LC-01577-G1-92156 . | A | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-08-28 | Joshua Sturgeon | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04475 | Verified | Remove debris inside the EE-01 debris screen. | A | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-08-23 | Shane Crowe | 2019-08-28 | Brian Ballard
CTS-01 | CTS-01 | PI04476 | Verified | Complete the exhaust T/C installation per LC-01577-LD-01031 I Detail d and g. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04477 | Verified | Complete the GT exhaust nozzles per LC-01577 – LD-01031 Detail a, b, c, e, f. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-11-04 | Kelvin Cook | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04478 | Verified | Clean and close the exhaust section. | A | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-10-28 | Joshua Sturgeon | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04479 | Verified | Complete the exhaust duct sound proofing wall per LC-01593 | B | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-12-11 | Tim Gallegos | 2020-01-15 | Ron McMurtry
CTS-01 | CTS-01 | PI04480 | Verified | Complete grout for the FGPA skid. | B | C | Johnny Campbell | McD | 2019-08-21 | Johnny Campbell | Const |  |  | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04482 | Verified | Complete the FGPA skid penetration plates per LC-01581 pages 32-40. | B | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04483 | Verified | Reposition the purge air shut off valve solenoid away from the purge air supply pipe. This pipe requires insulation. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04485 | Verified | Remove plastic debris from inside the PA unit. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-08-26 | Terry Deaton | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04486 | Verified | Caulk the FGPA skid per LC-01581 – Page 25. | B | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-10-10 | Tim Gallegos | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04487 | Verified | Tighten the fuel gas supply thermocouples unions inside the FG unit and complete tie-wire. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04488 | Verified | Install cap for the instrument air manifold inside the PA unit. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-23 | Gonzalo Pena | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04490 | Verified | Install the TD sound proof cover per LC-01579-G1-B6125, items 91, 92, 93, 94. | B | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-11-22 | Shane Crowe | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04492 | Verified | Install the TD enclosure penetration plates. | B | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-11-04 | Joshua Sturgeon | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04494 | Verified | Install nut for the TD dowel pins. | A | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-08-29 | Shane Crowe | 2019-10-24 | Brian Ballard
CTS-01 | CTS-01 | PI04495 | Verified | Restore the TD enclosure after the generator bearing oil seal restoration is complete. | B | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-11-04 | Joshua Sturgeon | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04496 | Verified | Clean the TD pipe trench and install covers per LF-00305-G1-Q9492 item 3 and LF-00305-G2-61338, items 1 and 2. | B | M | Carlos Wallen | McD | 2019-08-21 | Carlos Wallen | Const | 2019-11-11 | Shane Crowe | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04497 | Verified | Seal area between TD enclosure wall and pipe trench cover plate with plate and gasket. | B | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-11-04 | Joshua Sturgeon | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI04515 | Verified | 1AMBL01CP104, 105 - replace plastic plugs with SS plugs. | B | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-23 | Albert Burge
CTS-01 | CTS-01 | PI02804 | Verified | Install GT Package Heaters (2). | B | M | Shane Crowe | McD | 2019-07-26 | Shane Crowe | Const | 2019-10-17 | Shane Crowe | 2019-10-17 | Joshua Sturgeon
CTS-01 | CTS-01 | PI04666 | Verified | Perform clean & close on the TCA Cooler. | A | M | Shane Crowe | McD | 2019-08-29 | Shane Crowe | Const | 2019-08-30 | Joshua Sturgeon | 2019-08-30 | Joshua Sturgeon
CTS-01 | CTS-01 | PI04723 | Verified | MBA11AN101M01, GT Package Ventilation Fan (A), Install conduit , seatight and grounding for motor feed | A | E | Dustin Futrell | McD | 2019-09-03 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-09-18 | Mike Tabbert
CTS-01 | CTS-01 | PI04724 | Verified | MBA11AN102M01, GT Package Ventilation Fan (B), Install conduit , seatight and grounding for motor feed | A | E | Dustin Futrell | McD | 2019-09-03 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-09-18 | Mike Tabbert
CTS-01 | CTS-01 | PI04725 | Verified | MBA11AN103M01, GT Package Ventilation Fan (C), Install conduit , seatight and grounding for motor feed | A | E | Dustin Futrell | McD | 2019-09-03 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-09-18 | Mike Tabbert
CTS-01 | CTS-01 | PI04726 | Verified | MBY91GZ012, Gas Detector Panel For GT Package, Install Panel, Install tubing. (MBA11CQ001, 002 and 003) | A | I | Gonzalo Pena | McD | 2019-09-03 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-09-28 | Mike Tabbert
CTS-01 | CTS-01 | PI04727 | Verified | MBY91GZ012, Gas Detector Panel For GT Package, install conduit , sealtight and grounding for siginal cable. (MBA11CQ001, 002 and 003) | A | E | Dustin Futrell | McD | 2019-09-03 | Dustin Futrell | Const | 2019-09-13 | Richard Cruz | 2019-09-18 | Mike Tabbert
CTS-01 | CTS-01 | PI04728 | Verified | MBY91GZ013, Instrument Panel Exhaust Gas Duct Pressure, Install Panel, Install tubing. (MBR01CP102, 103 and 104) | A | I | Gonzalo Pena | McD | 2019-09-03 | Gonzalo Pena | Const | 2019-09-13 | Gonzalo Pena | 2019-09-18 | Mike Tabbert
CTS-01 | CTS-01 | PI04729 | Verified | MBY91GZ013, Instrument Panel Exhaust GasDuct Pressure, install conduit, sealtight and grounding for siginal cable.(MBR01CP102, 103 and 104) | A | E | Dustin Futrell | McD | 2019-09-03 | Dustin Futrell | Const | 2019-09-13 | Richard Cruz | 2019-09-18 | Mike Tabbert
CTS-01 | CTS-01 | PI04730 | Verified | MBY91GZ011, Instrument Panel GT Package Ventilation Fan Diff. Pressure, Install Panel, Install tubing. (MBA11CP501, 502 and 503) | A | I | Gonzalo Pena | McD | 2019-09-03 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-10-05 | Mike Tabbert
CTS-01 | CTS-01 | PI04731 | Verified | MBY91GZ011, Instrument Panel GT Package Ventilation Fan Diff. Pressure, install conduit, sealtight and grounding for siginal cable. (MBA11CP501, 502 and 503) | A | E | Dustin Futrell | McD | 2019-09-03 | Dustin Futrell | Const | 2019-09-13 | Richard Cruz | 2019-09-18 | Mike Tabbert
CTS-01 | CTS-01 | PI04732 | Verified | MBY91GZ014, Gas Detector Panel For GT Exhaust Gas Duct, Install Panel, Install tubing. | A | I | Gonzalo Pena | McD | 2019-09-03 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-18 | Mike Tabbert
CTS-01 | CTS-01 | PI04733 | Verified | MBY91GZ014, Gas Detector Panel For GT Exhaust Gas Duct, Install Conduit, Install sealtight and grounding for siginal cable. | A | E | Dustin Futrell | McD | 2019-09-03 | Dustin Futrell | Const | 2019-09-13 | Richard Cruz | 2019-09-18 | Mike Tabbert
CTS-01 | CTS-01 | PI04734 | Verified | MBY91GZ016 Panel, MBA11CQ004, Gas Detector for Fuel Gas Unit, Install tubing. | A | I | Gonzalo Pena | McD | 2019-09-03 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-18 | Mike Tabbert
CTS-01 | CTS-01 | PI04735 | Verified | MBY91GZ016 Panel, MBA11CQ004, Gas Detector for Fuel Gas Unit, Install conduit, install sealtight and grounding for siginal cable. | A | E | Dustin Futrell | McD | 2019-09-03 | Dustin Futrell | Const | 2019-09-13 | Richard Cruz | 2019-09-18 | Mike Tabbert
CTS-01 | CTS-01 | PI09314 | Verified | 1A-LM-01365-50 - FW1 & FW3 Needs Repair. | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const |  |  | 2019-10-29 | Tom Noble
CTS-01 | CTS-01 | PI09315 | Verified | 1A-LM-01364-49 - FW3 Needs Repair. | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const |  |  | 2019-10-17 | Tom Noble
CTS-01 | CTS-01 | PI09786 | Verified | Test Package CTS-T-1A-AF08 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-01 | Kelvin Cook
CTS-01 | CTS-01 | PI03258 | Verified | LM-1384 - Restore system, torque flanges after air blow | B | P | Lonnie Peters | McD | 2019-08-07 | Lonnie Peters | Const |  |  | 2019-12-04 | Kelvin Cook
CTS-01 | CTS-01 | PI12632 | Verified | Remove unused conduit - north GT enclosure | B | E | Dustin Futrell | McD | 2019-10-31 | Dustin Futrell | Const | 2019-11-05 | Richard Cruz | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI12633 | Verified | Correct tubing slope, FGAP sensor | A | I | Gonzalo Pena | McD | 2019-10-31 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2020-01-29 | Fred Michael
CTS-01 | CTS-01 | PI12634 | Verified | MBY91GZ006 instrument stand missing anchor bolts | B | I | Gonzalo Pena | McD | 2019-10-31 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI12635 | Verified | Replace broken flex, bearing 1 vibration sensor conduit | A | E | Dustin Futrell | McD | 2019-10-31 | Dustin Futrell | Const | 2019-11-05 | Richard Cruz | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI12636 | Verified | Attach ground exhaust support - north GT enclosure | A | E | Dustin Futrell | McD | 2019-10-31 | Dustin Futrell | Const | 2019-11-04 | Brad Stanford | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI12637 | Verified | Replace missing conduit covers and gaskets | A | E | Dustin Futrell | McD | 2019-10-31 | Dustin Futrell | Const | 2019-11-07 | Richard Cruz | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI12638 | Verified | Verify disc cavity TE's are safety wired | A | I | Gonzalo Pena | McD | 2019-10-31 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2020-01-15 | Richard Cummings
CTS-01 | CTS-01 | PI12639 | Verified | Install kick plates around conduit penetrations through grating | B | S | Bobby Williams | McD | 2019-10-31 | Bobby Williams | Const | 2020-03-04 | Bobby Williams | 2020-03-04 | Nelson Eichelberger
CTS-01 | CTS-01 | PI12640 | Verified | Install kick plates around instrument tubing penetrations through grating | B | S | Bobby Williams | McD | 2019-10-31 | Bobby Williams | Const | 2020-03-04 | Bobby Williams | 2020-03-04 | Nelson Eichelberger
CTS-01 | CTS-01 | PI12641 | Verified | MBY91GZ001 Install additional support | A | I | Gonzalo Pena | McD | 2019-10-31 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2020-01-29 | Fred Michael
CTS-01 | CTS-01 | PI12642 | Verified | Ground flex at MBA01CY003 | A | E | Dustin Futrell | McD | 2019-10-31 | Dustin Futrell | Const | 2019-11-05 | Richard Cruz | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI12643 | Verified | Replace broken flex at MBA01CT008 | A | E | Dustin Futrell | McD | 2019-10-31 | Dustin Futrell | Const | 2019-11-05 | Richard Cruz | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI12644 | Verified | Support flex at MBA01CT004, MBA01CT006, MBA01CT008 | A | E | Dustin Futrell | McD | 2019-10-31 | Dustin Futrell | Const | 2019-11-07 | Richard Cruz | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI12645 | Verified | Clean and remove rust from enclosures at GT and FGPA | B | E | Chris Colvin | McD | 2019-10-31 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2020-01-29 | Fred Michael
CTS-01 | CTS-01 | PI12646 | Verified | Ground GT enclosure exhaust fan skids | A | E | Dustin Futrell | McD | 2019-10-31 | Dustin Futrell | Const | 2019-11-05 | Richard Cruz | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI12647 | Verified | Replace missing Panduit cover inside MBY92GH004 | A | E | Dustin Futrell | McD | 2019-10-31 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI12648 | Verified | Replace missing conduit covers and gaskets at exhaust TE's | A | E | Dustin Futrell | McD | 2019-10-31 | Dustin Futrell | Const | 2019-11-06 | Richard Cruz | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI12649 | Verified | Grease threads and install covers on exhaust TE's | A | E | Dustin Futrell | McD | 2019-10-31 | Dustin Futrell | Const | 2019-11-06 | Richard Cruz | 2019-12-01 | Fred Michael
CTS-01 | CTS-01 | PI12650 | Verified | Torque and safety wire exhaust TE's | A | I | Gonzalo Pena | McD | 2019-10-31 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2020-01-15 | Richard Cummings
CTS-01 | CTS-01 | PI12747 | Verified | Replace Key Phasor Probe. | B | I | Brian Ballard | MHI | 2019-11-05 | Brian Ballard | Const |  |  | 2019-11-24 | Brian Ballard
CTS-01 | CTS-01 | PI14399 | Verified | Install performance test equipment | B | M | James Strange | MHI | 2019-12-06 | James Strange | Const |  |  | 2020-02-18 | Michael Law
CTS-01 | CTS-01 | PI14400 | Verified | Inspect Inlet (filters to inlet scroll) | B | M | James Strange | MHI | 2019-12-06 | James Strange | Const |  |  | 2020-02-07 | James Strange
CTS-01 | CTS-01 | PI14401 | Verified | Inspect exhaust | B | M | James Strange | MHI | 2019-12-06 | James Strange | Const |  |  | 2020-02-07 | James Strange
CTS-01 | CTS-01 | PI14402 | Verified | Re-tourque exhaust expansion joint bolts | B | M | Shane Crowe | McD | 2019-12-06 | Shane Crowe | Const | 2020-02-10 | Shane Crowe | 2020-03-03 | Michael Law
CTS-01 | CTS-01 | PI14403 | Verified | Inspect fuel gas inlet filter | B | M | James Strange | MHI | 2019-12-06 | James Strange | Const |  |  | 2020-02-07 | James Strange
CTS-01 | CTS-01 | PI14404 | Verified | Inspect temporary fuel gas strainers | B | M | James Strange | MHI | 2019-12-06 | James Strange | Const |  |  | 2020-02-07 | James Strange
CTS-01 | CTS-01 | PI14405 | Verified | Complete TCA piping modification | B | M | James Strange | MHI | 2019-12-06 | James Strange | Const |  |  | 2020-02-18 | Michael Law
CTS-01 | CTS-01 | PI15564 | Verified | 1A Generator Neutral Grounding for CTG - The bottom conduit cover bolting is all loose, and the cover has an approximate 1/2-inch gap that is allowing water intrusion. This needs to be addressed as soon as possible. | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17067 | Verified | Seal unused conduit penetrations inside 1AMBY92GH001; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deakd | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17068 | Verified | Heat shrink wire tags inside 1AMBY92GH001; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17069 | Verified | Insulate shields inside 1AMBY92GH001; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | B | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2020-04-07 | Randy Carpenter
CTS-01 | CTS-01 | PI17070 | Verified | Heat shrink wire tags inside 1AMBY92GH002; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17071 | Verified | Cables not terminated inside 1AMBY92GH002; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | B | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2020-04-07 | Randy Carpenter
CTS-01 | CTS-01 | PI17072 | Verified | Insulate shields inside 1AMBY92GH002; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | B | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2020-04-07 | Randy Carpenter
CTS-01 | CTS-01 | PI17073 | Verified | Terminal block numbers missing inside 1AMBY92GH002; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17074 | Verified | Missing cable at TB 2 terminations 1,2,3 inside 1AMBY92GH002; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | B | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17075 | Verified | Replace conduit covers inside 1AMBY92GH003; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17076 | Verified | Seal unused conduit penetrations inside 1AMBY92GH003; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17077 | Verified | Insulate shields inside 1AMBY92GH003; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | B | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm |  |  | 2020-03-04 | Nelson Eichelberger
CTS-01 | CTS-01 | PI17078 | Verified | Shields not terminated inside 1AMBY92GH004; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | B | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17079 | Verified | Seal unused conduit penetrations inside 1AMBY92GH004; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17080 | Verified | Heat shrink tags inside 1AMBY92GH004; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17081 | Verified | Clean up inside 1AMBY92GH005; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | C | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17082 | Verified | Seal unused conduit penetrations inside 1AMBY92GH005; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17083 | Verified | Ground conduit hubs inside 1AMBY92GH005; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | B | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17084 | Verified | Install conduit covers inside 1AMBY92GH005; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17085 | Verified | Clean out inside 1AMBY92GH006; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17086 | Verified | Cables not terminated inside 1AMBY92GH006; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | B | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17087 | Verified | Wires not terminated inside 1AMBY92GH006; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | B | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17088 | Verified | Seal unused conduit penetrations inside 1AMBY92GH006; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17089 | Verified | Run jumper from ground bar to back of panel ground connector inside 1AMBY92GH006; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | B | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17090 | Verified | Ground conduit hubs inside 1AMBY92GH007; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | B | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI12854 | Verified | Install one-pulse probe. | A | I | Richard Cummings | MHI | 2019-11-08 | Richard Cummings | Const |  |  | 2019-11-12 | Michael Law
CTS-01 | CTS-01 | PI12853 | Verified | Perform clean and close on the gas turbine enclosure. | B | P | Kelvin Cook | McD | 2019-11-08 | Kelvin Cook | Const |  |  | 2020-01-09 | Michael Law
CTS-01 | CTS-01 | PI17091 | Verified | Heat shrink tags inside 1AMBY92GH007; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17092 | Verified | Install conduit covers inside 1AMBY92GH007; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17093 | Verified | Cables not terminated inside 1AMBY92GH007; GT A Exterior Electrical Cabinet, East side of GT A Enclosure, upper deck | B | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17094 | Verified | Check all battery powered interior lighting, one panel has top Red LED Danger light illuminated, East wall, upper deck | C | E | Mike Tabbert | MHI | 2020-02-19 | Mike Tabbert | Comm | 2020-05-26 | Mike Tabbert | 2021-05-07 | John Watts
CTS-01 | CTS-01 | PI17095 | Verified | Seal piping penetrations above enclosure door, insulation fiber material exposed, West side upper deck | C | C | Tim Gallegos | McD | 2020-02-19 | Tim Gallegos | Comm | 2020-05-11 | Tim Gallegos | 2020-06-08 | John Watts
CTS-01 | CTS-01 | PI17096 | Verified | Trim excessive GT insulation wiring, midway of upper deck, East side | C | C | Tim Gallegos | McD | 2020-02-19 | Tim Gallegos | Comm | 2020-04-02 | Michael Law | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17097 | Verified | Flex ground disconnected at Pull Box, East side upper deck | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2020-08-12 | Nelson Eichelberger
CTS-01 | CTS-01 | PI17098 | Verified | Clean up all levels of GT A enclosure | C | C | Alan Huntsman | McD | 2020-02-19 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17099 | Verified | Oil leaking out of seam of GT A Inlet Air Duct, South end of GT | B | P | Lonnie Peters | MHI | 2020-02-19 | Lonnie Peters | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-01 | CTS-01 | PI17100 | Verified | Oil seeping out of concrete at South wall of GT A enclosure, bearing #1 area | B | P | Lonnie Peters | McD | 2020-02-19 | Lonnie Peters | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-01 | CTS-01 | PI17101 | Verified | Pour conduit seals located behind 1AMBH02AA701KD01; Bleed Valve skid, GT A enclosure, ground floor Southeast corner | B | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-03-11 | John Watts
CTS-01 | CTS-01 | PI17102 | Open | Finish installing insulation at 1AMBH02AA701KD01; Bleed Valve skid, GT A enclosure, ground floor Southeast corner | C | Q | Richard McSpadden | PCI | 2020-02-19 | Richard McSpadden | Comm
CTS-01 | CTS-01 | PI17103 | Verified | 1AMB101AA810; Drain Valve is not installed, need plug at 1AMBY91GZ004 Transmitter Rak, Southeast corner, upper deck, GT A enclosure | C | I | Gonzalo Pena | McD | 2020-02-19 | Gonzalo Pena | Comm | 2020-03-04 | Tim Green | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17104 | Verified | Tighten U-bolt nuts at 2" Compressor Blade Washing Piping, Southeast corner of GT enclosure, 1st horizontal support below penetration | C | P | James Beech | McD | 2020-02-19 | James Beech | Comm | 2020-05-27 | James Beech | 2021-05-27 | John Watts
CTS-01 | CTS-01 | PI17105 | Verified | Remove scaffolding from upper West side of GT enclosure | C | C | Alan Huntsman | McD | 2020-02-19 | Alan Huntsman | Comm | 2020-03-18 | Johnny Campbell | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17106 | Verified | Instrument Air Pressure Regulator to Air Chamber for GT Compressor Low Pressure Bleed Valve 1AMBH01AA701KD01 is installed backwards and gauge lens broken, West side of GT A, enclosure ground floor | B | I | Gonzalo Pena | McD | 2020-02-19 | Gonzalo Pena | Comm | 2020-03-04 | Tim Green | 2020-03-11 | John Watts
CTS-01 | CTS-01 | PI17107 | Verified | Open conduit penetration through GT A enclosure needs to be sealed, just North of West door, upper level | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Bernard Stasse
CTS-01 | CTS-01 | PI17108 | Verified | Clean and paint roof of GT Fuel Gas enclosure, upper level, West side of GT A | C | X | Jerry Smith | McD | 2020-02-19 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17109 | Verified | Remove carbon contamination at 1AMBY929H034; Termination Box, upper level, West side of GT A | C | C | Alan Huntsman | McD | 2020-02-19 | Alan Huntsman | Comm | 2020-03-16 | Jerry Smith | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17110 | Verified | Wires not labeled inside 1AMBY929H034; Termination Box, upper level, West side of GT A | C | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-01 | CTS-01 | PI17111 | Verified | Two battery powered interior lights are installed upside down, inside GT A enclosure, West wall upper level | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-18 | Randy Carpenter | 2020-03-18 | Randy Carpenter
CTS-01 | CTS-01 | PI17112 | Verified | Heat shrink wire tags inside 1AMBY91GZ016; Gas Detector Panel for GT Fuel Gas Unit GT A, GT A upper level, West side | C | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2020-04-07 | Randy Carpenter
CTS-01 | CTS-01 | PI17113 | Verified | Door handle loose at 1AMBY91GZ016; Gas Detector Panel for GT Fuel Gas Unit GT A, upper level, West side | C | M | Tim Gallegos | McD | 2020-02-19 | Tim Gallegos | Comm | 2020-05-18 | Tim Gallegos | 2020-06-03 | John Watts
CTS-01 | CTS-01 | PI17114 | Verified | Plug unused conduit penetrations inside 1AMBY91GZ016; Gas Detector Panel for GT Fuel Gas Unit GT A, upper level West side | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-01 | CTS-01 | PI17115 | Verified | Ground back panel inside 1AMBY91GZ016; Gas Detector Panel for GT Fuel Gas Unit GT A, upper level West side | B | E | Jonathan Donham | McD | 2020-02-19 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17116 | Verified | Remove carbon contamination from 1AMBY92GH031; Termination Box, GT A, upper level West side | C | X | Johnny Campbell | McD | 2020-02-19 | Johnny Campbell | Comm | 2020-04-15 | Johnny Campbell | 2020-08-12 | Nelson Eichelberger
CTS-01 | CTS-01 | PI17117 | Verified | Heat shrink tags inside 1AMBY92GH031; Termination Box, GT A, upper level West side | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17118 | Verified | Remove carbon contamination from 1AMBY92GH032; Termination Box, GT A, upper level West side | C | C | Alan Huntsman | McD | 2020-02-19 | Alan Huntsman | Comm | 2020-03-16 | Jerry Smith | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17119 | Verified | Unused conduit penetration needs seal at 1AMBY92GH032; Termination Box, GT A, upper level West side | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-04-07 | Randy Carpenter
CTS-01 | CTS-01 | PI17120 | Verified | Attach loose condolet covers at 1AMBY92GH032; Termination Box, GT A, upper level West side | C | E | Chris Colvin | McD | 2020-02-19 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-01 | CTS-01 | PI17121 | Verified | Remove carbon contamination from 1AMBY92GH033; Termination Box, GT A, upper level West side | C | C | Alan Huntsman | McD | 2020-02-19 | Alan Huntsman | Comm | 2020-03-16 | Jerry Smith | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17122 | Verified | Clean up Gas Valves inside GT Fuel Gas Enslosure GT A, upper level West side | C | C | Alan Huntsman | McD | 2020-02-19 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17123 | Verified | Clean up inside GT Fuel Gas Enslosure GT A, upper level West side | C | C | Alan Huntsman | McD | 2020-02-19 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-04-03 | Bernard Stasse
CTS-01 | CTS-01 | PI17124 | Verified | Finish installing insulation inside GT Fuel Gas Enslosure GT A, upper level West side | C | Q | Josh Koerner | PCI | 2020-02-19 | Josh Koerner | Comm | 2020-06-18 | Josh Koerner | 2021-04-21 | John Watts
CTS-01 | CTS-01 | PI17361 | Verified | 1A-MBP02CP634 - 1A-GT_FG_CV Positioner filter cartridges are leaking around threads. | B | I | Lonnie Peters | McD | 2020-02-28 | Lonnie Peters | Comm | 2020-03-26 | William Mitchell | 2020-04-17 | John Watts
CTS-01 | CTS-01 | PI17674 | Verified | 1A's GT Emergency stop push button protective cover is broken. It's currently secured with a zip tie. | C | E | Mike Tabbert | McD | 2020-03-04 | Mike Tabbert | Comm | 2020-03-11 | Mike Tabbert | 2020-04-17 | John Watts
CTS-01 | CTS-01 | PI17685 | Verified | 1A GT - small bore piping and electrical conduit create triping hazard. Ground floor of turbine compartment. | D | P | Michael Law | McD | 2020-03-04 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-01-05 | Keith Pollock
CTS-01 | CTS-01 | PI17688 | Verified | 1A GT - Conduit LB covers are missing or swung out of the way. Turbine comparment. | C | E | Chris Colvin | McD | 2020-03-04 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2021-05-27 | John Watts
CTS-01 | CTS-01 | PI17693 | Verified | 1A potential oil leak at bearing inlet to intake plenum. | B | M | William Mitchell | McD | 2020-03-04 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-10 | John Watts
CTS-01 | CTS-01 | PI17696 | Verified | 1A GT - Construction debris and combustible material in compartment needs to be removed - Rejected, union was backwards - D. Goldak 7/7/20 | C | C | Johnny Campbell | McD | 2020-03-04 | Johnny Campbell | Comm | 2020-07-16 | Brooks Baker | 2021-05-27 | John Watts
CTS-01 | CTS-01 | PI17825 | Verified | 87G-1A-1 / Generator Protection Relay (DPR 1) - There's a target on this NERC relay. | C | E | Jonathan Donham | McD | 2020-03-16 | Jonathan Donham | Const | 2020-03-31 | Jonathan Donham | 2020-06-04 | Donovan Anderson
CTS-01 | CTS-01 | PI17844 | Verified | 1A GT Auxiliary Package - The Plant West 1A Auxiliary Package Door is missing a bolt on the top of the interior door latch. This causes difficulty opening the door from the inside. | C | E | Chris Colvin | McD | 2020-03-16 | Chris Colvin | Const | 2020-04-01 | Jonathan Donham | 2021-04-21 | John Watts
CTS-01 | CTS-01 | PI18113 | Verified | 1A-CTS-MBH05AT101, 1A-CTS-MBH05AC301 - The clearance between the Gas Turbine Cooling Air Filter and the TCA Cooler Feedwater inlet is small. | D | M | Michael Law | McD | 2020-03-20 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-01-05 | Keith Pollock
CTS-01 | CTS-01 | PI18121 | Verified | 1A-CTS-EKE01AA105 - This valve has no stop for its closed position. It over travels and the gear inside the gear box comes loose, making it to where the valve will not close. | C | P | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-20 | William Mitchell | 2020-07-29 | John Watts
CTS-01 | CTS-01 | PI18172 | Verified | Mitsubishi commissioning paper work to submit after tuning and final testing are complete | C | M | James Strange | MHI | 2020-03-23 | James Strange | Comm | 2020-06-23 | James Strange | 2020-06-23 | Mike Tabbert
CTS-02 | CTS-02 | PI00404 | Verified | 1AYVAC0101, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-06-07 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-02 | CTS-02 | PI04384 | Verified | Install the generator end GT enclosure wall section after the No3 bearing oil seal plate restoration is complete and seal per LC-01587-GB00350003. | B | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-11-04 | Joshua Sturgeon | 2019-11-24 | Brian Ballard
CTS-02 | CTS-02 | PI04499 | Verified | Restore cover plate for the No5 generator bearing vapor pipe penetration. | B | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-10-18 | Shane Crowe | 2019-11-24 | Brian Ballard
CTS-02 | CTS-02 | PI04500 | Verified | Install guard for the TD motor shaft. | A | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-08-23 | Shane Crowe | 2019-10-24 | Brian Ballard
CTS-02 | CTS-02 | PI04501 | Verified | Restore the TD hand turning device. | A | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-08-29 | Shane Crowe | 2019-10-24 | Brian Ballard
CTS-02 | CTS-02 | PI04502 | Verified | Complete the TD enclosure caulking per LC-01586 page 47 and 52. | B | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-24 | Brian Ballard
CTS-02 | CTS-02 | PI04503 | Verified | Install the TD enclosure ground cable. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-26 | Dustin Futrell | 2019-10-24 | Brian Ballard
CTS-02 | CTS-02 | PI04504 | Verified | Complete the TD enclosure lighting. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-10-24 | Brian Ballard
CTS-02 | CTS-02 | PI05042 | Verified | 1A-CTS-XFM-0001 - paint welds. | C | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-28 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CTS-02 | CTS-02 | PI05043 | Verified | 1A-CTS-XFM-0001 - door limit switch is broken. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-24 | Dustin Futrell | 2019-09-26 | Mike Tabbert
CTS-02 | CTS-02 | PI05044 | Verified | 1A-CTS-XFM-0001 - install cap nuts on enclosure covers. | B | E | Mike Tabbert | McD | 2019-09-12 | Mike Tabbert | Const | 2019-09-28 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-02 | CTS-02 | PI05045 | Verified | 1A-CTS-XFM-0001 - attach door ground. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-24 | Randy Carpenter
CTS-02 | CTS-02 | PI05046 | Verified | 1A-CTS-XFM-0001 - conduit support on north side not sufficient. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-24 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-02 | CTS-02 | PI05047 | Verified | 1A-CTS-XFM-0001 - seal conduits. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Richard Cruz | 2019-09-26 | Logan Holland
CTS-02 | CTS-02 | PI05048 | Verified | 1A-CTS-XFM-0001 - clean out transformer. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Richard Cruz | 2019-09-20 | Fred Michael
CTS-02 | CTS-02 | PI05049 | Verified | 1A-CTS-XFM-0001 - seal the grounding stub ups. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-02 | CTS-02 | PI05050 | Verified | 1A-CTS-XFM-0001 - drill weep holes in shroud and remove yellow tape. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-24 | Dustin Futrell | 2019-09-26 | Mike Tabbert
CTS-02 | CTS-02 | PI05051 | Verified | EXC / SFC Package - exterior outlets missing covers. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-13 | Brad Stanford | 2019-12-01 | Albert Burge
CTS-02 | CTS-02 | PI05052 | Verified | EXC / SFC Package - seal penetrations in all cubicles. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-26 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-02 | CTS-02 | PI05053 | Verified | EXC / SFC Package - general housekeeping needed in package. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-13 | Brad Stanford | 2019-12-01 | Fred Michael
CTS-02 | CTS-02 | PI05054 | Verified | EXC / SFC Package - bolt & torque braids - DC bus. Logan to notify. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-13 | Brad Stanford | 2019-12-01 | Fred Michael
CTS-02 | CTS-02 | PI05055 | Verified | EXC / SFC Package - clean out 1AMKC01GU101. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Richard Cruz | 2019-12-01 | Fred Michael
CTS-02 | CTS-02 | PI05056 | Verified | EXC / SFC Package - 1AMKC01GU101 cover plates missing screws. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
CTS-02 | CTS-02 | PI05057 | Verified | EXC / SFC Package - collector bus needs ground (under package). | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Richard Cruz | 2019-09-26 | Logan Holland
CTS-02 | CTS-02 | PI05058 | Verified | EXC / SFC Package - seal collector bus penetration (under package). | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-13 | Mike Tabbert
CTS-02 | CTS-02 | PI05059 | Verified | EXC / SFC Package - adjust collector bus rain guard (under package). | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-11-20 | Fred Michael
CTS-02 | CTS-02 | PI05061 | Verified | EXC / SFC Package - all vertical trays under package need heavy duty clamps. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-12-02 | Brad Stanford | 2019-12-12 | Fred Michael
CTS-02 | CTS-02 | PI05062 | Verified | Remove temporary supports on GT bus (under package). | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Richard Cruz | 2019-09-18 | Mike Tabbert
CTS-02 | CTS-02 | PI05063 | Verified | Turning gear enclosure - clean out enclosure. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
CTS-02 | CTS-02 | PI05064 | Verified | Turning gear enclosure - seal all penetrations. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-21 | Richard Cruz | 2019-11-24 | Brian Ballard
CTS-02 | CTS-02 | PI05065 | Verified | Turning gear enclosure - HT detector missing plug. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-12-01 | Fred Michael
CTS-02 | CTS-02 | PI05066 | Verified | Turning gear enclosure - return lines u-bolts not attached (2). | A | P | James Beech | McD | 2019-09-12 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-11-24 | Brian Ballard
CTS-02 | CTS-02 | PI05067 | Verified | Turning gear enclosure - bend tabs on lock washers. | B | P | Lonnie Peters | McD | 2019-09-12 | Lonnie Peters | Const |  |  | 2019-11-24 | Brian Ballard
CTS-02 | CTS-02 | PI05068 | Verified | Turning gear enclosure - vapor line missing lock washers. | B | P | Lonnie Peters | McD | 2019-09-12 | Lonnie Peters | Const |  |  | 2019-11-24 | Brian Ballard
CTS-02 | CTS-02 | PI05069 | Verified | Turning gear enclosure - exterior term. box 1AMBY92GH012 - box & flex need ground. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
CTS-02 | CTS-02 | PI05070 | Verified | Turning gear enclosure - exterior term. box 1AMBY92GH013 - box & flex need ground. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
CTS-02 | CTS-02 | PI05071 | Verified | Turning gear enclosure - interior east side - 2" overhead conduit missing ground lug. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Richard Cruz | 2019-09-20 | Fred Michael
CTS-02 | CTS-02 | PI05072 | Verified | Turning gear enclosure - 3-way switches need phen. Tags. | C | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-02-07 | Fred Michael
CTS-02 | CTS-02 | PI05073 | Verified | Turning gear enclosure - conduit for 3-way switch needs low point drain. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-11-20 | Fred Michael
CTS-02 | CTS-02 | PI05074 | Verified | Turning gear enclosure - 1AMBV01AA828 - remove chicago fitting & install cap. | B | P | Lonnie Peters | McD | 2019-09-12 | Lonnie Peters | Const | 2020-01-16 | Lonnie Peters | 2020-01-27 | Ron McMurtry
CTS-02 | CTS-02 | PI05075 | Verified | Turning gear enclosure - turning gear motor support missing hardware. | A | M | Shane Crowe | McD | 2019-09-12 | Shane Crowe | Const | 2019-09-17 | Shane Crowe | 2020-01-15 | Ron McMurtry
CTS-02 | CTS-02 | PI05076 | Verified | GT east side cable tray - needs ground. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-27 | Mike Tabbert
CTS-02 | CTS-02 | PI05078 | Verified | GT east side cable tray - straighten out cables & cut ty-wraps. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-02 | CTS-02 | PI05079 | Verified | NRG enclosure 1ABAW11GH001 - connect grid ground. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-27 | Mike Tabbert
CTS-02 | CTS-02 | PI05080 | Verified | NRG enclosure 1ABAW11GH001 - need edge barrier on penetration cut-out. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-27 | Mike Tabbert
CTS-02 | CTS-02 | PI05081 | Verified | NRG enclosure 1ABAW11GH001 - clean interior. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
CTS-02 | CTS-02 | PI05082 | Verified | Complete installation in the NRG enclosure 1ABAW11GH001. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-26 | Mike Tabbert | 2019-09-26 | Mike Tabbert
CTS-02 | CTS-02 | PI05083 | Verified | NRG enclosure 1ABAW11GH001 - remove power. Logan to notify. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-12-01 | Fred Michael
CTS-02 | CTS-02 | PI05084 | Verified | NRG enclosure 1ABAW11GH001 - install plates. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-27 | Mike Tabbert
CTS-02 | CTS-02 | PI05085 | Verified | NRG enclosure 1ABAW11GH001 - ground all conduit that does not have LLC clamps. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-27 | Mike Tabbert
CTS-02 | CTS-02 | PI05087 | Verified | NRG enclosure 1ABAW11GH001 - seal conduits - north side. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-02 | CTS-02 | PI05088 | Verified | NRG enclosure 1ABAW11GH001 - install plates - north side. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Richard Cruz | 2019-09-27 | Mike Tabbert
CTS-02 | CTS-02 | PI05089 | Verified | NRG enclosure 1ABAW11GH001 - anchor enclosure | A | S | Tim Gallegos | McD | 2019-09-12 | Tim Gallegos | Const | 2019-09-23 | Tim Gallegos | 2019-09-27 | Mike Tabbert
CTS-02 | CTS-02 | PI05090 | Verified | AT control oil skid - MKW01CL201 / 202 & MKG01201 / 202 need bonding jumpers. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-26 | Dustin Futrell | 2019-09-27 | Albert Burge
CTS-02 | CTS-02 | PI05091 | Verified | AT control oil skid - MKW01CL201 / 202 & MKG01201 / 202 need bonding jumpers. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Gonzalo Pena | 2019-09-27 | Albert Burge
CTS-02 | CTS-02 | PI05092 | Verified | AT control oil skid - MKW01CL201 / 202 & MKG01201 / 202 need bonding jumpers. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Gonzalo Pena | 2019-09-27 | Albert Burge
CTS-02 | CTS-02 | PI05093 | Verified | AT control oil skid - MKW01CL201 / 202 & MKG01201 / 202 need bonding jumpers. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Gonzalo Pena | 2019-09-27 | Albert Burge
CTS-02 | CTS-02 | PI05094 | Verified | Torque grounds to bus bar - north of NRG. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
CTS-02 | CTS-02 | PI05095 | Verified | Pour all seals after commissioning. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CTS-02 | CTS-02 | PI05096 | Verified | Southeast corner NRG - 3/4" conduit needs support at LB. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
CTS-02 | CTS-02 | PI05097 | Verified | Hydrogen skid - paint bare metal prior to hydrogen - do not use grinder or do any hot work to prep for paint | B | C | Jorge Alexander | McD | 2019-09-12 | Jorge Alexander | Const | 2019-12-23 | Michael Law | 2020-01-01 | Albert Burge
CTS-02 | CTS-02 | PI05098 | Verified | GT control package - General Protection Panels - clean. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-12-02 | Brad Stanford | 2019-12-13 | Mike Tabbert
CTS-02 | CTS-02 | PI05099 | Verified | GT control package - seal penetrations. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05721 | Verified | 1ACTSC0003, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05722 | Verified | 1ACTSC0004, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05723 | Verified | 1ACTSC0006, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05724 | Verified | 1ACTSC0008, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05725 | Verified | 1ACTSC0017, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05726 | Verified | 1ACTSC0187, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05727 | Verified | 1ACTSC0194, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-17 | Mike Tabbert
CTS-02 | CTS-02 | PI05728 | Verified | 1ACTSK0007, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05729 | Verified | 1ACTSK0031, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05730 | Verified | 1ACTSK0034, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05731 | Verified | 1ACTSK0049, From Termination | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-04 | Michael Law
CTS-02 | CTS-02 | PI05732 | Verified | 1ACTSK0129, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-27 | Mike Tabbert
CTS-02 | CTS-02 | PI05733 | Verified | 1ACTSK0152, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05734 | Verified | 1ACTSC0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-02 | CTS-02 | PI05735 | Verified | 1ACTSC0002, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-02 | CTS-02 | PI05736 | Verified | 1ACTSC0003, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05737 | Verified | 1ACTSC0004, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05738 | Verified | 1ACTSC0006, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05739 | Verified | 1ACTSC0014, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05740 | Verified | 1ACTSC0017, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05741 | Verified | 1ACTSC0187, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-02 | CTS-02 | PI05742 | Verified | 1ACTSC0194, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-02 | CTS-02 | PI05743 | Verified | 1ACTSC0195, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05744 | Verified | 1ACTSC0342, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05745 | Verified | 1ACTSK0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-17 | Mike Tabbert
CTS-02 | CTS-02 | PI05746 | Verified | 1ACTSK0007, To Termination | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-25 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05747 | Verified | 1ACTSK0051, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05748 | Verified | 1ACTSK0073, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05749 | Verified | 1ACTSK0087, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05750 | Verified | 1ACTSK0129, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI05751 | Verified | 1ACTSK0152, To Termination | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-12-01 | Fred Michael
CTS-02 | CTS-02 | PI05752 | Verified | 1ACTSX0418, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-02 | CTS-02 | PI12651 | Verified | Support flex on west side of the generator | A | E | Dustin Futrell | McD | 2019-10-31 | Dustin Futrell | Comm | 2019-11-21 | Richard Cruz | 2019-12-01 | Fred Michael
CTS-02 | CTS-02 | PI12652 | Verified | Install terminal box covers on east side | A | E | Chris Colvin | McD | 2019-10-31 | Chris Colvin | Comm | 2019-12-23 | Michael Law | 2020-01-14 | Jonathan Donham
CTS-02 | CTS-02 | PI12653 | Verified | Duct seal embedded conduits | A | E | Chris Colvin | McD | 2019-10-31 | Chris Colvin | Comm | 2019-12-07 | Mark Ball | 2020-01-13 | Fred Michael
CTS-02 | CTS-02 | PI12654 | Verified | Install ground at MKA01CY501, MKA01CY502 enclosure | A | E | Chris Colvin | McD | 2019-10-31 | Chris Colvin | Comm | 2019-11-21 | Richard Cruz | 2020-01-14 | Jonathan Donham
CTS-02 | CTS-02 | PI15001 | Verified | Clean up inside 1A-CTS-CHC00GH001; GT Gen Control & Protective Relay Panel, Northeast side GT A Control Package | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
CTS-02 | CTS-02 | PI15002 | Verified | Heat shrink cable/wire tags inside 1A-CTS-CHC00GH001; GT Gen Control & Protective Relay Panel, Northeast side GT A Control Package | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-07 | Shannon Scott
CTS-02 | CTS-02 | PI15003 | Verified | Replace cable tags that are too big to heat shrink inside 1A-CTS-CHC00GH001; GT Gen Control & Protective Relay Panel, Northeast side GT A Control Package | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
CTS-02 | CTS-02 | PI15004 | Verified | 1A-CTS-CHC00GH001; GT Gen Control & Protective Relay Panel needs phenolic label, Northeast side of GT Control Package A | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-14 | Mike Tabbert | 2020-01-28 | Fred Michael
CTS-02 | CTS-02 | PI15687 | Verified | SAR 03506 1B barometric pressure transmitter with water damage.. | B | I | Albert Burge | McD | 2020-01-09 | Albert Burge | Const |  |  | 2020-01-09 | Ed Gober
CTS-02 | CTS-02 | PI16195 | Verified | 1ABVR01 (GT 125V DC Starter Panel) Spare has broken on/trip/off switch. GT1A Control package | C | E | Jonathan Donham | McD | 2020-01-20 | Jonathan Donham | Comm | 2020-04-02 | Mike Tabbert | 2020-04-07 | Randy Carpenter
CTS-02 | CTS-02 | PI16465 | Verified | Need plug for bronze fitting outside of Slip Ring Enclosure at East and West side | C | P | Alan Joiner | McD | 2020-02-03 | Alan Joiner | Comm | 2020-05-26 | Alan Joiner | 2020-08-12 | Nelson Eichelberger
CTS-02 | CTS-02 | PI16466 | Verified | Clean up Generator deck on East and West side | C | C | Alan Huntsman | McD | 2020-02-03 | Alan Huntsman | Comm | 2020-02-19 | Alan Huntsman | 2020-04-06 | Bernard Stasse
CTS-02 | CTS-02 | PI16467 | Verified | Clean Generator housing | C | C | Alan Huntsman | McD | 2020-02-03 | Alan Huntsman | Comm | 2020-03-18 | Johnny Campbell | 2020-04-06 | Bernard Stasse
CTS-02 | CTS-02 | PI16468 | Verified | Are filters required for vents at East and West side of Slip Ring Enclosure? | C | C | James Strange | MHI | 2020-02-03 | James Strange | Comm | 2020-03-30 | James Strange | 2020-04-06 | Bernard Stasse
CTS-02 | CTS-02 | PI16470 | Verified | Clean up Excitation Building | C | C | Alan Huntsman | McD | 2020-02-03 | Alan Huntsman | Comm | 2020-03-18 | Johnny Campbell | 2020-04-06 | Bernard Stasse
CTS-02 | CTS-02 | PI16471 | Verified | Install metal plates stored behind Excitation cabinets | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-04-06 | Chris Colvin | 2020-04-07 | Randy Carpenter
CTS-02 | CTS-02 | PI16472 | Verified | Electrical outlet cover plates missing screws throughout Excitation Enclosure | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-02 | CTS-02 | PI16473 | Verified | HVAC vents missing screws at trim inside Excitation Enclosure | C | E | Shane Crowe | McD | 2020-02-03 | Shane Crowe | Comm | 2020-03-27 | Shane Crowe | 2020-04-06 | Bernard Stasse
CTS-02 | CTS-02 | PI16474 | Verified | Clean out trash behind Excitation cabinets | C | C | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-02 | CTS-02 | PI16475 | Verified | Doors out of alignment at AC 480V Panel Board and AC 120V Panel Board | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-04-06 | Chris Colvin | 2020-04-07 | Randy Carpenter
CTS-02 | CTS-02 | PI16476 | Verified | Floor penetration not sealed at AC 480V Panel Board and AC 120V Panel Board | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-02 | CTS-02 | PI16477 | Verified | Screw not flush at South side of AC 480V Panel Board and AC 120V Panel Board | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-04-16 | Matt Gilmore | 2021-01-05 | Keith Pollock
CTS-02 | CTS-02 | PI16478 | Verified | Fire protection cable floor penetrations not sealed at North end of Excitation Enclosure | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-08-20 | Chris Colvin | 2021-01-05 | Keith Pollock
CTS-02 | CTS-02 | PI16479 | Verified | No fire extinguisher inside Excitation Enclosure | C | E | Jerry Smith | McD | 2020-02-03 | Jerry Smith | Comm | 2020-03-09 | Jerry Smith | 2020-04-06 | Bernard Stasse
CTS-02 | CTS-02 | PI16480 | Verified | A' HVAC thermostat is not working inside Excitation Enclosure | C | E | Mike Tabbert | McD | 2020-02-03 | Mike Tabbert | Comm | 2020-02-12 | Mike Tabbert | 2020-02-15 | Shannon Scott
CTS-02 | CTS-02 | PI16481 | Verified | Touch up Excitation Panel ground cable seal under Enclosure | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-02 | CTS-02 | PI16482 | Verified | Seal open penetrations under Excitation Enclosure | B | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
CTS-02 | CTS-02 | PI16483 | Verified | Tag all components at CO2/Hydrogen Control Skid | C | P | Kelvin Cook | McD | 2020-02-03 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-06 | Bernard Stasse
CTS-02 | CTS-02 | PI16484 | Verified | Replace carbon steel flange bolts with teflon coated B7 bolts at H2 Gas Feed flange MKG01, inlet side of flange is carbon steel connected to stainless steel at Gas Control Unit | B | P | Bobby Williams | McD | 2020-02-03 | Bobby Williams | Comm | 2020-02-10 | Kelvin Cook | 2020-02-15 | Shannon Scott
CTS-02 | CTS-02 | PI16485 | Verified | Replace carbon steel flange bolts with teflon coated B7 bolts at CO2 Gas Feed flange MKG11, inlet side of flange is carbon steel connected to stainless steel at Gas Control Unit | B | P | Bobby Williams | McD | 2020-02-03 | Bobby Williams | Comm | 2020-02-10 | Kelvin Cook | 2020-02-15 | Shannon Scott
CTS-02 | CTS-02 | PI16486 | Verified | Will the lifting eyes for the Turning Gear base plate be turned over to Entergy? | C | P | Shane Crowe | McD | 2020-02-03 | Shane Crowe | Comm | 2020-03-19 | Shane Crowe | 2020-04-07 | Randy Carpenter
CTS-02 | CTS-02 | PI16487 | Verified | Do the jacking bolts at Turning Gear need to be backed off? | C | P | James Strange | McD | 2020-02-03 | James Strange | Comm | 2020-04-09 | James Strange | 2020-06-08 | John Watts
CTS-02 | CTS-02 | PI16488 | Verified | Tighten screws at Turning Gear Motor termination box | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-02 | CTS-02 | PI16489 | Verified | Loose bolts at Turning Gear Motor shroud mounting bracket | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-02 | CTS-02 | PI16490 | Verified | SFC cabinet is not sealed at North end of Excitation Enclosure | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-02 | CTS-02 | PI16491 | Verified | Verify electrical conduit seals are poured at H2 Gas Dryer cabinet, paint red if sealed | B | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
CTS-02 | CTS-02 | PI16492 | Verified | Ground disconnected at Pressure Transmitter 1AMKGO1CP101, needs ground bushing | B | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-02-27 | Chris Colvin | 2020-03-03 | John Watts
CTS-02 | CTS-02 | PI16493 | Verified | Remove tape, wire, rope, tie wraps and old tags throughout Generator H2 and CO2 Gas Control System | C | C | Alan Huntsman | McD | 2020-02-03 | Alan Huntsman | Comm | 2020-03-18 | Johnny Campbell | 2020-04-06 | Bernard Stasse
CTS-02 | CTS-02 | PI16494 | Verified | Conduit penetration cover missing screws at H2 Gas Dryer Cabinet | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-02 | CTS-02 | PI16495 | Verified | H2 Gas Dryer Cabinet bottom cover needs to be sealed | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-04-14 | Chris Colvin | 2020-06-08 | John Watts
CTS-02 | CTS-02 | PI16496 | Verified | Cover plate inside H2 Dryer Cabinet is missing screws | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-04-14 | Chris Colvin | 2020-06-08 | John Watts
CTS-02 | CTS-02 | PI17694 | Verified | 1A GT - in the turning gear comparment the shaft guard is not in place exposing generator shaft. Install shaft guard. | C | M | Shane Crowe | McD | 2020-03-04 | Shane Crowe | Comm | 2020-05-19 | Shane Crowe | 2020-12-08 | Dave Goldak
CTS-02 | CTS-02 | PI18086 | Verified | Seal oil leak on the exciter side of the generator on the flange that connects the seal oil system to the generator. This leak can be seen from in between the H2 skid and the seal oil skid. | C | M | William Mitchell | McD | 2020-03-18 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2020-04-17 | John Watts
CTS-02 | CTS-02 | PI18173 | Verified | Mitsubishi commissioning paper work to submit after tuning and final testing are complete | C | M | Lonnie Peters | McD | 2020-03-23 | Lonnie Peters | Comm | 2020-04-01 | Lonnie Peters | 2020-04-01 | Eric Policarpio
CTS-03 | CTS-03 | PI01298 | Verified | Grout in Lube Oil Enclosure | C | C | Johnny Campbell | McD | 2019-05-31 | Johnny Campbell | Const | 2019-06-24 | Johnny Campbell | 2019-06-24 | Neil Simon
CTS-03 | CTS-03 | PI01299 | Verified | Rub down sides of Lube Oil Tank Skid | C | C | Johnny Campbell | McD | 2019-05-31 | Johnny Campbell | Const | 2019-07-16 | Johnny Campbell | 2019-11-23 | Michael Law
CTS-03 | CTS-03 | PI01300 | Verified | Rub Down sides of Lube Oil Control Skid | C | C | Johnny Campbell | McD | 2019-05-31 | Johnny Campbell | Const | 2019-07-16 | Johnny Campbell | 2019-11-23 | Michael Law
CTS-03 | CTS-03 | PI01301 | Verified | Dry Pack pipe supports on West side of Lube Oil Enclosure | C | C | Johnny Campbell | McD | 2019-05-31 | Johnny Campbell | Const | 2019-09-06 | Johnny Campbell | 2019-11-23 | Michael Law
CTS-03 | CTS-03 | PI01302 | Verified | Dry Pack pipe supports at bottom of Containment Pit | C | C | Johnny Campbell | McD | 2019-05-31 | Johnny Campbell | Const | 2019-10-08 | Johnny Campbell | 2019-11-23 | Michael Law
CTS-03 | CTS-03 | PI01303 | Verified | Clean out Lube Oil Containment Pit of Mud and Debris | C | C | Johnny Campbell | McD | 2019-05-31 | Johnny Campbell | Const | 2019-11-21 | Johnny Campbell | 2019-11-23 | Michael Law
CTS-03 | CTS-03 | PI01304 | Verified | Firestop all conduit penetrations in 1A Control Package. | C | E | Chris Colvin | McD | 2019-05-31 | Chris Colvin | Const | 2020-02-02 | Mike Tabbert | 2020-02-02 | Mike Tabbert
CTS-03 | CTS-03 | PI01305 | Verified | Condulet covers missing on the east side of Seal Oil Skid near cable tray. | B | E | Luis Cantu | McD | 2019-05-31 | Luis Cantu | Const | 2019-05-31 | Shannon Savoy | 2019-06-12 | Mike Tabbert
CTS-03 | CTS-03 | PI01306 | Verified | Cable tray grounding around the Seal Oil Skid | B | E | Luis Cantu | McD | 2019-05-31 | Luis Cantu | Const | 2019-05-31 | Shannon Savoy | 2019-06-12 | Mike Tabbert
CTS-03 | CTS-03 | PI01307 | Verified | T-Cover drains missing from condulet runs on Seal Oil Skid by panel. | B | E | Shannon Savoy | McD | 2019-05-31 | Shannon Savoy | Const | 2019-05-31 | Shannon Savoy | 2019-06-06 | Shannon Scott
CTS-03 | CTS-03 | PI01308 | Verified | Tighten thermocouple on Seal Oil Skid | B | I | Gonzalo Pena | McD | 2019-05-31 | Gonzalo Pena | Const | 2019-06-25 | Gonzalo Pena | 2019-06-28 | Shannon Scott
CTS-03 | CTS-03 | PI01309 | Verified | Complete installing vendor cables and devices on north side of Seal Oil Skid | B | E | Keith Mahoney | MHI | 2019-05-31 | Keith Mahoney | Const | 2019-09-25 | Keith Mahoney | 2019-09-25 | Shannon Scott
CTS-03 | CTS-03 | PI01317 | Verified | Insulate lugs on Main Lube Oil motors | A | E | Luis Cantu | McD | 2019-05-31 | Luis Cantu | Const | 2019-05-31 | Shannon Savoy | 2019-06-13 | Mike Tabbert
CTS-03 | CTS-03 | PI01323 | Verified | MBV01BR006: Sheet 1: Install MBV01BP181 after Lube Oil Flush is completed and torque flange. | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-06 | Kelvin Cook
CTS-03 | CTS-03 | PI01324 | Verified | MBV01BR006: Sheet 1: Torque flange at connection spool 27A0A-2 to flush strainer after Lube Oil Flush is completed | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-06 | Kelvin Cook
CTS-03 | CTS-03 | PI01325 | Verified | MBV01BR006: Sheet 2: torque flange at connection flush strainer to spool 27A0A-3 after Lube Oil Flush is completed | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-06 | Kelvin Cook
CTS-03 | CTS-03 | PI01326 | Verified | MBV01BR006: Sheet 2: 27AOA-PS-09 missing ubolt | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-05 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01327 | Verified | MBV01BR006: Sheet 2: 27AOA-PS-08 missing 2 ubolt | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01328 | Verified | MBV01BR006: Sheet 2: 27AOA-4 and MBV01AA829 1" gate valve are not installed | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-11 | Terry Deaton | 2019-06-13 | Kelvin Cook
CTS-03 | CTS-03 | PI01329 | Verified | MBV01BR117 sht 1 : Torque Flange to Turbine connection after Lube Oil Flush is completed | C | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-10 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01330 | Verified | MBV01BR117 sht 1 : Torqure Flange EXJ to 27A0A after Lube Oil Flush is completed | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-06 | Kelvin Cook
CTS-03 | CTS-03 | PI01331 | Verified | MBV01BR117 sht 2 : Install MBV01BP191 Orifice Plate after Lube Oil Flush is completed | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01332 | Verified | MBV01BR117 sht 2 : Install 1/4" or 3/8" shim plate to cross brace in contact with SS Lube Oil pipe. | A | S | Robert Risher | McD | 2019-05-31 | Robert Risher | Const | 2019-06-06 | Terry Deaton | 2019-06-13 | Kelvin Cook
CTS-03 | CTS-03 | PI01333 | Verified | MBV01BR117 sht 4 : 27A0A-PS-05 has a loose u bolt | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01334 | Verified | MBV01BR117- sht 4 : Torque Flange from spool 27A0A-8 to 27A0A-9 | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01335 | Verified | MBV01BR117- sht 4 : Torque Flange from spool 27A0A-8 to 27A0A-7 | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01336 | Verified | MBV01BR117 sht 4 : 27A0A-PS-03 is missing nuts on u bolt | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01337 | Verified | MBV01BR117 sht 4 : 27A0A-PS-02 is not installed | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01338 | Verified | MBV01BR117- sht 4 : Torque Flange from spool 27A0A-7 to 27A0A-03 | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01339 | Verified | MBV01BR120 : Install MBV01BP182 Orifice Plate after Lube Oil Flushis completed and torque Flange | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01340 | Verified | MBV01BR120 : Torque flange to Turbine Bearing Supply after Lube Oil Flush is completed | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01341 | Verified | MBV02BR101 sht 1 : Torque all flanges both flanges after Lube Oil Flush is completed | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01342 | Verified | MBV02BR101 sht 2 : Install TE*MBV02CT001 after Lube Oil Flush is completed | B | I | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01343 | Verified | MBV02BR103 : Install MBV02BP191 after LO flush is complete | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01344 | Verified | MBV02BR105 sht 1: Torque flange to spool 27A0B-07 to Turbine Bearing Drain after Lube Oil Flush is completed | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01345 | Verified | MBV02BR105 sht 3 : Loose u bolt at 27A0B-PS-01 | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01346 | Verified | MBV02BR105 sht 3 : Torque flange at spool 27A0B-08 to 27B0B-01 after Lube Oil Flush is completed | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01347 | Verified | MBV02BR107 : 27A0B-PS-03 Is not installed | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01348 | Verified | MBV02BR107 : Torque flanges spool 27A0B-08 to 27A0B-10 and sppol 27A0B-10 to 27A0B-12 after Lube Oil Flush is completed | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01349 | Verified | MBV03BR103 sht 1 : Torque flanges after pressure test is completed. | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01350 | Verified | MBV03BR103 sht 1 : Cold Galvanize the support 27A0C-03 | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-13 | Kelvin Cook
CTS-03 | CTS-03 | PI01351 | Verified | MBV03BR108 : Install 27A0C-PS-1 and 27A0C-PS-2 | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-07 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01352 | Verified | MBV03BR104 : 27BOB-PS-03 fill in holes and grind smooth, Install shim 4"X4", Install ubolt | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-13 | Kelvin Cook
CTS-03 | CTS-03 | PI01353 | Verified | MBV03BR106: 27BOB-PS-02 install 4"x4" shim plate, to close gap at support, Installed ubolt | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-07 | Terry Deaton | 2019-06-13 | Kelvin Cook
CTS-03 | CTS-03 | PI01354 | Verified | MBV03BR106: Torque flange after Pressure Test | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-07 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01355 | Verified | MBV03BR162: Torque flange after Pressure Test | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-05 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01356 | Verified | MBV03BR162: 27BOB-PS-1 missing shim & ubolt | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01357 | Verified | MBV03BR162: Flange not connected to GT turning gear/Vapor Vent Port | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-05 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01358 | Verified | MBV02BR110 : Torque Flange spool 3 to EXJ after Lube Oil flush is completed | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01359 | Verified | MBV02BR110 : Torque flange spool 4 to EXJ after Lube Oil flush is completed | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const | 2019-12-14 | Kelvin Cook | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01360 | Verified | MBV02BR110 : Reinstall Expansion Joint for commissioning flush | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01361 | Verified | MBV02BR161: 27BOB-PS-10 is not installed | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01362 | Verified | MBV02BR162: sheet 1: Torque flange to GT turning Gear/Oil outlet Port B after Lube Oil Flush is completed | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01363 | Verified | MBV02BR162: sheet 1: 27BOB-PS-12 fix ubolt, fill in hole and redrill | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-14 | Terry Deaton | 2019-06-21 | Kelvin Cook
CTS-03 | CTS-03 | PI01364 | Verified | MBV02BR162: sheet 1: 27BOB-PS-13 weld support | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-06-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01365 | Verified | MBV02BR162: sheet 3: plug not installed at gate valve | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-14 | Terry Deaton | 2019-07-19 | Kelvin Cook
CTS-03 | CTS-03 | PI01366 | Verified | MBV02BR162: sheet 3: 27BOB-PS-11 u bolt has too much gap snug it down to 1/16" | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01367 | Verified | MBV02BR171: Troque Flange spool 27B0B-5 to AZ31307 O-1 | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01368 | Verified | MBV02BR172: Torque flange spool 27B0B-6 to Melco | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01369 | Verified | MBV01BR003: Torque flanges after Pressure Test 2 each | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01370 | Verified | MBV01BR003: 27BOB-PS-02 SS wrap and hose clamps are not installed | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-06-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01371 | Verified | MBV01BR004: 27BOB-PS-03 fill in holes from ubolt & SS wrap and hose clamps are not installed | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-06-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01372 | Verified | MBV01BR116: 27BOA-PS-01 SS wrap is not installed | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-06-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01373 | Verified | MBV01BR116: 27BOA-PS-01 Improper shim and Loose ubolt | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01374 | Verified | MBV01BR162 : sheet 1: 27BOA-PS-04 is not installed | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01375 | Verified | MBV01BR162 : sheet 1: Torque flange after Lube Oil flush is completed | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01376 | Verified | MBV01BR162 : sheet 2: 27BOB-PS-10 SS wrap and hose clamps are not installed | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-21 | Kelvin Cook
CTS-03 | CTS-03 | PI01377 | Verified | MBV01BR162 : sheet 2: 27BOB-PS-11 SS wrap and hose clampsares not installed & loose ubolt | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01378 | Verified | MBV01BR162 : sheet 2: plug is not installed | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01379 | Verified | MBV01BR162 : sheet 2: MBV01BP161 to be installed after Lube Oil Flush is completed and Torque Flanges | B | P | Lonnie Peters | McD | 2019-05-31 | Lonnie Peters | Const |  |  | 2019-12-14 | Kelvin Cook
CTS-03 | CTS-03 | PI01380 | Verified | MBV01BR162 : sheet 2: Valve MBV01AA828 is missing a plug | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-11 | Terry Deaton | 2019-06-13 | Kelvin Cook
CTS-03 | CTS-03 | PI01388 | Verified | Lube oil tank blind flange missing 1 bolt. | A | M | Shane Crowe | McD | 2019-05-31 | Shane Crowe | Const | 2019-06-14 | Joshua Sturgeon | 2019-07-22 | Danny Pase
CTS-03 | CTS-03 | PI01389 | Verified | Clean the Seal Oil Skid. | B | M | Shane Crowe | McD | 2019-05-31 | Shane Crowe | Const | 2019-06-14 | Joshua Sturgeon | 2019-06-14 | Joshua Sturgeon
CTS-03 | CTS-03 | PI01390 | Verified | Remove scaffold at the seal oil skid. | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-07 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-03 | CTS-03 | PI01391 | Verified | Install BOP vapor piping. | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-18 | Terry Deaton | 2019-07-19 | Kelvin Cook
CTS-03 | CTS-03 | PI01392 | Verified | Install turning gear cover. | A | M | Shane Crowe | McD | 2019-05-31 | Shane Crowe | Const | 2019-06-11 | Shane Crowe | 2019-07-19 | Kelvin Cook
CTS-03 | CTS-03 | PI01393 | Verified | Missing gasket at flange for #4 bearing at the generator deck. | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-07-22 | Danny Pase
CTS-03 | CTS-03 | PI01394 | Verified | The #4 bearing sight glass at the return line is missing piping. | A | P | James Beech | McD | 2019-05-31 | James Beech | Const | 2019-06-05 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-03 | CTS-03 | PI01395 | Verified | Need foundation for the vapor extractor motor on the generator deck | B | C | Johnny Campbell | McD | 2019-05-31 | Johnny Campbell | Const | 2019-07-22 | Johnny Campbell | 2020-01-01 | Lonnie Peters
CTS-03 | CTS-03 | PI01396 | Verified | The #3 bearing sight glass needs to be secured. | B | P | James Beech | McD | 2019-05-31 | James Beech | Const | 2019-06-05 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-03 | CTS-03 | PI01397 | Verified | Complete trough at the generator. | B | C | Johnny Campbell | McD | 2019-05-31 | Johnny Campbell | Const | 2019-06-25 | Johnny Campbell | 2019-06-25 | Kelvin Cook
CTS-03 | CTS-03 | PI01398 | Verified | The #3 bearing overflow return line is missing hardware. | A | P | James Beech | McD | 2019-05-31 | James Beech | Const | 2019-06-06 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-03 | CTS-03 | PI01399 | Verified | 1ACTSC0105, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-04 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-03 | CTS-03 | PI01400 | Verified | 1ACTSC0116, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-04 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-03 | CTS-03 | PI01401 | Verified | 1ACTSK0039, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-04 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-03 | CTS-03 | PI01403 | Verified | 1ACTSK0064, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-04 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-03 | CTS-03 | PI01404 | Verified | 1ACTSK0065, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-04 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-03 | CTS-03 | PI01405 | Verified | 1ACTSK0092, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-04 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-03 | CTS-03 | PI01406 | Verified | 1ACTSX0318, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-04 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-03 | CTS-03 | PI02767 | Verified | Install lube oil enclosure heaters (2). | C | M | Shane Crowe | McD | 2019-07-25 | Shane Crowe | Const | 2019-10-18 | Shane Crowe | 2019-10-18 | Joshua Sturgeon
CTS-03 | CTS-03 | PI02789 | Verified | Submit CCFs for 1A-CTS-MBA12AH101 & 102. | B | M | Joshua Sturgeon | McD | 2019-07-25 | Joshua Sturgeon | Const | 2019-10-18 | Joshua Sturgeon | 2019-10-18 | Ed Gober
CTS-03 | CTS-03 | PI02790 | Verified | Submit CCFs for 1A-MBV01AP401 (2 sheets). | B | M | Joshua Sturgeon | McD | 2019-07-25 | Joshua Sturgeon | Const | 2019-08-07 | Joshua Sturgeon | 2019-08-07 | Ed Gober
CTS-03 | CTS-03 | PI03417 | Verified | Install lock washers for the No. 1 bearing LO return expansion joint flanges | B | M | Dillion Starkey | McD | 2019-08-09 | Dillion Starkey | Const |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI03530 | Verified | Install permanent hardware for the No. 1 bearing drip plate drain pipe per LC-01611-27AOJ-1, items F6, G8, B9/10/11. Remove plastic | B | P | Dillion Starkey | McD | 2019-08-09 | Dillion Starkey | Const |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI03535 | Verified | Remove shipping stops from the No. 1 bearing LO supply expansion joint after restoration | B | P | Dillion Starkey | McD | 2019-08-09 | Dillion Starkey | Const |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI03546 | Verified | Install missing U-bolt for the No. 2 bearing LO return pipe. | B | P | Dillion Starkey | McD | 2019-08-09 | Dillion Starkey | Const |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI03548 | Verified | Remove the LO supply pipe air fitting and install plug. | A | P | Dillion Starkey | McD | 2019-08-09 | Dillion Starkey | Const |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI03549 | Verified | Install lock washers for the No. 2 bearing LO return pipe. | A | P | Dillion Starkey | McD | 2019-08-09 | Dillion Starkey | Const |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04379 | Verified | Install correct hardware and restore the No2 bearing LO return flange per LC-01602-27AOB-15, items G4, B5/6/7 are required. Torque and bend lock washers when complete. | B | M | Dillion Starkey | McD | 2019-08-21 | Dillion Starkey | Comm |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04380 | Verified | Install the No2 bearing LO return thermocouple and LO thrust bearing return thermocouple. | B | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-23 | Gonzalo Pena | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04381 | Verified | Install correct hardware for the No2 bearing LO supply pipe . Torque and bend lock washers. | B | M | Lonnie Peters | McD | 2019-08-21 | Lonnie Peters | Comm | 2020-01-10 | Lonnie Peters | 2020-01-15 | Ron McMurtry
CTS-03 | CTS-03 | PI04382 | Verified | Complete the generator air leakage test | A | M | Dillion Starkey | McD | 2019-08-21 | Dillion Starkey | Comm |  |  | 2019-10-05 | Mike Tabbert
CTS-03 | CTS-03 | PI04383 | Verified | Restore the No3 bearing oil seal cover plate. Complete the upper half coupling cover installation per LC-01583 | B | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-10-18 | Shane Crowe | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04385 | Verified | Install / Bend lock washers for the No2 bearing LO return and vapor pipe. | B | M | Lonnie Peters | McD | 2019-08-21 | Lonnie Peters | Comm | 2020-01-10 | Lonnie Peters | 2020-01-15 | Ron McMurtry
CTS-03 | CTS-03 | PI04393 | Verified | Install the No1 bearing vent pressure pipe support per LC-01818-G1-B9879 shown in section EE. | B | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-05 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04394 | Verified | Remove foreign material for the No1 bearing vapor pipe and torque / bend lock washers. | B | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-05 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04403 | Verified | Install lock washers for the LO trunion cooling flanges | B | M | Dillion Starkey | McD | 2019-08-21 | Dillion Starkey | Comm |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04432 | Verified | Complete welding for the LO vapor extractor pipe support . | B | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-13 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04458 | Verified | Complete the Aux enclosure penetration plates per LC-01588 page 56. | B | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const |  |  | 2019-11-24 | Brian Ballard
CTS-03 | CTS-03 | PI04459 | Verified | Complete the Aux enclosure external caulking per LC-01588 page 34 and 58. | B | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const |  |  | 2019-11-24 | Brian Ballard
CTS-03 | CTS-03 | PI04460 | Verified | Complete the Aux enclosure panel to panel earthing cable installation per LC-01588 page 59. | B | E | Chris Colvin | McD | 2019-08-21 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2020-01-15 | Ron McMurtry
CTS-03 | CTS-03 | PI04461 | Verified | Seal un-used conduit ports inside the Aux enclosure. | B | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-11 | Fred Michael | 2019-11-24 | Brian Ballard
CTS-03 | CTS-03 | PI04462 | Verified | Tie-wire all CO and EO supply flange hardware. | B | M | Lonnie Peters | McD | 2019-08-21 | Lonnie Peters | Comm | 2020-01-10 | Lonnie Peters | 2020-01-15 | Ron McMurtry
CTS-03 | CTS-03 | PI04463 | Verified | Restore the LO supply pipe U-bolt inside the Aux enclosure. | B | M | Dillion Starkey | McD | 2019-08-21 | Dillion Starkey | Comm |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04464 | Verified | Restore the LO return expansion joint cover clips. | B | M | Dillion Starkey | McD | 2019-08-21 | Dillion Starkey | Comm |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04465 | Verified | Remove construction material inside the Aux Enclosure. | B | M | Dillion Starkey | McD | 2019-08-21 | Dillion Starkey | Comm |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04467 | Verified | Remove debris on top of the CO2 FF dampers inside the Aux enclosure. | B | M | Lonnie Peters | McD | 2019-08-21 | Lonnie Peters | Comm |  |  | 2019-11-24 | Brian Ballard
CTS-03 | CTS-03 | PI04468 | Verified | Install lock washers for the LO vapor extraction pipe connection at the tank and torque. | B | M | Dillion Starkey | McD | 2019-08-21 | Dillion Starkey | Comm |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04469 | Verified | Bend all lock washers for pipe inside the Aux enclosure. | B | M | Dillion Starkey | McD | 2019-08-21 | Dillion Starkey | Comm |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04470 | Verified | Complete the instrument air supply tubing to the LO TCV. | B | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-23 | Gonzalo Pena | 2019-08-28 | Brian Ballard
CTS-03 | CTS-03 | PI04471 | Verified | Complete electrical work for the LO TCV. | B | E | Logan Holland | McD | 2019-08-21 | Logan Holland | Comm |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04472 | Verified | Install the LO return debris screen. | B | M | Lonnie Peters | McD | 2019-08-21 | Lonnie Peters | Comm | 2020-01-10 | Lonnie Peters | 2020-01-15 | Ron McMurtry
CTS-03 | CTS-03 | PI04473 | Verified | Restore leak guard for the main LO pump flange. | B | M | Dillion Starkey | McD | 2019-08-21 | Dillion Starkey | Comm |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04489 | Verified | Install lock washers for the TD vapor extraction pipe. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-08-28 | Terry Deaton | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI04491 | Verified | Restore the TD LO return pipe U-bolts. | B | M | Lonnie Peters | McD | 2019-08-21 | Lonnie Peters | Comm |  |  | 2019-11-24 | Brian Ballard
CTS-03 | CTS-03 | PI04493 | Verified | Bend / Install lock washers for the TD LO return and supply pipe . | B | M | Lonnie Peters | McD | 2019-08-21 | Lonnie Peters | Comm |  |  | 2019-11-24 | Brian Ballard
CTS-03 | CTS-03 | PI04498 | Verified | Remove air fitting and install plug for the TD LO supply line. | B | M | Dillion Starkey | McD | 2019-08-21 | Dillion Starkey | Comm |  |  | 2019-10-24 | Brian Ballard
CTS-03 | CTS-03 | PI12655 | Verified | Seal all unused conduit penetrations | A | E | Chris Colvin | McD | 2019-10-31 | Chris Colvin | Comm | 2019-11-21 | Richard Cruz | 2020-01-28 | Fred Michael
CTS-03 | CTS-03 | PI12656 | Verified | Replace missing covers and gaskets | A | E | Chris Colvin | McD | 2019-10-31 | Chris Colvin | Comm |  |  | 2020-01-13 | Fred Michael
CTS-03 | CTS-03 | PI12657 | Verified | Remove scaffold materials | B | C | Jerry Smith | McD | 2019-10-31 | Jerry Smith | Comm | 2019-11-11 | Jerry Smith | 2020-01-13 | Fred Michael
CTS-03 | CTS-03 | PI12658 | Verified | Reinstall covers on light switches | A | E | Chris Colvin | McD | 2019-10-31 | Chris Colvin | Comm | 2019-11-21 | Richard Cruz | 2020-01-13 | Fred Michael
CTS-03 | CTS-03 | PI16116 | Verified | Oil leak at flange under 1AMBV01BB203 Accumulator | B | P | William Mitchell | McD | 2020-01-16 | William Mitchell | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-03 | CTS-03 | PI16117 | Verified | SW enclosure door handle is missing nut at outside end | B | C | Bobby Williams | McD | 2020-01-16 | Bobby Williams | Comm | 2020-02-02 | Bobby Williams | 2020-02-10 | Shannon Scott
CTS-03 | CTS-03 | PI16118 | Verified | Reinstall blind atMBV01AA001 at NE end of Lube Oil Reservoir | B | P | William Mitchell | McD | 2020-01-16 | William Mitchell | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-03 | CTS-03 | PI16119 | Verified | 1AMBY02AT101; Reservoir Strainer cover is missing bolt | C | P | William Mitchell | McD | 2020-01-16 | William Mitchell | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-03 | CTS-03 | PI16120 | Verified | Remove jacking bolt from Lube Oil Reservoir bottom hold down flange, NW side of reservoir | C | P | Bobby Williams | McD | 2020-01-16 | Bobby Williams | Comm | 2020-01-21 | Charlie English | 2020-02-10 | Shannon Scott
CTS-03 | CTS-03 | PI16121 | Verified | Clean up top of Lube Oil Reservoir; remove scaffold parts, temporary lighting, wire etc. | C | C | Alan Huntsman | McD | 2020-01-16 | Alan Huntsman | Comm | 2020-03-18 | Johnny Campbell | 2020-04-06 | Bernard Stasse
CTS-03 | CTS-03 | PI16122 | Verified | MBV01AH101 and MBV01AH102; GT Lube Oil Heater A/B missing flange bolts | B | P | William Mitchell | McD | 2020-01-16 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-10 | John Watts
CTS-03 | CTS-03 | PI16123 | Verified | Repair oil leak at MBV01AA804; Site Glass, bottom isolation valve | B | M | Lonnie Peters | McD | 2020-01-16 | Lonnie Peters | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-03 | CTS-03 | PI16124 | Verified | 1" flange birdmouthed and leaking below Lube Oil return piping, inside GT A enclosure, South end middle of wall | B | P | William Mitchell | McD | 2020-01-16 | William Mitchell | Comm | 2020-03-09 | Michael Law | 2020-08-06 | Dave Goldak
CTS-03 | CTS-03 | PI16125 | Verified | 2" flange leaking below Lube Oil return piping, inside GT A enclosure, South end middle of wall | B | P | William Mitchell | McD | 2020-01-16 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-10 | John Watts
CTS-03 | CTS-03 | PI16126 | Verified | IA regulator leaking at MBV01AAA701; GT Lube Oil Temperature Control Valve | B | I | Albert Burge | McD | 2020-01-16 | Albert Burge | Comm | 2020-02-05 | Albert Burge | 2020-03-03 | John Watts
CTS-03 | CTS-03 | PI16127 | Verified | Pressure Indicators on top of Accumulators not shown on Mitsubishi drawing | C | I | James Strange | MHI | 2020-01-16 | James Strange | Comm | 2020-05-21 | Ron McMurtry | 2021-02-01 | Dave Goldak
CTS-03 | CTS-03 | PI16128 | Verified | 1AMBV21CP703; Oil Supply Pressure Indicator is leaking at Lube Oil Purifier System, S end of Lube Oil Reservoir | B | P | Albert Burge | McD | 2020-01-16 | Albert Burge | Comm | 2020-03-10 | Albert Burge | 2020-04-06 | Bernard Stasse
CTS-03 | CTS-03 | PI16129 | Verified | Tag all Seal Oil skid components | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-04 | Kelvin Cook | 2020-08-06 | Dave Goldak
CTS-03 | CTS-03 | PI16130 | Verified | Support U-Bolt loose at NE end corner of Seal Oil skid, ground level | C | P | Bobby Williams | McD | 2020-01-16 | Bobby Williams | Comm | 2020-02-11 | Charlie English | 2020-04-06 | Bernard Stasse
CTS-03 | CTS-03 | PI16131 | Verified | Line No. 1-1A-CTS-0240 shown on P&ID not installed | B | P | James Beech | McD | 2020-01-16 | James Beech | Comm | 2020-02-19 | Bobby Williams | 2020-03-03 | John Watts
CTS-03 | CTS-03 | PI16132 | Verified | U-bolt nuts loose at Mist Eliminator vent just below goose neck, E side of GT Inlet Air Filter House | C | P | Tim Gallegos | McD | 2020-01-16 | Tim Gallegos | Comm | 2020-05-07 | Tim Gallegos | 2020-08-17 | Dave Goldak
CTS-03 | CTS-03 | PI16133 | Verified | U-Bolt nuts loose at Mist Eliminator 12" drain, E side of GT A Inlet Air Filter House | C | P | Tim Gallegos | McD | 2020-01-16 | Tim Gallegos | Comm | 2020-05-07 | Tim Gallegos | 2020-08-17 | Dave Goldak
CTS-03 | CTS-03 | PI16134 | Verified | U-Bolt nuts loose at Mist Eliminator 2" drain at ground level, E side of GT A | C | P | Bobby Williams | McD | 2020-01-16 | Bobby Williams | Comm | 2020-01-21 | Charlie English | 2020-03-09 | Dave Goldak
CTS-03 | CTS-03 | PI16135 | Verified | Cold gal rust spots on Mist Eliminator pipe supports, E side of GT A Inlet Air Filter House | C | X | Jerry Smith | McD | 2020-01-16 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-08-06 | Dave Goldak
CTS-03 | CTS-03 | PI16136 | Verified | Touch up paint on Lube Oil Skid and Mist Eliminator vent piping | C | X | Jerry Smith | McD | 2020-01-16 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-08-06 | Dave Goldak
CTS-03 | CTS-03 | PI16668 | Verified | 1AMKW01AA007 - 1A's seal oil pressure relief valve is leaking at the top of the valve. | B | M | William Mitchell | McD | 2020-02-07 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-10 | John Watts
CTS-03 | CTS-03 | PI17692 | Verified | 1A mist eliminator blowers are leaking oil housing gasket. | B | M | William Mitchell | McD | 2020-03-04 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-10 | John Watts
CTS-03 | CTS-03 | PI17752 | Verified | Pipe Support 1A-CTS-HGR-0026 not installed | C | P | James Beech | McD | 2020-03-10 | James Beech | Const | 2020-04-29 | James Beech | 2020-06-03 | John Watts
CTS-03 | CTS-03 | PI17753 | Verified | Pipe Support 1A-CTS-HGR-0028 not installed | C | P | James Beech | McD | 2020-03-10 | James Beech | Const | 2020-04-29 | James Beech | 2020-06-03 | John Watts
CTS-03 | CTS-03 | PI18125 | Verified | 1A A Lube Oil Pump Seal Leak | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2020-04-30 | John Watts
CTS-04 | CTS-04 | PI01592 | Verified | 1ACTSK0066, Terminate Cable | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
CTS-04 | CTS-04 | PI01593 | Verified | Install Battery at CO-2 Storage Tank | B | E | Chris Boudreaux | McD | 2019-06-27 | Chris Boudreaux | Const |  |  | 2019-11-23 | Michael Law
CTS-04 | CTS-04 | PI01594 | Verified | Several condulet covers missing at CO-2 storage tank. | B | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-04 | CTS-04 | PI01595 | Verified | Relocate 3" and 2" conduit at north side of CO-2 storage tank to to piping interferance. | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-04 | CTS-04 | PI01596 | Verified | Trim tie raps that secure cables in cable tray. | B | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-04 | CTS-04 | PI01597 | Verified | Grout conduit stands at CO-2 storage tanks. | C | C | Johnny Campbell | McD | 2019-06-27 | Johnny Campbell | Const | 2019-07-22 | Johnny Campbell | 2019-08-21 | Fred Michael
CTS-04 | CTS-04 | PI01598 | Verified | Clean paint from CO-2 stirage tank | C | X | Javier Buelvas | McD | 2019-06-27 | Javier Buelvas | Const |  |  | 2019-11-23 | Michael Law
CTS-04 | CTS-04 | PI01608 | Verified | Complete air blows to the entire piping system | B | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-25 | Kelvin Cook | 2019-07-25 | Kelvin Cook
CTS-04 | CTS-04 | PI01609 | Verified | Install fill connections piping to CO2 tank | A | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-11 | Eric Czajka | 2019-07-19 | Kelvin Cook
CTS-04 | CTS-04 | PI01610 | Verified | Provide pressure testing for the entire piping system | A | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-19 | Kelvin Cook | 2019-07-19 | Kelvin Cook
CTS-04 | CTS-04 | PI01611 | Verified | Remove all plugs after pressure test & comm. blows & install nozzles | B | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-25 | Kelvin Cook | 2019-07-25 | Kelvin Cook
CTS-04 | CTS-04 | PI01612 | Verified | cold galve all pipe supports | C | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const |  |  | 2019-12-04 | Kelvin Cook
CTS-04 | CTS-04 | PI01613 | Verified | Make final connections to pneumatic siren in FG-PA unit after pressure test | B | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-26 | Kelvin Cook | 2019-07-26 | Kelvin Cook
CTS-04 | CTS-04 | PI01614 | Verified | remove all three temporary piggy back support & install proper support | A | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-11 | Eric Czajka | 2019-07-19 | Kelvin Cook
CTS-04 | CTS-04 | PI01615 | Verified | At south west corner of Aux enclosure install support for 3/4" pipe | A | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-11 | Eric Czajka | 2019-07-19 | Kelvin Cook
CTS-04 | CTS-04 | PI01616 | Verified | grout all supports around CO2 tank | C | C | Johnny Campbell | McD | 2019-06-27 | Johnny Campbell | Const | 2019-07-24 | Jack Fields | 2019-08-08 | Kelvin Cook
CTS-04 | CTS-04 | PI01617 | Verified | Grout CO2 tank | B | C | Johnny Campbell | McD | 2019-06-27 | Johnny Campbell | Const | 2019-07-24 | Jack Fields | 2019-07-26 | Kelvin Cook
CTS-04 | CTS-04 | PI01618 | Verified | Install damper pneumatic trip switches to all dampers GT enclosures | A | I | Gonzalo Pena | McD | 2019-06-27 | Gonzalo Pena | Const | 2019-08-20 | Gonzalo Pena | 2019-08-23 | Kelvin Cook
CTS-04 | CTS-04 | PI01619 | Verified | Install damper pneumatic trip switches to all dampers Aux enclosures | A | I | Gonzalo Pena | McD | 2019-06-27 | Gonzalo Pena | Const | 2019-08-20 | Gonzalo Pena | 2019-08-23 | Kelvin Cook
CTS-04 | CTS-04 | PI01620 | Verified | Make final connections to pneumatic siren in turbine bearing enclosure after pressure test | A | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-26 | Kelvin Cook | 2019-07-26 | Kelvin Cook
CTS-04 | CTS-04 | PI01635 | Verified | Install all CO2 warning signs. | B | M | Lonnie Peters | McD | 2019-06-27 | Lonnie Peters | Const | 2019-12-06 | Michael Law | 2020-01-15 | Ron McMurtry
CTS-04 | CTS-04 | PI01646 | Verified | Elbow conduit missing gasket, west ide of the skid | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-06-28 | Shannon Scott
CTS-04 | CTS-04 | PI01647 | Verified | Seal conduits inside the panel | C | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-04 | CTS-04 | PI01648 | Verified | Connect the grounding inside C02 Tank control panel | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-04 | CTS-04 | PI01649 | Verified | Ground the back panel on Pneumatic time delay cabinet | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-04 | CTS-04 | PI01650 | Verified | Ground the back panel on Refrigeration control panel | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-04 | CTS-04 | PI01651 | Verified | Verify if the tag number of C02 tank control panel is correct as per drawing. Tag starts at '11' | B | E | Mike Tabbert | McD | 2019-06-27 | Mike Tabbert | Const | 2019-07-19 | Mike Tabbert | 2019-08-16 | Logan Holland
CTS-04 | CTS-04 | PI03112 | Verified | 1ACTSC0293, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-04 | CTS-04 | PI03113 | Verified | 1ACTSC0301, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-04 | CTS-04 | PI03114 | Verified | 1ACTSC0312, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-04 | CTS-04 | PI03115 | Verified | 1ACTSC0316, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-04 | CTS-04 | PI03116 | Verified | 1ACTSC0290, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-08-29 | Mike Tabbert
CTS-04 | CTS-04 | PI03117 | Verified | 1ACTSC0291, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-04 | CTS-04 | PI03118 | Verified | 1ACTSC0293, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-04 | CTS-04 | PI03119 | Verified | 1ACTSC0301, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-04 | CTS-04 | PI03120 | Verified | 1ACTSC0307, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-08-29 | Mike Tabbert
CTS-04 | CTS-04 | PI03121 | Verified | 1ACTSC0312, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-04 | CTS-04 | PI03122 | Verified | 1ACTSC0313, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
CTS-04 | CTS-04 | PI03123 | Verified | 1ACTSC0314, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-04 | CTS-04 | PI03124 | Verified | 1ACTSC0316, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
CTS-04 | CTS-04 | PI03125 | Verified | At turning gear pull and terminate vendor supplied cable to 4 heat detectors, 301, 302, 303 and 304 from terminal box 013. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-15 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-04 | CTS-04 | PI03126 | Verified | At turning gear pull and terminate vendor supplied cable to two lockout valve status indicator 301 and 302 from terminal box 013. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-20 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-04 | CTS-04 | PI03127 | Verified | At turning gear pull and terminate vendor supplied cable to three horn/strobe EH-301 and 302, EI-301 from terminal box 013. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-15 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-04 | CTS-04 | PI03128 | Verified | At turning gear pull and terminate vendor supplied cablemto two manual pull stations 301 and 302 from terminal box 013. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-15 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-04 | CTS-04 | PI03129 | Verified | At turning gear pull and terminate vendor supplied cable from JBF11 to JBF12. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-15 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-04 | CTS-04 | PI03130 | Verified | At GT enclosure pull and terminate vendor supplied cable from JBF01 to EG-102 and 104 | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-30 | Mike Tabbert
CTS-04 | CTS-04 | PI03131 | Verified | At GT enclosure pull and terminate vendor supplied cable from JBF02 to JBF01. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-30 | Mike Tabbert
CTS-04 | CTS-04 | PI03132 | Verified | At GT enclosure, mount device, Install conduit, pull and terminate vendor supplied cable from JBF03 to GJ-104, GK-104EH-104, GJ-102, GK-102, and EH-102 | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-30 | Mike Tabbert
CTS-04 | CTS-04 | PI03133 | Verified | At GT enclosure, mount device, Install conduit, pull and terminate vendor supplied cable from JBF04 to EH-106, GJ-106, GK-106. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-04 | CTS-04 | PI03134 | Verified | At GT enclosure, mount device, Install conduit, pull and terminate vendor supplied cable from JBF06 to GJ-103, GK-103, EH-103, GJ-101, GK-101, EH-101. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-04 | CTS-04 | PI03135 | Verified | At GT enclosure, mount device, Install conduit, pull and terminate vendor supplied cable from JBF07 to EG-101, EG-103, EH-105, GJ-107, GK-105. | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-08-28 | Mike Tabbert
CTS-04 | CTS-04 | PI03136 | Verified | GT enclosure fire dampers missing Pressure switches. (18) | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-09 | Gonzalo Pena
CTS-04 | CTS-04 | PI03835 | Verified | Ground 1A-JBF02 & 03 inside enclosure, east side. | A | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-09-26 | Logan Holland
CTS-04 | CTS-04 | PI03836 | Verified | Ground 1A-JBF05 & 06 inside enclosure, west side. | A | E | Dustin Futrell | McD | 2019-08-13 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-09-26 | Logan Holland
CTS-04 | CTS-04 | PI04484 | Verified | Complete installation for the CO2 FF system heat detector. Inside the PA skid. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-10-24 | Brian Ballard
CTS-04 | CTS-04 | PI04583 | Verified | Label term. Blocks in 1A-CTS-SGY03GH001. Tomco skid panel. | B | E | Mike Tabbert | McD | 2019-08-23 | Mike Tabbert | Const | 2019-09-09 | Richard Cruz | 2019-09-09 | Fred Michael
CTS-04 | CTS-04 | PI04584 | Verified | JBF-05 - wiring not complete. West side of GT enclosure - mezz. | A | E | Dustin Futrell | McD | 2019-08-23 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-06 | Martin Perry
CTS-04 | CTS-04 | PI04585 | Verified | Re-connect tubing for dampers in the FGPA. After pressure test. | A | I | Gonzalo Pena | McD | 2019-08-23 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-12-18 | Keith Mahoney
CTS-04 | CTS-04 | PI04586 | Verified | Missing condulet cover for 1ASGJ02LS105. West side of GT ground level. | B | E | Dustin Futrell | McD | 2019-08-23 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-04 | CTS-04 | PI04587 | Verified | Labels for 1ASGJ02LS105 and 103 are swapped. May be able to red-line P&ID per Keith M. | C | I | Bobby Williams | McD | 2019-08-23 | Bobby Williams | Const | 2020-02-10 | Bobby Williams | 2020-02-10 | Mike Tabbert
CTS-04 | CTS-04 | PI04588 | Verified | 1ASGJ02LS103 - complete wiring. East side of GT ground level. | A | E | Dustin Futrell | McD | 2019-08-23 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-04 | CTS-04 | PI04589 | Verified | 1ASGJ02GK102 - condulet cover missing 1 screw. East side ground level. | B | E | Dustin Futrell | McD | 2019-08-23 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-11 | Fred Michael
CTS-04 | CTS-04 | PI04590 | Verified | 1AMBY92GH006 - complete termination. East side of GT, mezz level. | A | E | Dustin Futrell | McD | 2019-08-23 | Dustin Futrell | Const | 2019-09-03 | Dustin Futrell | 2019-09-05 | Martin Perry
CTS-04 | CTS-04 | PI04591 | Verified | JBF-03 - door needs bond ground. East side inside GT enclosure. | A | E | Dustin Futrell | McD | 2019-08-23 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-09-03 | Martin Perry
CTS-04 | CTS-04 | PI04592 | Verified | JBF-02 - wires not labeled. East side inside GT enclosure. | A | E | Dustin Futrell | McD | 2019-08-23 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-05 | Martin Perry
CTS-04 | CTS-04 | PI04593 | Verified | LS-208 is incorrectly tagged LS-205. NE corner of lube oil enclosure. | B | E | Bobby Williams | McD | 2019-08-23 | Bobby Williams | Const |  |  | 2019-12-20 | Fred Michael
CTS-04 | CTS-04 | PI04594 | Verified | Limit switch to be set on 1ASGJ02LS203 | B | I | Albert Burge | McD | 2019-08-23 | Albert Burge | Const | 2019-12-02 | Albert Burge | 2019-12-02 | Albert Burge
CTS-04 | CTS-04 | PI04595 | Verified | Dampers are all tagged wrong. Limit switch tags are tagged wrong. Correct tag labelling or MHPS to issue redline drawings showing the actual location on the dampers and switches at site | C | I | Bobby Williams | McD | 2019-08-23 | Bobby Williams | Const | 2020-02-10 | Bobby Williams | 2020-02-10 | Mike Tabbert
CTS-04 | CTS-04 | PI04596 | Verified | JBF011 at turning gear area missing stainless steel tag | A | E | Dustin Futrell | McD | 2019-08-23 | Dustin Futrell | Const | 2019-08-26 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-04 | CTS-04 | PI04597 | Verified | GK106 and EH106 not complete, at GT enclosure area | A | E | Dustin Futrell | McD | 2019-08-23 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-09-03 | Mike Tabbert
CTS-04 | CTS-04 | PI04818 | Verified | Change tank fill and return lines to 304 SS. | B | P | Sheri Fritz | JAN | 2019-09-09 | Sheri Fritz | Const |  |  | 2019-11-05 | Michael Law
CTS-04 | CTS-04 | PI16497 | Verified | Repair and paint dent at North side GT A CO2 Tank | C | X | Jerry Smith | McD | 2020-02-03 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-04-07 | Randy Carpenter
CTS-04 | CTS-04 | PI16498 | Verified | Remove gray paint splatter at S side of GT A CO2 Tank | C | X | Jerry Smith | McD | 2020-02-03 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-04-06 | Bernard Stasse
CTS-04 | CTS-04 | PI16499 | Verified | Vapor and fill line u-bolts loose at North side of GT A CO2 Tank | C | P | Bobby Williams | McD | 2020-02-03 | Bobby Williams | Comm | 2020-02-25 | Bobby Williams | 2020-02-28 | Keith Pollock
CTS-04 | CTS-04 | PI16500 | Verified | Vapor and fill line is missing u-bolt shield at second support upstream of fill station | C | P | Bobby Williams | McD | 2020-02-03 | Bobby Williams | Comm | 2020-02-11 | Charlie English | 2020-02-15 | Shannon Scott
CTS-04 | CTS-04 | PI16501 | Verified | Vapor line is out of plumb at North side of GT A CO2 Tank | C | P | Bobby Williams | McD | 2020-02-03 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-02-21 | Keith Pollock
CTS-04 | CTS-04 | PI16502 | Verified | Remove paint splatter from condensing unit at East end of GT A CO2 Tank | C | X | Jerry Smith | McD | 2020-02-03 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-04-06 | Bernard Stasse
CTS-04 | CTS-04 | PI16503 | Verified | Tubing tray at E end of GT A CO2 Tank is loose, support needs to be redesigned | C | I | Gonzalo Pena | McD | 2020-02-03 | Gonzalo Pena | Comm | 2020-02-10 | James Tanner | 2020-02-10 | Shannon Scott
CTS-04 | CTS-04 | PI16504 | Verified | Missing Limit Switch 1/4" SS tubing clamps on all sides of GT A Lube Oil Enclosure | C | I | Gonzalo Pena | McD | 2020-02-03 | Gonzalo Pena | Comm | 2020-02-10 | James Tanner | 2020-02-15 | Shannon Scott
CTS-04 | CTS-04 | PI16505 | Verified | Missing flex ground NW outside corner of GT A Lube Oil Enclosure | C | E | Sheri Fritz | TRI | 2020-02-03 | Sheri Fritz | Comm | 2020-04-03 | Sheri Fritz | 2020-04-07 | Randy Carpenter
CTS-04 | CTS-04 | PI16506 | Verified | Pnuematic Horn bracket missing screw inside GT A Turning Gear Enclosure | C | E | Chris Colvin | McD | 2020-02-03 | Chris Colvin | Comm | 2020-04-08 | Chris Colvin | 2020-06-08 | John Watts
CTS-04 | CTS-04 | PI16507 | Verified | Clean out GT A Lube Oil, Turning Gear, Fuel Gas/ Purge Air Valve House and GT Enclosures | C | C | Alan Huntsman | McD | 2020-02-03 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-04-06 | Bernard Stasse
CTS-04 | CTS-04 | PI16508 | Verified | Clean off rust and paint top of all Fire Dampers throughout system | C | X | Johnny Campbell | McD | 2020-02-03 | Johnny Campbell | Comm | 2020-04-06 | Johnny Campbell | 2020-04-07 | Randy Carpenter
CTS-04 | CTS-04 | PI16509 | Verified | GT A Fuel Gas / Purge Air bottom door hinge is broken | C | C | James Strange | MHI | 2020-02-03 | James Strange | Comm | 2020-04-13 | James Strange | 2020-06-08 | John Watts
CTS-04 | CTS-04 | PI16510 | Verified | AA 107 Damper sensing line bracket is loose, not attached to enclosure wall, missing screws | B | I | Gonzalo Pena | McD | 2020-02-03 | Gonzalo Pena | Comm | 2020-02-10 | James Tanner | 2020-02-15 | Shannon Scott
CTS-04 | CTS-04 | PI16511 | Verified | CO2 Fire Suppression piping and nozzles inside GT A Enclosure does not match the vendor drawing | C | P | James Strange | McD | 2020-02-03 | James Strange | Comm | 2020-04-09 | James Strange | 2020-06-08 | John Watts
CTS-04 | CTS-04 | PI16512 | Verified | Dampers and Limit Switches are not numbered per vendor drawing throughout system | C | P | James Strange | McD | 2020-02-03 | James Strange | Comm | 2020-04-09 | James Strange | 2020-06-08 | John Watts
CTS-04 | CTS-04 | PI16513 | Verified | Damper AA-112 and Limit Switch LS-108 are missing tags at GT A Fuel Gas / Purge Air Enclosure | C | M | Shane Crowe | McD | 2020-02-03 | Shane Crowe | Comm | 2020-05-04 | Shane Crowe | 2020-07-29 | John Watts
CTS-04 | CTS-04 | PI16514 | Verified | All valves and components at GT A CO2 tank missing tags | C | P | Kelvin Cook | McD | 2020-02-03 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-06 | Bernard Stasse
CTS-04 | CTS-04 | PI16515 | Verified | What is the purpose of bronze fitting tie wrapped to under side of all dampers? | C | P | Kelvin Cook | McD | 2020-02-03 | Kelvin Cook | Comm | 2020-02-18 | Michael Law | 2020-04-06 | Bernard Stasse
CTS-05 | CTS-05 | PI03231 | Verified | Valve 1AQFF11AA122 needs packing gland stud | A | M | Joshua Sturgeon | McD | 2019-08-06 | Joshua Sturgeon | Const | 2019-08-09 | Shane Crowe | 2019-08-09 | Joshua Sturgeon
CTS-05 | CTS-05 | PI03232 | Verified | Receiver valves need labels | C | M | James Strange | MHI | 2019-08-06 | James Strange | Const | 2020-04-01 | James Strange | 2020-04-01 | Eric Policarpio
CTS-05 | CTS-05 | PI03234 | Verified | LM-1373 - Remove wood from 1A-CTS-PD-HGR-23BOA-16 | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-05 | CTS-05 | PI03235 | Verified | LM-1373 - Install pipe support stand 1A-CTS-PD-HDGR-23B0A-17 | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-19 | Kelvin Cook
CTS-05 | CTS-05 | PI03236 | Verified | LM-1373 - PS-12 complete installation | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-15 | Terry Deaton | 2019-08-16 | Kelvin Cook
CTS-05 | CTS-05 | PI03237 | Verified | LM-1373 - PS-11 complete installation | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-15 | Terry Deaton | 2019-08-16 | Kelvin Cook
CTS-05 | CTS-05 | PI03238 | Verified | LM-1373 - PS-02 complete installation | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-05 | CTS-05 | PI03239 | Verified | LM-1373 - PS-04 complete installation | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-05 | CTS-05 | PI03240 | Verified | LM-1373 - Connect 1APITMBL03CP101 | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-14 | Kelvin Cook
CTS-05 | CTS-05 | PI03241 | Verified | LM-1373 - Remove all dunnage from piping | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-05 | CTS-05 | PI03242 | Verified | LM-1373 - PS-03 complete installation | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-05 | CTS-05 | PI03243 | Verified | LM-1373 - PS-01 & 08 install proper bolts to the base plate on spring can | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-05 | CTS-05 | PI03244 | Verified | LM-1373 - Air tank SRV needs piping or tubing to ground | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-14 | Kelvin Cook
CTS-05 | CTS-05 | PI03245 | Verified | LM-1373 - Air Tank Drain valve needs piping or tubing to ground | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-08 | Kelvin Cook | 2019-08-08 | Kelvin Cook
CTS-05 | CTS-05 | PI03246 | Verified | LM-1373 - 1A-CTS-P41-130-01 install pipe support 1A-CTS-HGR-0151 | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-28 | Kelvin Cook
CTS-05 | CTS-05 | PI03247 | Verified | LM-1362 - Install gasket and torque spool at exhaust ? | A | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-08-28 | Terry Deaton | 2019-09-18 | Kelvin Cook
CTS-05 | CTS-05 | PI03248 | Verified | LM-1362 - Remove all braces at expansion joints | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-15 | Terry Deaton | 2019-08-16 | Kelvin Cook
CTS-05 | CTS-05 | PI03249 | Verified | LM-1362 - Set spring cans to cold setting | A | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-08-28 | Terry Deaton | 2019-09-04 | Kelvin Cook
CTS-05 | CTS-05 | PI03250 | Verified | LM-1367 - Torque flanges except spool 23AOG-10 | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-19 | Kelvin Cook
CTS-05 | CTS-05 | PI03251 | Verified | LM-1367 - Torque flanges as noted and install cover on expansion joint | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-19 | Kelvin Cook
CTS-05 | CTS-05 | PI03252 | Verified | LM-1365 - Install gasket, flange, install cover at expansion joint on LP Line | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-29 | Terry Deaton | 2019-08-29 | Kelvin Cook
CTS-05 | CTS-05 | PI03253 | Verified | LM-1362 - Bend secondary tabs on bolt tabs | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-29 | Terry Deaton | 2019-08-29 | Kelvin Cook
CTS-05 | CTS-05 | PI03254 | Verified | LM-1364 - Bend secondary tabs on bolt tabs | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-29 | Terry Deaton | 2019-08-29 | Kelvin Cook
CTS-05 | CTS-05 | PI03255 | Verified | LK-1365 - Bend secondary tabs on bolt tabs | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-29 | Terry Deaton | 2019-08-29 | Kelvin Cook
CTS-05 | CTS-05 | PI03256 | Verified | LM-1365 - PS-02 missing one bolt at base plate of spring can | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-20 | Kelvin Cook
CTS-05 | CTS-05 | PI03257 | Verified | LM-1365 Lock tabs on clamp are backwards | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-20 | Kelvin Cook
CTS-05 | CTS-05 | PI03259 | Verified | LM-1381 - Install bolts and gaskets 23AOH-12 | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-16 | Tom Noble
CTS-05 | CTS-05 | PI03260 | Verified | LM-1381 - Torque all flanges with exception to connections to turbine | A | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-09-05 | Damon Turner | 2019-09-18 | Kelvin Cook
CTS-05 | CTS-05 | PI03261 | Verified | LM-1381 - Install orifice 23AOH-06 and 07 | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-16 | Tom Noble
CTS-05 | CTS-05 | PI03262 | Verified | LM-1381 - Restore after pressure testing | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-05 | CTS-05 | PI03263 | Verified | LM-1381 - Tighten all U-bolts | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-20 | Kelvin Cook
CTS-05 | CTS-05 | PI03264 | Verified | LM-1385 - PS-04 missing bolts at spring can base | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-20 | Kelvin Cook
CTS-05 | CTS-05 | PI03265 | Verified | LM-1363 - 23BOB missing bolts, flange connections to 6" control valve | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
CTS-05 | CTS-05 | PI03266 | Verified | LM-1383 - Restore system after pressure testing for TCA pipe coming from filter | A | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-09-05 | Damon Turner | 2019-10-03 | Kelvin Cook
CTS-05 | CTS-05 | PI03268 | Verified | LM-1385 - Tab washer missing and bolts, no gasket | A | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-10-03 | Kelvin Cook
CTS-05 | CTS-05 | PI03269 | Verified | LM-1383 - Restore spool, missing bolts | A | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-09-25 | Kelvin Cook
CTS-05 | CTS-05 | PI03270 | Verified | LM-1383 - PS-02 not installed | A | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-18 | Kelvin Cook
CTS-05 | CTS-05 | PI03271 | Verified | LM-1383 - Fix 3 Bolt Clamp PS-23DOE-02 | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
CTS-05 | CTS-05 | PI03272 | Verified | LM-1383 - PS-06 not installed | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-28 | Kelvin Cook
CTS-05 | CTS-05 | PI03273 | Verified | LM-1383 - Rotate actuator head | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
CTS-05 | CTS-05 | PI03274 | Verified | LM-1373 - PS-13 not installed | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-05 | CTS-05 | PI03275 | Verified | LM-1381 - Seal Air line west side ground level north end shoes require lift guides PS-05 | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-05 | CTS-05 | PI03276 | Verified | LM-1381 - Seal Air line west side ground level north end shoes require lift guides PS-06 | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-05 | CTS-05 | PI03277 | Verified | LM-1381 - Seal Air line west side ground level north end shoes require lift guides PS-07 | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-05 | CTS-05 | PI03278 | Verified | PS-19 set in proper location according to detal | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-05 | CTS-05 | PI03556 | Verified | Clean and close the inlet manifold | B | M | Shane Crowe | McD | 2019-08-09 | Shane Crowe | Const | 2019-10-18 | Shane Crowe | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04250 | Verified | Perform clean & close on Air Inlet Filter House and duct work. | A | P | Bobby Williams | McD | 2019-08-14 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-13 | Joshua Sturgeon
CTS-05 | CTS-05 | PI04252 | Verified | Perform clean & close on Inlet Filter House duct work. | A | S | Robert Risher | McD | 2019-08-14 | Robert Risher | Const | 2019-08-16 | Ed Gober | 2019-08-16 | Ed Gober
CTS-05 | CTS-05 | PI04254 | Verified | Torque the inlet duct expansion joint. | A | M | Shane Crowe | McD | 2019-08-15 | Shane Crowe | Const | 2019-08-16 | Shane Crowe | 2019-08-16 | Joshua Sturgeon
CTS-05 | CTS-05 | PI04391 | Verified | Complete and terminate the inlet manifold thermocouple installation | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04405 | Verified | Complete transition / silencer bracing hardware lock welding , QTY 8 bolts. | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Comm | 2019-08-29 | Bobby Williams | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04406 | Verified | Complete the evap cooler pipe support installation welding per LC-01589 pg 118-120. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04407 | Verified | Remove debris inside evap cooler modules and verify cleanliness by BSI. Or seal weld area closed. There are a QTY of 48 through holes 16 holes per level 2, 3, and 4. | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-09-05 | Tim Gallegos | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04408 | Verified | Complete painting / welding / cleaning / and final inspection and remove scaffolding on upstream side of silencer. | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-10-09 | Bobby Williams | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04409 | Verified | Remove gasket material in flow path area along silencer floor. | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-09-04 | Tim Gallegos | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04410 | Verified | Clean silencer floor area and remove debris / inspect. Install isolation plastic to seal off from transition area | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-10-01 | Tim Gallegos | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04411 | Verified | Complete the transition drainage pipe per LC-01589 Pg 123 and complete the Evap Cooler access plenum drainage pipe per LC-01589 Pg 304. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04412 | Verified | Complete the evap cooler pipe installation per LC-01589 pages 117-122. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04413 | Verified | Complete the weather hood drainage pipe work installation per LC-01589 pg 302. | A | P | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-10-09 | Bobby Williams | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04414 | Verified | Install the evap cooler sump to module hardware.. | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04415 | Verified | Install weather hood blanking plates. | A | M | Brian Ballard | MHI | 2019-08-21 | Brian Ballard | Const | 2019-10-03 | Bobby Williams | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04416 | Verified | Complete the anti-ice pipe support installation near AIFH deck, hot work in this area will not be available soon. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-11 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04417 | Verified | Clean transition / Evap cooler trays / Evap cooler access plenum / Filter modules and remove all foreign material | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-24 | Brian Ballard
CTS-05 | CTS-05 | PI04418 | Verified | Remove excess gasket and caulking in the flow path area around the evap cooler / transition interface. | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-09-11 | Tim Gallegos | 2019-11-24 | Brian Ballard
CTS-05 | CTS-05 | PI04419 | Verified | Clean the evap cooler sump and trays and remove all foreign material. | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-24 | Brian Ballard
CTS-05 | CTS-05 | PI04420 | Verified | Complete the final filter and evap cooler media | B | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-24 | Brian Ballard
CTS-05 | CTS-05 | PI04421 | Verified | Drifdek installation per LC- 01589 pages 124 - 125. | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-11-06 | Bobby Williams | 2019-11-24 | Brian Ballard
CTS-05 | CTS-05 | PI04422 | Verified | Complete the pitot tube tubing installation. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-11-24 | Brian Ballard
CTS-05 | CTS-05 | PI04423 | Verified | Remove debris on top of trash screens. | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-10-10 | Tim Gallegos | 2019-11-24 | Brian Ballard
CTS-05 | CTS-05 | PI04424 | Verified | Replace or repair damaged trash screens. | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-10-11 | Tim Gallegos | 2019-11-24 | Brian Ballard
CTS-05 | CTS-05 | PI04425 | Verified | Complete the AIFH insulation and cladding. | B | Q | Jorge Alexander | PCI | 2019-08-21 | Jorge Alexander | Const | 2019-12-17 | Jorge Alexander | 2020-01-15 | Ron McMurtry
CTS-05 | CTS-05 | PI04426 | Verified | Caulk / seal the weather hood flashing per LC-01589 page 238- 239. | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-10-02 | Bobby Williams | 2019-11-24 | Brian Ballard
CTS-05 | CTS-05 | PI04427 | Verified | Complete the evap cooler sump level gauge installation. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-29 | Gonzalo Pena | 2020-01-15 | Ron McMurtry
CTS-05 | CTS-05 | PI04428 | Verified | Remove debris inside the weather hood gutters. | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-10-02 | Bobby Williams | 2019-11-24 | Brian Ballard
CTS-05 | CTS-05 | PI04429 | Verified | Complete the 5 ton / 6 ton / 3 ton trolley installation per LC-01589 page 67 - 69. | B | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2020-01-15 | Bobby Williams | 2020-03-03 | Michael Law
CTS-05 | CTS-05 | PI04430 | Verified | Complete the AIFH earth cable installation per LC-01589 page 211. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-11-24 | Brian Ballard
CTS-05 | CTS-05 | PI04444 | Verified | Complete the anti-ice pipe tubing installation. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-08-28 | Brian Ballard
CTS-05 | CTS-05 | PI04445 | Verified | Install SS shims to separate dissimilar materials for all anti-ice and 2C cooling external pipe supports. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-05 | Damon Turner | 2019-10-24 | Brian Ballard
CTS-05 | CTS-05 | PI04505 | Verified | Panel 1AMBL30GH001 - need earth ground on panel. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-04 | Dustin Futrell | 2019-09-10 | Albert Burge
CTS-05 | CTS-05 | PI04506 | Verified | Panel 1AMBL30GH001 - missing condulet covers. | B | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-10 | Albert Burge
CTS-05 | CTS-05 | PI04507 | Verified | Panel 1AMBL30GH001 - complete instrument tubing to transmitters (4). | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-10 | Albert Burge
CTS-05 | CTS-05 | PI04508 | Verified | Panel 1AMBL30GH001 - replace plastic plugs with SS plugs - 1/4". | B | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-16 | Albert Burge
CTS-05 | CTS-05 | PI04509 | Verified | Panel 1AMBL30GH001 - terminate wiring for lights & receptacles. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-05 | CTS-05 | PI04510 | Verified | Panel 1AMBL30GH001 - conduit needs low point drains. | B | E | Chris Colvin | McD | 2019-08-21 | Chris Colvin | Const | 2019-09-09 | Richard Cruz | 2020-01-13 | Fred Michael
CTS-05 | CTS-05 | PI04511 | Verified | Panel 1AMBL30GH001 - 2" conduit missing strap. | B | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-10-15 | Fred Michael
CTS-05 | CTS-05 | PI04512 | Verified | Panel 1ABML30GH002 - clean inside & outside of panel. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-04 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-05 | CTS-05 | PI04513 | Verified | Panel 1ABML30GH002 - replace 1/4" plastic plugs with SS plugs. | B | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-11-20 | Fred Michael
CTS-05 | CTS-05 | PI04514 | Verified | Panel 1ABML30GH002 - repair or replace rusty ground bar. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-04 | Dustin Futrell | 2019-09-10 | Albert Burge
CTS-05 | CTS-05 | PI04516 | Verified | 1AMBL01CT101 - complete termination. Top of IFH - south. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-16 | Albert Burge
CTS-05 | CTS-05 | PI04517 | Verified | 1AMBL01CT102 - complete termination. Top of IFH - south. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-16 | Albert Burge
CTS-05 | CTS-05 | PI04518 | Verified | 1AMBL01CM101 - complete termination. Top of IFH - south. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-16 | Albert Burge
CTS-05 | CTS-05 | PI04519 | Verified | 1AMBL01CM101 - complete termination. Top of IFH - south. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-16 | Albert Burge
CTS-05 | CTS-05 | PI04520 | Verified | 1AMBL01CT101 / 102 - missing condulet covers. | B | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-05 | CTS-05 | PI04521 | Verified | Tighten & straighten flex on 1A-CTS-MBL02AP201M02 - Evap. Cooler pump motor. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-04 | Dustin Futrell | 2019-09-26 | Jonathan Donham
CTS-05 | CTS-05 | PI04522 | Verified | 1A-CTS-MBL02AP201M01 - term. Blocks in motor term. Box rusted - clean. (Evap. Cooler pump motor). Term. blocks okay, need to wipe down motor. | A | P | Kelvin Cook | McD | 2019-08-21 | Kelvin Cook | Const | 2019-11-06 | Joshua Sturgeon | 2020-01-13 | Fred Michael
CTS-05 | CTS-05 | PI04523 | Verified | 1A-CTS-MBL02AP201M02- term. Blocks in motor term. Box rusted - clean. (Evap. Cooler pump motor). Term. blocks okay, need to wipe down motor. | A | P | Kelvin Cook | McD | 2019-08-21 | Kelvin Cook | Const | 2019-11-06 | Joshua Sturgeon | 2020-01-13 | Fred Michael
CTS-05 | CTS-05 | PI04524 | Verified | 1AMBL02CP101 (Pressure Flow) connector broken. IFH top east side. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-10 | Albert Burge
CTS-05 | CTS-05 | PI04525 | Verified | Hood / eave for row of indicators hangs too low covering visibility to see indicator. - Top of IFH - east. | B | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const |  |  | 2019-09-16 | Albert Burge
CTS-05 | CTS-05 | PI04526 | Verified | Complete tubing for Evap. Cooler sump level transmitter. Top of IFH east. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-08-28 | Albert Burge
CTS-05 | CTS-05 | PI04527 | Verified | 1AMBL02AA701KA01 needs bug screen. Top of IFH east. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-09-11 | Gonzalo Pena | 2019-09-23 | Albert Burge
CTS-05 | CTS-05 | PI04528 | Verified | 1AMBL02AA902KA02 needs bug screen. Top of IFH east. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-09-11 | Gonzalo Pena | 2019-09-23 | Albert Burge
CTS-05 | CTS-05 | PI04529 | Verified | Panel 1AMBL02AC301 - Non-scheduled power feeder cable not installed. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-09-20 | Mike Tabbert
CTS-05 | CTS-05 | PI04530 | Verified | Panel 1AMBL02AC301 - Clean inside of panel. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-05 | CTS-05 | PI04531 | Verified | Panel 1AMBL02AC301 - Ground back plate. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-10-02 | Fred Michael
CTS-05 | CTS-05 | PI04532 | Verified | Complete bolting of Evap. Cooler Skid. | A | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-08-28 | Shane Crowe | 2019-09-20 | Mike Tabbert
CTS-05 | CTS-05 | PI04533 | Verified | Plug spare conduit - NW corner of Evap. Cooler skid. | B | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-13 | Richard Cruz | 2019-09-28 | Mike Tabbert
CTS-05 | CTS-05 | PI04534 | Verified | Valve 1AMBL03AA704 - missing explosion proof cover on limit switch. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-20 | Fred Michael
CTS-05 | CTS-05 | PI04535 | Verified | Valve 1AMBL03AA703 - tagged incorrectly & regulator missing tag. | C | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2020-01-03 | Gonzalo Pena | 2020-01-13 | Fred Michael
CTS-05 | CTS-05 | PI04536 | Verified | Valve 1AMBL03AA703 - condulet covers missing at valves (two 3/4" and one 3"). | B | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-10-02 | Fred Michael
CTS-05 | CTS-05 | PI04537 | Verified | 1AMBL03AA702 - complete IA tubing. Ground level east side. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-08-28 | Albert Burge
CTS-05 | CTS-05 | PI04538 | Verified | 1AMBL03AA701 - complete IA tubing. Ground level east side. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-08-28 | Albert Burge
CTS-05 | CTS-05 | PI04539 | Verified | 1AMBL03AA707 - complete IA tubing. Ground level east side. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-08-28 | Albert Burge
CTS-05 | CTS-05 | PI04540 | Verified | 1AMBL03AA702 - water in gauge. Ground level east side. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-08-28 | Albert Burge
CTS-05 | CTS-05 | PI04541 | Verified | 1AMBH04CT002 - tighten instrument & flex. Ground level east side. | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-09-20 | Fred Michael
CTS-05 | CTS-05 | PI04542 | Verified | 1AMBL03AA701 - ground flex on actuator. Ground level east side. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-20 | Fred Michael
CTS-05 | CTS-05 | PI04543 | Verified | 1AMBH04AA712- flex too short on positioner. Ground level east side. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-16 | Albert Burge
CTS-05 | CTS-05 | PI04544 | Verified | 1AMBH04AA712- missing condulet cover. Ground level east side. | B | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-16 | Albert Burge
CTS-05 | CTS-05 | PI04545 | Verified | 1AMBH05AA751 & 752 - missing tags . Ground level east side. | C | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-23 | Albert Burge
CTS-05 | CTS-05 | PI04546 | Verified | 1AMBH05AA752 - need 90 on seal tite . Ground level east side. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-16 | Albert Burge
CTS-05 | CTS-05 | PI04547 | Verified | 1AMBH05AA752 - missing condulet covers . Ground level east side. | B | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-16 | Albert Burge
CTS-05 | CTS-05 | PI04548 | Verified | 1AMBH05CL202, 203 204 & 205 - missing tag. Ground level east side. | C | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-16 | Albert Burge
CTS-05 | CTS-05 | PI04549 | Verified | 1AMBH05CL205 - put cable in conduit. Ground level east side. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-16 | Albert Burge
CTS-05 | CTS-05 | PI04550 | Verified | 1AMBH05CL205 - tighten seal tite. Ground level east side. | A | E | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-16 | Albert Burge
CTS-05 | CTS-05 | PI08170 | Verified | Complete conduit and cabling for hoist MBL30AE202. | B | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-11 | Mike Tabbert
CTS-05 | CTS-05 | PI08171 | Verified | Complete cabling for hoist MBL30AE201. | B | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-11 | Mike Tabbert
CTS-05 | CTS-05 | PI09787 | Verified | Test Package CTS-T-1A-AF09 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-01 | Kelvin Cook
CTS-05 | CTS-05 | PI10005 | Verified | LM-1373 - Restore system, torque flanges after air blow | B | P | Dillion Starkey | McD | 2019-10-22 | Dillion Starkey | Const |  |  | 2019-11-04 | Kelvin Cook
CTS-05 | CTS-05 | PI12594 | Verified | Boroscope inspection MP & LP bleed air lines at exhaust tie in. | B | P | Kelvin Cook | McD | 2019-10-28 | Kelvin Cook | Const | 2019-11-04 | Kelvin Cook | 2019-11-24 | Brian Ballard
CTS-05 | CTS-05 | PI12659 | Verified | Cut grating at MBL30GH002, eliminate rub point on tubing | A | I | Gonzalo Pena | McD | 2019-10-31 | Gonzalo Pena | Const | 2019-11-01 | Kelvin Cook | 2020-02-27 | Michael Law
CTS-05 | CTS-05 | PI12660 | Verified | Relocate 1ACNC00GZ001 away from air inlet | A | I | Gonzalo Pena | McD | 2019-10-31 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2020-01-28 | Fred Michael
CTS-05 | CTS-05 | PI12598 | Verified | Replace evap. cooler pump motor B. | B | M | Shane Crowe | McD | 2019-10-29 | Shane Crowe | Const | 2019-12-02 | Shane Crowe | 2019-12-12 | Michael Law
CTS-05 | CTS-05 | PI15685 | Verified | SAR 03505 1A indicator switch damaged during re-installation of anti- icing valve 1A. | B | I | Albert Burge | McD | 2020-01-09 | Albert Burge | Comm | 2020-02-03 | Albert Burge | 2020-02-27 | Michael Law
CTS-05 | CTS-05 | PI15686 | Verified | SAR 03506 1B barometric pressure transmitter with water damage.. - on order | B | I | Albert Burge | McD | 2020-01-09 | Albert Burge | Comm | 2020-03-26 | Albert Burge | 2020-04-02 | Michael Law
CTS-05 | CTS-05 | PI16910 | Verified | Complete cable terminations at 1AMBL30GH001; Air Intake System Power Distrubtion/Instrument Panel, GT A Inet Air Filter House grating platform, West side | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
CTS-05 | CTS-05 | PI16911 | Verified | Clean out inside of 1AMBL30GH002; Air Intake Duct Differential Pressure Instrument Panel | C | I | Gonzalo Pena | McD | 2020-02-18 | Gonzalo Pena | Comm | 2020-02-24 | James Tanner | 2020-04-06 | Bernard Stasse
CTS-05 | CTS-05 | PI16912 | Verified | Identify and tag spare pair inside 1AMBL30GH002; Air Intake Duct Differential Pressure Instrument Panel, GT A Inet Air Filter House grating platform, West side | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
CTS-05 | CTS-05 | PI16913 | Verified | Insulation on shields are too short at 1AMBL30GH002; Air Intake Duct Differential Pressure Instrument Panel, GT A Inet Air Filter House grating platform, West side | B | E | Jonathan Donham | McD | 2020-02-18 | Jonathan Donham | Comm | 2020-03-26 | Jonathan Donham | 2020-04-06 | Bernard Stasse
CTS-05 | CTS-05 | PI16914 | Verified | Verify shield to ground on wire 1ACTSX0314 inside 1AMBL30GH002; Air Intake Duct Differential Pressure Instrument Panel, GT A Inet Air Filter House grating platform, West side | C | E | Jonathan Donham | McD | 2020-02-18 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2020-04-07 | Randy Carpenter
CTS-05 | CTS-05 | PI16915 | Verified | Install plug on MBL03AA922; Drain Valve, downstream of PIT-MBL03CP101, 10" Anti-Icing line, GT A Inet Air Filter House grating platform, East side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-01 | James Beech | 2020-07-29 | John Watts
CTS-05 | CTS-05 | PI16916 | Verified | Flex conduit ground disconnected at MBL03AA704; GT Anti-Icing Air Temperature Control Valve (B), GT A Inet Air Filter House grating platform, East side | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
CTS-05 | CTS-05 | PI16917 | Verified | Repair damaged insulation on Anti-Icing 10" line downstream of MBL03AA704; GT Anti-Icing Air Temperature Control Valve (B), GT A Inet Air Filter House grating platform, East side | C | Q | Josh Koerner | PCI | 2020-02-18 | Josh Koerner | Comm | 2020-06-19 | Jason Ezell | 2020-06-19 | Jason Ezell
CTS-05 | CTS-05 | PI16918 | Verified | Flex conduit connections loose at MBL03AA703; GT Anti-Icing Air Temperature Control Valve (A), GT A Inet Air Filter House grating platform, East side | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
CTS-05 | CTS-05 | PI16920 | Verified | Install plug on MBL03AA934 Drain Valve, downstream of MBL03AA704; GT Anti-Icing Air Temperature Control Valve (B), GT A Inet Air Filter House grating platform, East side | C | P | Bobby Williams | McD | 2020-02-18 | Bobby Williams | Comm | 2020-02-25 | Tim Gallegos | 2020-04-06 | Bernard Stasse
CTS-05 | CTS-05 | PI16922 | Verified | Remove scaffolding, materials, trash etc from GT A Inlet Air Filter House grating platform | C | C | Alan Huntsman | McD | 2020-02-18 | Alan Huntsman | Comm | 2020-03-18 | Johnny Campbell | 2020-04-06 | Bernard Stasse
CTS-05 | CTS-05 | PI16923 | Verified | Loose grating at NE side of GT A Inlet Air Filter House grating platform, between Anti-Icing piping and Filter House | B | S | Bobby Williams | McD | 2020-02-18 | Bobby Williams | Comm | 2020-02-25 | Tim Gallegos | 2020-03-03 | John Watts
CTS-05 | CTS-05 | PI16924 | Verified | One (1) cable not terminated inside 1AMBL02AC301; Evaporator Cooler Control Panel, GT A Inet Air Filter House grating platform, East side | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-03-03 | John Watts
CTS-05 | CTS-05 | PI16925 | Verified | Heat shrink wire tags inside 1AMBL02AC301; Evaporator Cooler Control Panel, GT A Inet Air Filter House grating platform, East side | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-06 | Bernard Stasse
CTS-05 | CTS-05 | PI16926 | Verified | Two cable tags buried in penetration seal inside 1AMBL02AC301; Evaporator Cooler Control Panel, GT A Inet Air Filter House grating platform, East side | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-03-03 | John Watts
CTS-05 | CTS-05 | PI16927 | Verified | Analog Fix MA Repeaters (2) are not mounted inside 1AMBL02AC301; Evaporator Cooler Control Panel, GT A Inet Air Filter House grating platform, East side | C | I | James Strange | MHI | 2020-02-18 | James Strange | Comm | 2020-03-27 | James Strange | 2020-04-06 | Bernard Stasse
CTS-05 | CTS-05 | PI16928 | Verified | U-Bolt nut loose on Flow Indicator manifold, Evaporative Cooler skid, GT A Inet Air Filter house grating platform, East side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-01 | James Beech | 2020-07-29 | John Watts
CTS-05 | CTS-05 | PI16929 | Verified | MBL02AP201; Evap Cooler Pump A Suction Strainer (S2) flange bolts under flush, Evap Cooler Skid, GT A Inlet Air Filter House grating platform, East side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-01 | James Beech | 2020-07-29 | John Watts
CTS-05 | CTS-05 | PI16930 | Verified | Screw missing at MBL02AP202; Evap Cooler Pump B Motor cable termination box cover Evap Cooler Skid, GT A Inlet Air Filter House grating platform, East side | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-06 | Bernard Stasse
CTS-05 | CTS-05 | PI16931 | Verified | Conduit open ended, needs plug at NW corner of Evap Cooler skid, GT A Inlet Filter House grating platform, East side | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-05 | CTS-05 | PI16932 | Verified | Equipment tags missing at Evap Cooler skid components, GT A Inlet Filter House grating platform, East side | C | M | James Strange | MHI | 2020-02-18 | James Strange | Comm | 2020-04-09 | James Strange | 2020-07-29 | John Watts
CTS-05 | CTS-05 | PI16933 | Verified | Loose U-bolt nuts at 10" Evap Cooler Pump suction piping, West side of Evap Cooler Pump skid, GT A Inlet Filter House grating platform, East side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-01 | James Beech | 2020-07-29 | John Watts
CTS-05 | CTS-05 | PI16934 | Verified | Rotate 2" PVC Drain Valve that connects to carbon steel drain line, currently rubbing against 1AMBL30GH001; Air Intake System Power Distribution/Instrument tubing, GT A Inlet Filter House grating platform West side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-01 | James Beech | 2020-07-29 | John Watts
CTS-05 | CTS-05 | PI16935 | Verified | Loose bolt on PVC blind flange under Grat 21 (1st Filter House grating platform), GT A Inlet Filter House grating platform West side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-01 | James Beech | 2020-07-29 | John Watts
CTS-05 | CTS-05 | PI17754 | Verified | Repair gap in pipe lagging, Large Diameter anti-icing piping, east of 1A inlet . | C | Q | Josh Koerner | PCI | 2020-03-10 | Josh Koerner | Const | 2020-06-19 | Jason Ezell | 2020-06-19 | Jason Ezell
CTS-05 | CTS-05 | PI18098 | Verified | 1A-CTS-MBL03, 1A-CTS-MBA01AE101, 1A-CTS-MNL01AT101 - SCPS ran both GTs to base load and did an inspection that showed hot spots on the evap cooler drift eliminators. This was due to the anti-icing air system that runs at all times below 95% base load. | C | M | James Strange | MHI | 2020-03-18 | James Strange | Comm | 2020-04-14 | James Strange | 2020-06-02 | Cintrel Spears
CTS-06 | CTS-06 | PI03163 | Verified | Grout 1A GT Casing Cooling Air Fan Unit Skid 1A-CTS-QEF13. | B | C | Johnny Campbell | McD | 2019-08-05 | Johnny Campbell | Const | 2019-08-14 | Johnny Campbell | 2019-08-20 | Joshua Sturgeon
CTS-06 | CTS-06 | PI03165 | Verified | Complete eng. Pipe rework. ISO 1A-CTS-PD-P40-0206-01. | A | P | Terry Deaton | McD | 2019-08-05 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-06 | CTS-06 | PI03167 | Verified | LM 13-72 internal - install SS wrap & hose clamp. ISO 1A-CTS-PS-7A0A-01. | B | P | Terry Deaton | McD | 2019-08-05 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-16 | Kelvin Cook
CTS-06 | CTS-06 | PI03169 | Verified | LM 13-72 internal - Torque all flanges & bend tabs. | A | P | Terry Deaton | McD | 2019-08-05 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-06 | CTS-06 | PI03171 | Verified | LM 13-72 external - remove dunnage from under pipe. | B | P | Terry Deaton | McD | 2019-08-05 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-20 | Kelvin Cook
CTS-06 | CTS-06 | PI03173 | Verified | LM 13-72 external Install & tighten u-bolts. | B | P | Terry Deaton | McD | 2019-08-05 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-20 | Kelvin Cook
CTS-06 | CTS-06 | PI03174 | Verified | LM 13-72 external - Torque all flanges & bend tabs. | A | P | Terry Deaton | McD | 2019-08-05 | Terry Deaton | Const | 2019-08-15 | Terry Deaton | 2019-08-16 | Kelvin Cook
CTS-06 | CTS-06 | PI03176 | Verified | Set spring can to cold setting 1A-CTS-PS-7A0A-03 | B | P | Damon Turner | McD | 2019-08-05 | Damon Turner | Const | 2019-08-16 | Terry Deaton | 2019-10-03 | Kelvin Cook
CTS-06 | CTS-06 | PI03178 | Verified | 1ACTSK0020, terminate motor space heater after temporary power is removed. | A | E | Logan Holland | McD | 2019-08-05 | Logan Holland | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
CTS-06 | CTS-06 | PI03179 | Verified | 1ACTSC0252, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-07 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-06 | CTS-06 | PI03180 | Verified | 1ACTSC0253, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-07 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-06 | CTS-06 | PI03181 | Verified | 1ACTSC0254, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-07 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-06 | CTS-06 | PI03182 | Verified | 1ACTSC0255, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-07 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-06 | CTS-06 | PI03183 | Verified | 1ACTSC0256, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-07 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-06 | CTS-06 | PI03184 | Verified | 1ACTSC0257, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-07 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-06 | CTS-06 | PI03185 | Verified | 1ACTSX0353, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-07 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-06 | CTS-06 | PI03186 | Verified | 1ACTSK0042, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-07 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-06 | CTS-06 | PI03187 | Verified | 1ACTSX0354, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-07 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-06 | CTS-06 | PI03188 | Verified | Condulet Covers need to be installed around Casing Cooling skid, total of 10. | B | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-14 | Mike Tabbert
CTS-06 | CTS-06 | PI03189 | Verified | 1A-PDIT-DEF13CP501, sealtight connectors loose and sealtight grounds loose. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-14 | Mike Tabbert
CTS-06 | CTS-06 | PI03190 | Verified | Pour hazardous area electrical seals after commissioning. | B | E | Chris Colvin | McD | 2019-08-05 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CTS-06 | CTS-06 | PI03191 | Verified | 1A-CTS-QEF13AN101-M01, motor feed sealtight and space heater connectors loose and sealtight grounding loose. | B | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
CTS-06 | CTS-06 | PI03192 | Verified | Ground Case Cooling fan skid to ground grid. | B | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-14 | Mike Tabbert
CTS-06 | CTS-06 | PI03193 | Verified | Complete tubing going to instrument 1A-CTS-QEF13AA711. | A | I | Gonzalo Pena | McD | 2019-08-05 | Gonzalo Pena | Const | 2019-08-07 | Gonzalo Pena | 2019-08-14 | Mike Tabbert
CTS-06 | CTS-06 | PI03194 | Verified | 1ACTSK0042, terminate motor cable using motor termination kits. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-14 | Mike Tabbert
CTS-06 | CTS-06 | PI03195 | Verified | Install tubing going to valves 1A-CTS-QEF13AA701KA01 and 1A-CTS-QEF13AA702KA01 | A | I | Gonzalo Pena | McD | 2019-08-05 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-14 | Mike Tabbert
CTS-06 | CTS-06 | PI03196 | Verified | Tail in cables going to valves 1A-CTS-QEF13AA701KA01 and 1A-CTS-QEF13AA702KA01 | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Michael Law
CTS-06 | CTS-06 | PI03197 | Verified | Turn in all completion paperwork | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-15 | Dustin Futrell | 2019-08-16 | Mike Tabbert
CTS-06 | CTS-06 | PI03198 | Verified | Seal tight and conduit need to be completed going to valves 1A-CTS-QEF13AA701KA01 and 1A-CTS-QEF13AA702KA01 | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Michael Law
CTS-06 | CTS-06 | PI03267 | Verified | LM-1385 - Restore system after pressure testing for TCA pipe coming from filter | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-06 | CTS-06 | PI03820 | Verified | Complete pipe test & submit CCFs to turnover. | A | P | Terry Deaton | McD | 2019-08-13 | Terry Deaton | Const | 2019-08-14 | Kelvin Cook | 2019-08-16 | Ed Gober
CTS-06 | CTS-06 | PI16956 | Verified | GT A Casing Cooling Air Fan skid components need to be cleaned and painted | C | X | Jerry Smith | McD | 2020-02-18 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-04-06 | Bernard Stasse
CTS-06 | CTS-06 | PI16957 | Verified | Resurface GT A Casing Cooling Air Fan equipment pad, previously bush hammered | C | C | Alan Huntsman | McD | 2020-02-18 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-04-06 | Bernard Stasse
CTS-06 | CTS-06 | PI16958 | Verified | Double nut U-Bolts on 6" SS piping to GT A Fuel Gas Purge Air Supply | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-08 | James Beech | 2020-07-29 | John Watts
CTS-06 | CTS-06 | PI16959 | Verified | Remove carbon contamination from all SS piping throughout sub-system | C | C | Alan Huntsman | McD | 2020-02-18 | Alan Huntsman | Comm | 2020-03-18 | Johnny Campbell | 2020-04-06 | Bernard Stasse
CTS-06 | CTS-06 | PI16960 | Verified | Complete handrails at South end of valve platform | C | C | Bobby Williams | McD | 2020-02-18 | Bobby Williams | Comm | 2020-02-26 | Tim Gallegos | 2020-04-06 | Bernard Stasse
CTS-06 | CTS-06 | PI16961 | Verified | Remove teflon tape from Instrument Air fitting to QEF13AA702; GT A Casing Cooling Air Supply Valve, replace with pipe thread compound, located at valve platform, West side of GT A | C | I | Gonzalo Pena | McD | 2020-02-18 | Gonzalo Pena | Comm | 2020-02-20 | James Tanner | 2020-04-06 | Bernard Stasse
CTS-06 | CTS-06 | PI16962 | Verified | Weld uni-strut horizontal conduit support at grating level, currently loose, located at valve platform, West side of GT A | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-08-20 | Tim Green | 2021-05-27 | John Watts
CTS-06 | CTS-06 | PI16963 | Verified | Replace u-bolt at Instrument Air line to QEF13AA702; GT A Casing Cooling Air Supply Valve, valve platform, West side of GT A | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-08 | James Beech | 2020-08-14 | Nelson Eichelberger
CTS-06 | CTS-06 | PI16964 | Verified | QEF13AA702; GT A Casing Cooling Air Supply Valve pressure regulator gauge lens cover is broken | B | I | Gonzalo Pena | McD | 2020-02-18 | Gonzalo Pena | Comm | 2020-02-20 | James Tanner | 2020-03-05 | Nelson Eichelberger
CTS-06 | CTS-06 | PI16965 | Verified | 1 inch drain valve installed outside of GT A Fuel Gas Purge Air Supply Enclosure is not shown on Mitsubishi drawing | D | P | Kelvin Cook | McD | 2020-02-18 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-03-11 | Keith Pollock
CTS-06 | CTS-06 | PI16966 | Verified | PDIT QEF13CP501; GT A Casing Cooling Air Fan Inlet Filter Pressure Differential Indicating Transmitter missing tag | C | P | Gonzalo Pena | McD | 2020-02-18 | Gonzalo Pena | Comm | 2020-02-20 | James Tanner | 2020-04-06 | Bernard Stasse
CTS-06 | CTS-06 | PI16967 | Verified | QEF13AT711; GT A Casing Cooling Air Fan Inlet Filter missing tag | C | P | Shane Crowe | McD | 2020-02-18 | Shane Crowe | Comm | 2020-03-19 | Shane Crowe | 2020-04-06 | Bernard Stasse
CTS-06 | CTS-06 | PI16968 | Verified | QEF13AN101; GT A Casing Cooling Air Fan missing tag | C | P | Shane Crowe | McD | 2020-02-18 | Shane Crowe | Comm | 2020-03-19 | Shane Crowe | 2020-04-06 | Bernard Stasse
CTS-06 | CTS-06 | PI16969 | Verified | QEF13AN101M01; GT A Casing Cooling Air Fan Motor missing tag | C | P | Shane Crowe | McD | 2020-02-18 | Shane Crowe | Comm | 2020-03-19 | Shane Crowe | 2020-04-06 | Bernard Stasse
CTS-06 | CTS-06 | PI16970 | Verified | QEF13AA711; GT A Casing Cooling Air Fan Damper missing tag | C | P | Shane Crowe | McD | 2020-02-18 | Shane Crowe | Comm | 2020-03-19 | Shane Crowe | 2020-04-06 | Bernard Stasse
CTS-07 | CTS-07 | PI01138 | Verified | 1BCTSK0051, Terminate Cable | A | E | Luis Cantu | McD | 2019-05-22 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-07-01 | Mike Tabbert
CTS-07 | CTS-07 | PI02602 | Verified | LK-1B-CTS-PD-P40-0120-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-14 | Lucas Foster
CTS-07 | CTS-07 | PI02603 | Verified | LK-1B-CTS-PD-P40-0120-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-29 | Terry Deaton | 2019-08-03 | Tom Noble
CTS-07 | CTS-07 | PI02604 | Verified | LK-1B-CTS-PD-P40-0140-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-29 | Bijo Varghese | 2019-08-29 | Bijo Varghese
CTS-07 | CTS-07 | PI02605 | Verified | LK-1B-CTS-PD-P40-0140-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-29 | Terry Deaton | 2019-08-03 | Tom Noble
CTS-07 | CTS-07 | PI02606 | Verified | LK-1B-CTS-PD-P40-0141-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-09-03 | Damon Turner | 2019-09-03 | Bijo Varghese
CTS-07 | CTS-07 | PI02607 | Verified | LK-1B-CTS-PD-P40-0141-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-29 | Bijo Varghese | 2019-08-29 | Bijo Varghese
CTS-07 | CTS-07 | PI02608 | Verified | LK-1B-CTS-PD-P40-0141-03 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-16 | Tom Noble
CTS-07 | CTS-07 | PI02609 | Verified | LK-1B-CTS-PD-P40-0206-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-12 | Tom Noble
CTS-07 | CTS-07 | PI02610 | Verified | LK-1B-CTS-PD-P40-0206-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-12 | Tom Noble
CTS-07 | CTS-07 | PI02611 | Verified | LK-1B-CTS-PD-P40-0308-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-12 | Tom Noble
CTS-07 | CTS-07 | PI02612 | Verified | LK-1B-CTS-PD-P40-0315-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const |  |  | 2019-08-12 | Tom Noble
CTS-07 | CTS-07 | PI02613 | Verified | LK-1B-CTS-PD-P41-0110-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-16 | Tom Noble
CTS-07 | CTS-07 | PI02614 | Verified | LK-1B-CTS-PD-P41-0116-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-14 | Lucas Foster
CTS-07 | CTS-07 | PI02615 | Verified | LK-1B-CTS-PD-P41-0215-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-20 | Tom Noble
CTS-07 | CTS-07 | PI02616 | Verified | LK-1B-CTS-PD-P41-0320-03 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-03 | Terry Deaton | 2019-08-03 | Tom Noble
CTS-07 | CTS-07 | PI02617 | Verified | LM-01377 (155126-110100-01-SD-000234) - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Tom Noble
CTS-07 | CTS-07 | PI02618 | Verified | LM-01377 (155126-110100-01-SD-000234) - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Tom Noble
CTS-07 | CTS-07 | PI02619 | Verified | LM-01380 (155126-110100-01-SD-000236) - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-08 | Tom Noble
CTS-07 | CTS-07 | PI03318 | Verified | LM-1357 - Torque all flanges and bend tags. After air blows. | B | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-18 | Kelvin Cook
CTS-07 | CTS-07 | PI03320 | Verified | LM-1367 - Install permanent gasket at turbine connection (bleed air). After air blows. | B | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
CTS-07 | CTS-07 | PI03321 | Verified | LM-1355 - All torqued flanges need 2nd tab bent over. After air blows. | B | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-18 | Kelvin Cook
CTS-07 | CTS-07 | PI03322 | Verified | LM-1379 - Complete installation of instrument air tubing in the gas turbine enclosure. | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-14 | Kelvin Cook
CTS-07 | CTS-07 | PI03323 | Verified | LM-1379 - Complete instrument air supports in the gas turbine enclosure. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-10-09 | Bobby Williams | 2019-10-19 | Kelvin Cook
CTS-07 | CTS-07 | PI03324 | Verified | LM-1357 - PS2 - loose u-bolt. | B | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-10-03 | Kelvin Cook
CTS-07 | CTS-07 | PI03325 | Verified | Ground all flanges at burners in gas turbine enclosure. After air blows. | B | E | Dustin Futrell | McD | 2019-08-07 | Dustin Futrell | Const |  |  | 2019-10-19 | Kelvin Cook
CTS-07 | CTS-07 | PI03326 | Verified | LM-1355 - 1BMBG03AA831 & 832 - Install flex hose. | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-20 | Kelvin Cook
CTS-07 | CTS-07 | PI03327 | Verified | LM-1353 - 1BMBG03AA821,822, 8223 & 824 - install both flex hoses. | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-20 | Kelvin Cook
CTS-07 | CTS-07 | PI03328 | Verified | LM-1357 - PS3 - Loose u-bolt. | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
CTS-07 | CTS-07 | PI03329 | Verified | LM-1357 - Blind flange is "cocked" - torque properly. Bottom LP drain connection. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-27 | Kelvin Cook
CTS-07 | CTS-07 | PI03330 | Verified | LM-1380 - 24A0A-PS1 - not welded. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-16 | Tom Noble
CTS-07 | CTS-07 | PI03331 | Verified | Instrument Air Receiver tank drain valve. Check if additional pipe run is needed. | B | P | Ron McMurtry | MHI | 2019-08-07 | Ron McMurtry | Const |  |  | 2019-12-19 | Kelvin Cook
CTS-07 | CTS-07 | PI03332 | Verified | 1380 - Restore system after pressure test. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-14 | Terry Deaton
CTS-07 | CTS-07 | PI03333 | Verified | Tag all Instrument Air skid components in the GT enclosure. | C | M | James Strange | MHI | 2019-08-07 | James Strange | Const | 2020-04-01 | James Strange | 2021-01-22 | Eric Policarpio
CTS-07 | CTS-07 | PI03334 | Verified | Tag all Seal Air skid components in the GT enclosure. | C | M | James Strange | McD | 2019-08-07 | James Strange | Const | 2020-04-09 | James Strange | 2021-01-22 | Eric Policarpio
CTS-07 | CTS-07 | PI03335 | Verified | LM-1365 - Install 2nd flex hose to LP control valve. | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-15 | Kelvin Cook
CTS-07 | CTS-07 | PI03336 | Verified | LM-1362 - Install instrument air tubing & flex hose to HP control valve. | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-15 | Kelvin Cook
CTS-07 | CTS-07 | PI03337 | Verified | LM-1364 - Install instrument air tubing & flex hose to HP control valve. | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-15 | Kelvin Cook
CTS-07 | CTS-07 | PI03338 | Verified | LM-1357 - Wrong gasket installed (spool 21A0D-22) | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-27 | Kelvin Cook
CTS-07 | CTS-07 | PI03339 | Verified | LM-1357 - Restore system properly after pressure test (spacer plate required). | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-27 | Kelvin Cook
CTS-07 | CTS-07 | PI03340 | Verified | LM-1359 - Restore system properly after pressure test (spacer plate required). | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-27 | Kelvin Cook
CTS-07 | CTS-07 | PI03341 | Verified | LM-1355 - Restore system properly after pressure test (spacer plate required). | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-26 | Terry Deaton | 2019-08-28 | Kelvin Cook
CTS-07 | CTS-07 | PI03342 | Verified | LM-1353 - Restore system properly after pressure test (spacer plate required). | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-26 | Terry Deaton | 2019-08-28 | Kelvin Cook
CTS-07 | CTS-07 | PI03343 | Verified | LM-1353 - Complete torque & bend tabs at the FGPA unit. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-26 | Terry Deaton | 2019-08-29 | Kelvin Cook
CTS-07 | CTS-07 | PI03344 | Verified | LM-1353 - Complete torque & bend tabs and ground flanges at the FGPA unit. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-26 | Terry Deaton | 2019-08-29 | Kelvin Cook
CTS-07 | CTS-07 | PI03345 | Verified | LM-1355 - Complete torque & bend tabs and ground flanges at the FGPA unit. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-26 | Terry Deaton | 2019-08-29 | Kelvin Cook
CTS-07 | CTS-07 | PI03346 | Verified | LM-1357 - Complete torque & bend tabs and ground flanges at the FGPA unit. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-26 | Terry Deaton | 2019-08-29 | Kelvin Cook
CTS-07 | CTS-07 | PI03347 | Verified | LM-1359 - Complete torque & bend tabs and ground flanges at the FGPA unit. | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-26 | Terry Deaton | 2019-08-29 | Kelvin Cook
CTS-07 | CTS-07 | PI03821 | Verified | Complete pipe test & submit CCFs to turnover. | A | P | James Beech | McD | 2019-08-13 | James Beech | Const | 2019-10-28 | Kelvin Cook | 2019-10-28 | Ed Gober
CTS-07 | CTS-07 | PI04997 | Verified | Complete IA pipe at the seal air skid - ground level east side. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-12-13 | Albert Burge
CTS-07 | CTS-07 | PI04998 | Verified | Ground flex to bleed air skid - ground level east side. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-15 | Fred Michael
CTS-07 | CTS-07 | PI04999 | Verified | Plug conduit at bleed air skid - ground level east side wall penetration. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Fred Michael | 2019-10-02 | Fred Michael
CTS-07 | CTS-07 | PI05000 | Verified | Complete IA at the bleed air skid - ground level west side. To flame detectors & ignitors. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-05 | Albert Burge
CTS-07 | CTS-07 | PI05001 | Verified | Missing plate & red hat on 1BMBY91GZ007 - ground level. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-09-25 | Damon Turner | 2019-10-16 | Albert Burge
CTS-07 | CTS-07 | PI05002 | Verified | Complete tubing on 1BMBY91GZ007 - ground level. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-05 | Albert Burge
CTS-07 | CTS-07 | PI05003 | Verified | Valve 1BMBH01AA701 - need tubing & bug screen - ground level. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-09-25 | Damon Turner | 2019-10-28 | Albert Burge
CTS-07 | CTS-07 | PI05004 | Verified | Ground the 2" flex - ground level south under turbine. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-15 | Fred Michael
CTS-07 | CTS-07 | PI05005 | Verified | 1BMBH03AA701 - hook up flex - ground level south. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-12-01 | Albert Burge
CTS-07 | CTS-07 | PI05006 | Verified | Hook up all flex hoses to ignitors. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-12-13 | Mike Tabbert
CTS-07 | CTS-07 | PI05007 | Verified | Grout all supports under the turbine. | C | C | Johnny Campbell | McD | 2019-09-12 | Johnny Campbell | Const | 2019-10-08 | Johnny Campbell | 2019-12-13 | Mike Tabbert
CTS-07 | CTS-07 | PI05008 | Verified | Ground cable tray - west side. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-10-04 | Richard Cruz | 2019-12-13 | Mike Tabbert
CTS-07 | CTS-07 | PI05009 | Verified | Ground bond the FGPA building. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-10-04 | Richard Cruz | 2019-12-13 | Mike Tabbert
CTS-07 | CTS-07 | PI05010 | Verified | Replace plastic plugs on transmitters in panels at both ends of the FGPA (upper level). | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-16 | Albert Burge
CTS-07 | CTS-07 | PI05011 | Verified | FGPA skid - Rain gutter on south side - self-tapping bolt is broken. | C | S | Tim Gallegos | McD | 2019-09-12 | Tim Gallegos | Const | 2020-01-06 | Tim Gallegos | 2020-02-27 | Michael Law
CTS-07 | CTS-07 | PI05012 | Verified | 1B-MBX01CP651 missing cover in FGPA. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-11-19 | James Tanner | 2019-11-21 | Albert Burge
CTS-07 | CTS-07 | PI05013 | Verified | Panels 1BMBY92GH031, 32 & 33 - clean inside panels - north side of FGPA. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Richard Cruz | 2019-11-20 | Fred Michael
CTS-07 | CTS-07 | PI05014 | Verified | 1B-MBP02CP101 in the FGPA - cannot operate manifold valve (interference). | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-11-13 | James Tanner | 2019-11-21 | Albert Burge
CTS-07 | CTS-07 | PI05015 | Verified | FGPA gas detector panel - ground seal tite. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-12-02 | Brad Stanford | 2019-12-13 | Mike Tabbert
CTS-07 | CTS-07 | PI05016 | Verified | FGPA gas detector panel - missing condulet covers. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Fred Michael | 2019-10-02 | Fred Michael
CTS-07 | CTS-07 | PI05017 | Verified | Panels 1BMBY92GH031, 32 & 33 - ground panels - north side of FGPA. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-05 | Richard Cruz | 2019-11-20 | Fred Michael
CTS-07 | CTS-07 | PI05018 | Verified | Panels 1BMBY92GH031, 32 & 33 - attach panduit covers - north side of FGPA. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Fred Michael | 2019-10-02 | Fred Michael
CTS-07 | CTS-07 | PI05019 | Verified | Panels 1BMBY92GH032 - ground conduit bushings - north side of FGPA. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-05 | Richard Cruz | 2019-11-20 | Fred Michael
CTS-07 | CTS-07 | PI05020 | Verified | Panels 1BMBY92GH031, & 33 - modify grounds in panels (2 grounds only per lug) - north side of FGPA. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-05 | Richard Cruz | 2019-11-20 | Fred Michael
CTS-07 | CTS-07 | PI05021 | Verified | Ground all seal tite in the turbine enclosure. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Fred Michael | 2019-10-02 | Fred Michael
CTS-07 | CTS-07 | PI05022 | Verified | Missing condulet covers in the turbine enclosure. | C | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-13 | Mike Tabbert
CTS-07 | CTS-07 | PI05023 | Verified | Screw on all TE covers in the turbine enclosure. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-13 | Mike Tabbert
CTS-07 | CTS-07 | PI05024 | Verified | Casing metal TE's not installed - upper turbine enclosure. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-28 | Albert Burge
CTS-07 | CTS-07 | PI05025 | Verified | Complete bearing #2 instrumentation. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-04 | Albert Burge
CTS-07 | CTS-07 | PI05026 | Verified | West side cable tray - ground tray. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05027 | Verified | West side cable tray - LLCs missing bolts. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Fred Michael | 2019-10-02 | Fred Michael
CTS-07 | CTS-07 | PI05028 | Verified | West side cable tray - missing tray splice connectors. Cut ty-wraps. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-15 | Fred Michael
CTS-07 | CTS-07 | PI05029 | Verified | Missing bug screens (5) for purge air valves in the FGPA | B | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-10-16 | Albert Burge
CTS-07 | CTS-07 | PI05030 | Verified | 1B-QEF14AA711KA01 - missing vented red hat in FGPA. | B | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-10-16 | Albert Burge
CTS-07 | CTS-07 | PI05031 | Verified | Run ground to ground plates on the FGPA skid. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Richard Cruz | 2019-10-15 | Fred Michael
CTS-07 | CTS-07 | PI05032 | Verified | 1BMBY92GH001-7 - clean interior & exterior. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-12 | Fred Michael
CTS-07 | CTS-07 | PI05033 | Verified | 1BMBY92GH001-7 - ground bushings. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-13 | Mike Tabbert
CTS-07 | CTS-07 | PI05034 | Verified | 1BMBY92GH001-7 - ground panel. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-06 | Richard Cruz | 2019-12-13 | Mike Tabbert
CTS-07 | CTS-07 | PI05035 | Verified | 1BMBY92GH001-7 - tighten seal tie connectors. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-15 | Fred Michael | 2019-10-15 | Fred Michael
CTS-07 | CTS-07 | PI05036 | Verified | 1BMBY92GH001-5, 6 & 7 - ty-wrap cables. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Fred Michael | 2019-10-02 | Fred Michael
CTS-07 | CTS-07 | PI05037 | Verified | 1BMBY92GH001-5, 6 & 7 - complete seal tite grounding. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Fred Michael | 2019-10-02 | Fred Michael
CTS-07 | CTS-07 | PI05038 | Verified | GT east side cable tray - needs grounding. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-06 | Richard Cruz | 2019-12-13 | Mike Tabbert
CTS-07 | CTS-07 | PI05040 | Verified | GT east side cable tray - straighten out cables in a neat & orderly manner. Ty-wrap. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-26 | Mike Tabbert | 2019-09-26 | Mike Tabbert
CTS-07 | CTS-07 | PI05041 | Verified | Complete air pipe to flame scanners. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-05 | Albert Burge
CTS-07 | CTS-07 | PI05281 | Verified | 1BCTSC0043, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05282 | Verified | 1BCTSC0044, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05283 | Verified | 1BCTSC0046, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05284 | Verified | 1BCTSC0047, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05285 | Verified | 1BCTS-CHC00GH001-DS120-C0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05286 | Verified | 1BCTSK0095, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
CTS-07 | CTS-07 | PI05287 | Verified | 1BCTSK0096, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
CTS-07 | CTS-07 | PI05288 | Verified | 1BCTSK0097, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05289 | Verified | 1BCTSK0132, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05290 | Verified | 1BCTSK0133, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05291 | Verified | 1BCTSK0134, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05292 | Verified | 1BCTSK0140, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05293 | Verified | 1BCTSK0141, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05294 | Verified | 1BCTSK0142, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05295 | Verified | 1BCTSK0143, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05296 | Verified | 1BCTSK0144, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05297 | Verified | 1BCTSK0145, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05298 | Verified | 1BCTSK0146, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05299 | Verified | 1BCTSK0147, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05300 | Verified | 1BCTSK0149, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05301 | Verified | 1BCTS-MBA13GH001-AC001-K0078, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05302 | Verified | 1BCTS-MBA13GH001-AC101-K0079, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05303 | Verified | 1BCTS-MBA13GH001-AC201-K0080, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05304 | Verified | 1BCTS-MBA13GH001-AC301-K0098, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05305 | Verified | 1BCTS-MBA13GH001-AC401-K0099, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05306 | Verified | 1BCTS-MBA13GH001-AC402-K0081, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05307 | Verified | 1BCTS-MBA13GH001-AC403-K0082, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05308 | Verified | 1BCTS-MKA01CY501-AS001-X0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05309 | Verified | 1BCTS-MKA01CY502-AS001-X0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05310 | Verified | 1BCTS-MKA01CY503-AS001-X0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05311 | Verified | 1BCTS-MKA01CY504-AS001-X0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CTS-07 | CTS-07 | PI05312 | Verified | 1BCTS-MKC01CY501-AS001-X0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05313 | Verified | 1BCTS-MKC01CY502-AS001-X0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05314 | Verified | 1BCTSX0109, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05315 | Verified | 1BCTSX0110, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05316 | Verified | 1BCTSX0111, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05317 | Verified | 1BCTSX0112, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05318 | Verified | 1BCTSX0113, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05319 | Verified | 1BCTSX0114, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05320 | Verified | 1BCTSX0160, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05321 | Verified | 1BCTSX0162, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05322 | Verified | 1BCTSX0164, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05323 | Verified | 1BCTSX0166, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05324 | Verified | 1BCTSX0168, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05325 | Verified | 1BCTSX0180, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05326 | Verified | 1BCTSX0182, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05327 | Verified | 1BCTSX0184, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05328 | Verified | 1BCTSX0185, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05329 | Verified | 1BCTSX0186, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05330 | Verified | 1BCTSX0187, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05331 | Verified | 1BCTSX0188, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05332 | Verified | 1BCTSX0190, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05333 | Verified | 1BCTSX0201, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05334 | Verified | 1BCTSX0203, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05335 | Verified | 1BCTSX0207, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05336 | Verified | 1BCTSX0208, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05337 | Verified | 1BCTSX0212, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05338 | Verified | 1BCTSX0217, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05339 | Verified | 1BCTSX0233, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05340 | Verified | 1BCTSX0234, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CTS-07 | CTS-07 | PI05341 | Verified | 1BCTSX0322, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05342 | Verified | 1BCTSX0329, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05343 | Verified | 1BCTSX0330, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05344 | Verified | 1BCTSX0334, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05345 | Verified | 1BCTSX0335, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05346 | Verified | 1BCTSX0363, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05347 | Verified | 1BCTSC0043, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05348 | Verified | 1BCTSC0044, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05349 | Verified | 1BCTSC0046, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05350 | Verified | 1BCTSC0047, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05351 | Verified | 1BCTSC0172, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05352 | Verified | 1BCTSC0173, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05353 | Verified | 1BCTSC0200, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05354 | Verified | 1BCTSC0204, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CTS-07 | CTS-07 | PI05355 | Verified | 1BCTSC0210, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CTS-07 | CTS-07 | PI05356 | Verified | 1BCTSC0211, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05357 | Verified | 1BCTSC0214, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CTS-07 | CTS-07 | PI05358 | Verified | 1BCTSC0258, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05359 | Verified | 1BCTSC0259, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05360 | Verified | 1BCTSC0260, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05361 | Verified | 1BCTSC0265, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05362 | Verified | 1BCTSC0266, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05363 | Verified | 1BCTSC0267, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05364 | Verified | 1BCTSC0268, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-20 | Albert Burge
CTS-07 | CTS-07 | PI05365 | Verified | 1BCTSC0269, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05366 | Verified | 1BCTSC0270, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05367 | Verified | 1BCTSC0271, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05368 | Verified | 1BCTSC0272, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05369 | Verified | 1BCTSC0273, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05370 | Verified | 1BCTSC0274, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05371 | Verified | 1BCTSC0320, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05372 | Verified | 1BCTSC0324, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05373 | Verified | 1BCTSC0328, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05374 | Verified | 1BCTSC0329, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05375 | Verified | 1BCTSC0336, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05376 | Verified | 1BCTSC0340, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05377 | Verified | 1BCTSC0346, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05378 | Verified | 1BCTSC0356, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05379 | Verified | 1BCTSC0357, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05380 | Verified | 1BCTSC0359, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05381 | Verified | 1BCTS-CHC00GH001-DS003-C0001, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05382 | Verified | 1BCTS-CHC00GH001-DS120-C0001, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05383 | Verified | 1BCTS-CKC00GH001-DC001-K0003, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05384 | Verified | 1BCTSK0021, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05385 | Verified | 1BCTSK0023, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05386 | Verified | 1BCTSK0038, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05387 | Verified | 1BCTSK0040, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05388 | Verified | 1BCTSK0052, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05389 | Verified | 1BCTSK0054, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05390 | Verified | 1BCTSK0056, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-24 | Michael Law | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05391 | Verified | 1BCTSK0057, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05392 | Verified | 1BCTSK0068, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05393 | Verified | 1BCTSK0072, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05394 | Verified | 1BCTSK0095, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CTS-07 | CTS-07 | PI05395 | Verified | 1BCTSK0096, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CTS-07 | CTS-07 | PI05396 | Verified | 1BCTSK0097, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CTS-07 | CTS-07 | PI05397 | Verified | 1BCTSK0098, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05398 | Verified | 1BCTSK0111, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05399 | Verified | 1BCTSK0113, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05400 | Verified | 1BCTSK0114, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05401 | Verified | 1BCTSK0115, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05402 | Verified | 1BCTSK0116, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05403 | Verified | 1BCTSK0120, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05404 | Verified | 1BCTSK0121, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05405 | Verified | 1BCTSK0122, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05406 | Verified | 1BCTSK0124, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05407 | Verified | 1BCTSK0132, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05408 | Verified | 1BCTSK0133, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05409 | Verified | 1BCTSK0134, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05410 | Verified | 1BCTSK0140, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05411 | Verified | 1BCTSK0141, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05412 | Verified | 1BCTSK0142, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05413 | Verified | 1BCTSK0143, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05414 | Verified | 1BCTSK0144, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05415 | Verified | 1BCTSK0145, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05416 | Verified | 1BCTSK0146, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05417 | Verified | 1BCTSK0147, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05418 | Verified | 1BCTSK0149, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05419 | Verified | 1BCTS-MBA13GH001-AC001-K0078, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05420 | Verified | 1BCTS-MBA13GH001-AC101-K0079, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05421 | Verified | 1BCTS-MBA13GH001-AC201-K0080, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05422 | Verified | 1BCTS-MBA13GH001-AC301-K0098, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05423 | Verified | 1BCTS-MBA13GH001-AC401-K0099, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Martin Perry
CTS-07 | CTS-07 | PI05424 | Verified | 1BCTS-MBA13GH001-AC402-K0081, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05425 | Verified | 1BCTS-MBA13GH001-AC403-K0082, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05426 | Verified | 1BCTS-MKA01CY501-AS001-X0001, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05427 | Verified | 1BCTS-MKA01CY502-AS001-X0001, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05428 | Verified | 1BCTS-MKA01CY503-AS001-X0001, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05429 | Verified | 1BCTS-MKA01CY504-AS001-X0001, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Johnson
CTS-07 | CTS-07 | PI05430 | Verified | 1BCTS-MKC01CY501-AS001-X0001, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05431 | Verified | 1BCTS-MKC01CY502-AS001-X0001, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05432 | Verified | 1BCTSX0109, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Mike Tabbert | 2019-10-02 | Mike Tabbert
CTS-07 | CTS-07 | PI05433 | Verified | 1BCTSX0110, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Mike Tabbert | 2019-10-02 | Mike Tabbert
CTS-07 | CTS-07 | PI05434 | Verified | 1BCTSX0111, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05435 | Verified | 1BCTSX0112, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05436 | Verified | 1BCTSX0113, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05437 | Verified | 1BCTSX0114, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05438 | Verified | 1BCTSX0150, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05439 | Verified | 1BCTSX0160, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05440 | Verified | 1BCTSX0162, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05441 | Verified | 1BCTSX0164, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05442 | Verified | 1BCTSX0166, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05443 | Verified | 1BCTSX0168, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05444 | Verified | 1BCTSX0172, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05445 | Verified | 1BCTSX0180, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05446 | Verified | 1BCTSX0181, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05447 | Verified | 1BCTSX0182, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05448 | Verified | 1BCTSX0184, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05449 | Verified | 1BCTSX0185, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05450 | Verified | 1BCTSX0186, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05451 | Verified | 1BCTSX0187, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05452 | Verified | 1BCTSX0188, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05453 | Verified | 1BCTSX0190, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05454 | Verified | 1BCTSX0201, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05455 | Verified | 1BCTSX0203, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI05456 | Verified | 1BCTSX0207, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05457 | Verified | 1BCTSX0208, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05458 | Verified | 1BCTSX0212, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05459 | Verified | 1BCTSX0217, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05460 | Verified | 1BCTSX0230, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05461 | Verified | 1BCTSX0231, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05462 | Verified | 1BCTSX0232, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05463 | Verified | 1BCTSX0233, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Mike Tabbert | 2019-10-02 | Mike Tabbert
CTS-07 | CTS-07 | PI05464 | Verified | 1BCTSX0245, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05465 | Verified | 1BCTSX0260, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05466 | Verified | 1BCTSX0261, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05467 | Verified | 1BCTSX0262, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05468 | Verified | 1BCTSX0263, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05469 | Verified | 1BCTSX0264, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05470 | Verified | 1BCTSX0265, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05471 | Verified | 1BCTSX0266, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05472 | Verified | 1BCTSX0267, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05473 | Verified | 1BCTSX0271, From Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
CTS-07 | CTS-07 | PI05474 | Verified | 1BCTSX0272, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05475 | Verified | 1BCTSX0275, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05476 | Verified | 1BCTSX0284, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05477 | Verified | 1BCTSX0285, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05478 | Verified | 1BCTSX0292, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05479 | Verified | 1BCTSX0294, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05480 | Verified | 1BCTSX0307, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05481 | Verified | 1BCTSX0322, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05482 | Verified | 1BCTSX0325, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05483 | Verified | 1BCTSX0327, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Michael Law | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05484 | Verified | 1BCTSX0328, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05485 | Verified | 1BCTSX0329, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05486 | Verified | 1BCTSX0330, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05487 | Verified | 1BCTSX0331, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05488 | Verified | 1BCTSX0332, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Michael Law | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05489 | Verified | 1BCTSX0334, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05490 | Verified | 1BCTSX0335, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05491 | Verified | 1BCTSX0336, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05492 | Verified | 1BCTSX0337, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05493 | Verified | 1BCTSX0338, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05494 | Verified | 1BCTSX0356, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05495 | Verified | 1BCTSX0357, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05496 | Verified | 1BCTSX0363, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05497 | Verified | 1BCTSX0364, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05498 | Verified | 1BCTSX0365, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05499 | Verified | 1BCTSX0366, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05500 | Verified | 1BCTSX0367, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05501 | Verified | 1BCTSX0377, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05502 | Verified | 1BCTSX0378, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05503 | Verified | 1BCTSX0379, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05504 | Verified | 1BCTSX0380, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05505 | Verified | 1BCTSX0381, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05506 | Verified | 1BCTSX0382, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05507 | Verified | 1BCTSX0408, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05508 | Verified | 1BCTSX0412, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05509 | Verified | 1BCTSX0419, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05510 | Verified | 1BCTSX0422, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05511 | Verified | 1BCTSX0423, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05512 | Verified | 1BCTSX0424, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05513 | Verified | 1BCTSX0425, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05514 | Verified | 1BCTSX0440, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05515 | Verified | 1+A32:A311BCTSC0024, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05516 | Verified | 1BCTSC0025, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05517 | Verified | 1BCTSC0043, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05518 | Verified | 1BCTSC0044, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05519 | Verified | 1BCTSC0046, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05520 | Verified | 1BCTSC0047, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05521 | Verified | 1BCTSC0121, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05522 | Verified | 1BCTSC0123, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05523 | Verified | 1BCTSC0124, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05524 | Verified | 1BCTSC0130, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CTS-07 | CTS-07 | PI05525 | Verified | 1BCTSC0133, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05526 | Verified | 1BCTSC0136, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05527 | Verified | 1BCTSC0139, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05528 | Verified | 1BCTSC0142, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05529 | Verified | 1BCTSC0143, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05530 | Verified | 1BCTSC0144, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05531 | Verified | 1BCTSC0145, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05532 | Verified | 1BCTSC0146, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05533 | Verified | 1BCTSC0173, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05534 | Verified | 1BCTSC0208, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05535 | Verified | 1BCTSC0211, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05536 | Verified | 1BCTSC0214, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CTS-07 | CTS-07 | PI05537 | Verified | 1BCTSC0325, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CTS-07 | CTS-07 | PI05538 | Verified | 1BCTSC0329, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05539 | Verified | 1BCTSC0336, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05540 | Verified | 1BCTSC0346, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05541 | Verified | 1BCTSC0357, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05542 | Verified | 1BCTSC0359, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05543 | Verified | 1BCTS-CHC00GH001-DS003-C0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05544 | Verified | 1BCTS-CHC00GH001-DS120-C0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Johnson
CTS-07 | CTS-07 | PI05545 | Verified | 1BCTS-CKC00GH001-DC001-K0003, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05546 | Verified | 1BCTSK0017, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05547 | Verified | 1BCTSK0038, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05548 | Verified | 1BCTSK0040, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05549 | Verified | 1BCTSK0068, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05550 | Verified | 1BCTSK0072, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05551 | Verified | 1BCTSK0095, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CTS-07 | CTS-07 | PI05552 | Verified | 1BCTSK0096, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CTS-07 | CTS-07 | PI05553 | Verified | 1BCTSK0097, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05554 | Verified | 1BCTSK0098, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-23 | Michael Law
CTS-07 | CTS-07 | PI05555 | Verified | 1BCTSK0115, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05556 | Verified | 1BCTSK0116, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05557 | Verified | 1BCTSK0120, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05558 | Verified | 1BCTSK0121, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05559 | Verified | 1BCTSK0122, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05560 | Verified | 1BCTSK0124, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05561 | Verified | 1BCTSK0132, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05562 | Verified | 1BCTSK0133, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05563 | Verified | 1BCTSK0134, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05564 | Verified | 1BCTSK0140, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05565 | Verified | 1BCTSK0141, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05566 | Verified | 1BCTSK0142, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05567 | Verified | 1BCTSK0143, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05568 | Verified | 1BCTSK0144, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05569 | Verified | 1BCTSK0145, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05570 | Verified | 1BCTSK0146, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05571 | Verified | 1BCTSK0147, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05572 | Verified | 1BCTSK0149, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05573 | Verified | 1BCTS-MBA13GH001-AC001-K0078, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05574 | Verified | 1BCTS-MBA13GH001-AC101-K0079, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05575 | Verified | 1BCTS-MBA13GH001-AC201-K0080, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05576 | Verified | 1BCTS-MBA13GH001-AC301-K0098, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05577 | Verified | 1BCTS-MBA13GH001-AC401-K0099, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05578 | Verified | 1BCTS-MBA13GH001-AC402-K0081, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05579 | Verified | 1BCTS-MBA13GH001-AC403-K0082, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05580 | Verified | 1BCTS-MKA01CY501-AS001-X0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05581 | Verified | 1BCTS-MKA01CY502-AS001-X0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05582 | Verified | 1BCTS-MKA01CY503-AS001-X0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05583 | Verified | 1BCTS-MKA01CY504-AS001-X0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05584 | Verified | 1BCTS-MKC01CY501-AS001-X0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05585 | Verified | 1BCTS-MKC01CY502-AS001-X0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05586 | Verified | 1BCTSX0109, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05587 | Verified | 1BCTSX0110, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05588 | Verified | 1BCTSX0111, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05589 | Verified | 1BCTSX0112, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05590 | Verified | 1BCTSX0113, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05591 | Verified | 1BCTSX0114, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05592 | Verified | 1BCTSX0129, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05593 | Verified | 1BCTSX0136, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05594 | Verified | 1BCTSX0137, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05595 | Verified | 1BCTSX0143, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05596 | Verified | 1BCTSX0150, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05597 | Verified | 1BCTSX0151, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Johnson
CTS-07 | CTS-07 | PI05598 | Verified | 1BCTSX0152, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05599 | Verified | 1BCTSX0153, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05600 | Verified | 1BCTSX0160, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05601 | Verified | 1BCTSX0161, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-24 | Michael Law | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05602 | Verified | 1BCTSX0162, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05603 | Verified | 1BCTSX0163, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05604 | Verified | 1BCTSX0164, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
CTS-07 | CTS-07 | PI05605 | Verified | 1BCTSX0165, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05606 | Verified | 1BCTSX0166, To Termination | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05607 | Verified | 1BCTSX0167, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05608 | Verified | 1BCTSX0168, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
CTS-07 | CTS-07 | PI05609 | Verified | 1BCTSX0169, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-25 | Michael Law | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05610 | Verified | 1BCTSX0172, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05611 | Verified | 1BCTSX0174, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05612 | Verified | 1BCTSX0175, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05613 | Verified | 1BCTSX0176, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05614 | Verified | 1BCTSX0177, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05615 | Verified | 1BCTSX0178, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05616 | Verified | 1BCTSX0179, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05617 | Verified | 1BCTSX0180, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05618 | Verified | 1BCTSX0182, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05619 | Verified | 1BCTSX0183, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05620 | Verified | 1BCTSX0184, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05621 | Verified | 1BCTSX0185, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CTS-07 | CTS-07 | PI05622 | Verified | 1BCTSX0186, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05623 | Verified | 1BCTSX0187, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05624 | Verified | 1BCTSX0188, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05625 | Verified | 1BCTSX0189, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05626 | Verified | 1BCTSX0190, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05627 | Verified | 1BCTSX0191, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05628 | Verified | 1BCTSX0192, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05629 | Verified | 1BCTSX0197, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05630 | Verified | 1BCTSX0200, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05631 | Verified | 1BCTSX0201, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05632 | Verified | 1BCTSX0202, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05633 | Verified | 1BCTSX0203, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05634 | Verified | 1BCTSX0204, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05635 | Verified | 1BCTSX0206, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05636 | Verified | 1BCTSX0207, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05637 | Verified | 1BCTSX0208, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05638 | Verified | 1BCTSX0212, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05639 | Verified | 1BCTSX0215, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05640 | Verified | 1BCTSX0217, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05641 | Verified | 1BCTSX0218, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05642 | Verified | 1BCTSX0219, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05643 | Verified | 1BCTSX0220, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05644 | Verified | 1BCTSX0223, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05645 | Verified | 1BCTSX0225, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05646 | Verified | 1BCTSX0229, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05647 | Verified | 1BCTSX0230, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05648 | Verified | 1BCTSX0232, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05649 | Verified | 1BCTSX0233, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05650 | Verified | 1BCTSX0234, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05651 | Verified | 1BCTSX0238, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05652 | Verified | 1BCTSX0239, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05653 | Verified | 1BCTSX0240, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05654 | Verified | 1BCTSX0241, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05655 | Verified | 1BCTSX0245, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-25 | Michael Law
CTS-07 | CTS-07 | PI05656 | Verified | 1BCTSX0246, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05657 | Verified | 1BCTSX0247, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05658 | Verified | 1BCTSX0248, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05659 | Verified | 1BCTSX0252, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
CTS-07 | CTS-07 | PI05660 | Verified | 1BCTSX0253, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
CTS-07 | CTS-07 | PI05661 | Verified | 1BCTSX0254, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
CTS-07 | CTS-07 | PI05662 | Verified | 1BCTSX0256, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
CTS-07 | CTS-07 | PI05663 | Verified | 1BCTSX0257, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
CTS-07 | CTS-07 | PI05664 | Verified | 1BCTSX0258, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
CTS-07 | CTS-07 | PI05665 | Verified | 1BCTSX0259, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-24 | Michael Law | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05666 | Verified | 1BCTSX0260, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
CTS-07 | CTS-07 | PI05667 | Verified | 1BCTSX0261, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
CTS-07 | CTS-07 | PI05668 | Verified | 1BCTSX0262, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
CTS-07 | CTS-07 | PI05669 | Verified | 1BCTSX0263, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
CTS-07 | CTS-07 | PI05670 | Verified | 1BCTSX0264, To Termination | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-26 | Chris Caywood
CTS-07 | CTS-07 | PI05671 | Verified | 1BCTSX0265, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
CTS-07 | CTS-07 | PI05672 | Verified | 1BCTSX0266, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
CTS-07 | CTS-07 | PI05673 | Verified | 1BCTSX0267, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05674 | Verified | 1BCTSX0269, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05675 | Verified | 1BCTSX0270, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05676 | Verified | 1BCTSX0271, To Termination | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05677 | Verified | 1BCTSX0272, To Termination | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-20 | Mike Tabbert
CTS-07 | CTS-07 | PI05678 | Verified | 1BCTSX0274, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05679 | Verified | 1BCTSX0283, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05680 | Verified | 1BCTSX0322, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05681 | Verified | 1BCTSX0324, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05682 | Verified | 1BCTSX0325, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05683 | Verified | 1BCTSX0327, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05684 | Verified | 1BCTSX0329, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05685 | Verified | 1BCTSX0330, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05686 | Verified | 1BCTSX0331, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
CTS-07 | CTS-07 | PI05687 | Verified | 1BCTSX0334, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05688 | Verified | 1BCTSX0335, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05689 | Verified | 1BCTSX0338, To Terminationv | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05690 | Verified | 1BCTSX0346, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-11 | Brad Stanford | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05691 | Verified | 1BCTSX0355, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05692 | Verified | 1BCTSX0356, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-07 | CTS-07 | PI05693 | Verified | 1BCTSX0357, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05694 | Verified | 1BCTSX0358, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05695 | Verified | 1BCTSX0359, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05696 | Verified | 1BCTSX0360, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05697 | Verified | 1BCTSX0361, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05698 | Verified | 1BCTSX0362, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05699 | Verified | 1BCTSX0363, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
CTS-07 | CTS-07 | PI05700 | Verified | 1BCTSX0364, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05701 | Verified | 1BCTSX0367, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-07 | CTS-07 | PI05702 | Verified | 1BCTSX0380, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05703 | Verified | 1BCTSX0382, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05704 | Verified | 1BCTSX0411, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05705 | Verified | 1BCTSX0412, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05706 | Verified | 1BCTSX0419, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-11 | Brad Stanford | 2019-11-14 | Mike Tabbert
CTS-07 | CTS-07 | PI05707 | Verified | 1BCTSX0425, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CTS-07 | CTS-07 | PI05708 | Verified | 1BCTSX0440, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-07 | CTS-07 | PI05709 | Verified | MBA11AN101M01, GT Package Ventilation Fan (A), Install conduit , seatight and grounding for motor feed | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Richard Cruz | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05710 | Verified | MBA11AN102M01, GT Package Ventilation Fan (B), Install conduit , seatight and grounding for motor feed | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Richard Cruz | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05711 | Verified | MBA11AN103M01, GT Package Ventilation Fan (C), Install conduit , seatight and grounding for motor feed | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-13 | Richard Cruz | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05712 | Verified | MBY91GZ012, Gas Detector Panel For GT Package, install conduit , sealtight and grounding for siginal cable. (MBA11CQ001, 002 and 003) | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-05 | Richard Cruz | 2019-12-13 | Mike Tabbert
CTS-07 | CTS-07 | PI05713 | Verified | MBY91GZ013, Instrument Panel Exhaust Gas Duct Pressure, Install tubing. (MBR01CP102, 103 and 104) | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-09-13 | Gonzalo Pena | 2019-09-18 | Mike Tabbert
CTS-07 | CTS-07 | PI05714 | Verified | MBY91GZ013, Instrument Panel Exhaust GasDuct Pressure, install conduit, sealtight and grounding for siginal cable.(MBR01CP102, 103 and 104) | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-05 | Richard Cruz | 2019-11-23 | Michael Law
CTS-07 | CTS-07 | PI05715 | Verified | MBY91GZ011, Instrument Panel GT Package Ventilation Fan Diff. Pressure, Install tubing. (MBA11CP501, 502 and 503) | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-11-23 | Michael Law
CTS-07 | CTS-07 | PI05716 | Verified | MBY91GZ011, Instrument Panel GT Package Ventilation Fan Diff. Pressure, install conduit, sealtight and grounding for signal cable. (MBA11CP501, 502 and 503) | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-05 | Richard Cruz | 2019-11-23 | Michael Law
CTS-07 | CTS-07 | PI05717 | Verified | MBY91GZ014, Gas Detector Panel For GT Exhaust Gas Duct, Install tubing. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-23 | Michael Law
CTS-07 | CTS-07 | PI05718 | Verified | MBY91GZ014, Gas Detector Panel For GT Exhaust Gas Duct, Install Conduit, Install sealtight and grounding for siginal cable. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-05 | Richard Cruz | 2019-11-23 | Michael Law
CTS-07 | CTS-07 | PI05719 | Verified | MBY91GZ016 Panel, MBA11CQ004, Gas Detector for Fuel Gas Unit, Install tubing. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-09-13 | Gonzalo Pena | 2019-09-28 | Mike Tabbert
CTS-07 | CTS-07 | PI05720 | Verified | MBY91GZ016 Panel, MBA11CQ004, Gas Detector for Fuel Gas Unit, Install conduit, install sealtight and grounding for siginal cable. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-07 | CTS-07 | PI09316 | Verified | 1B-LM-01364-49 - FW3 Needs Repair. | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const |  |  | 2019-10-29 | Tom Noble
CTS-07 | CTS-07 | PI09317 | Verified | 1B-LM-01365-50 - FW1 Needs Repair. | A | P | Bobby Williams | McD | 2019-10-08 | Bobby Williams | Const |  |  | 2019-10-29 | Tom Noble
CTS-07 | CTS-07 | PI09788 | Verified | Test Package CTS-T-1B-AF08 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
CTS-07 | CTS-07 | PI12855 | Verified | Install one-pulse probe. | B | I | Richard Cummings | MHI | 2019-11-08 | Richard Cummings | Const | 2020-01-10 | Michael Law | 2020-02-10 | Fred Michael
CTS-07 | CTS-07 | PI12856 | Verified | Install speed probes. | B | I | Richard Cummings | MHI | 2019-11-08 | Richard Cummings | Const | 2020-01-10 | Michael Law | 2020-02-27 | Michael Law
CTS-07 | CTS-07 | PI12862 | Verified | FG Main A Ring Header replace valve MBP03AA824 | A | P | Bobby Williams | McD | 2019-11-11 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-13 | Kelvin Cook
CTS-07 | CTS-07 | PI12863 | Verified | FG Main B Ring Header replace valve MBP03AA832 and MBP03AA834 | A | P | Bobby Williams | McD | 2019-11-11 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-13 | Kelvin Cook
CTS-07 | CTS-07 | PI12867 | Verified | Missing stud bolts at 2 connections at the EVAP COOLER | A | P | Bobby Williams | McD | 2019-11-11 | Bobby Williams | Const |  |  | 2019-11-20 | Michael Law
CTS-07 | CTS-07 | PI13140 | Verified | Replace casing cooling valve actuator | A | P | Bobby Williams | McD | 2019-11-18 | Bobby Williams | Const |  |  | 2019-11-19 | Ed Gober
CTS-07 | CTS-07 | PI13141 | Verified | Replace casing cooling air valve actuator. | A | P | Bobby Williams | McD | 2019-11-18 | Bobby Williams | Const |  |  | 2019-11-25 | Michael Law
CTS-07 | CTS-07 | PI14406 | Verified | Install performance test equipment | B | M | James Strange | MHI | 2019-12-06 | James Strange | Const |  |  | 2020-02-18 | Michael Law
CTS-07 | CTS-07 | PI14407 | Verified | Inspect Inlet (filters to inlet scroll) | B | M | James Strange | MHI | 2019-12-06 | James Strange | Const |  |  | 2020-02-07 | James Strange
CTS-07 | CTS-07 | PI14408 | Verified | Inspect exhaust | B | M | James Strange | MHI | 2019-12-06 | James Strange | Const |  |  | 2020-02-07 | James Strange
CTS-07 | CTS-07 | PI14409 | Verified | Re-tourque exhaust expansion joint bolts (EE-01) | B | M | Shane Crowe | McD | 2019-12-06 | Shane Crowe | Const | 2020-02-06 | Shane Crowe | 2020-02-27 | Michael Law
CTS-07 | CTS-07 | PI14410 | Verified | Inspect fuel gas inlet filter | B | M | James Strange | MHI | 2019-12-06 | James Strange | Const |  |  | 2020-02-07 | James Strange
CTS-07 | CTS-07 | PI14411 | Verified | Inspect temporary fuel gas strainers | B | M | James Strange | MHI | 2019-12-06 | James Strange | Const |  |  | 2020-02-07 | James Strange
CTS-07 | CTS-07 | PI14412 | Verified | Complete TCA piping modification | B | M | James Strange | MHI | 2019-12-06 | James Strange | Const |  |  | 2020-02-18 | Michael Law
CTS-07 | CTS-07 | PI15563 | Verified | 1B Generator Neutral Grounding for CTG - The bottom conduit cover is missing one (1) bolt, and the top conduit cover is completely missing bolts. This needs to be addressed before the unit is spun to purge speed. | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-02-28 | Chris Colvin | 2020-02-28 | John Watts
CTS-07 | CTS-07 | PI17311 | Verified | Clean up inside GT B enclosure, remove tools, scaffolding, and materials | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-03-26 | John Watts
CTS-07 | CTS-07 | PI17360 | Verified | 1B-MBP02CP634 - 1B-GT_FG_CV Positioner filter cartridges are leaking around threads | B | I | Lonnie Peters | McD | 2020-02-28 | Lonnie Peters | Comm | 2020-03-26 | William Mitchell | 2020-04-17 | John Watts
CTS-07 | CTS-07 | PI17658 | Verified | 1BMBA13SS101 (GT Control Package A) HVAC Unit 1BMBA13AH102, there is a major leak at the wall where the HVAC unit and the Control Package connect. The top ledge/lip that seals the AC to the control package building is bent back from the building allowing a lot of moisture in the Control Package. The water goes through the opening and is blown into the building by the HVAC. As a result, water is on the floor and condensation is forming inside the GT Control Panel, MBY01GH001-008. The closer to the leak, the worse the condensation is in the cabinet. The McDermott crew working inside the building have put desiccant sacks in the cabinets as well as wiping the cabinets with clean rags but the condensation is still severe. | C | S | Tim Gallegos | McD | 2020-03-04 | Tim Gallegos | Comm | 2020-05-18 | Tim Gallegos | 2021-01-15 | Dave Goldak
CTS-07 | CTS-07 | PI17684 | Verified | 1B GT - right side of inlet plenum lower level, inlet intrument sensing line is rubbing on an angle iron support frame. | C | P | James Beech | McD | 2020-03-04 | James Beech | Comm | 2020-05-08 | James Beech | 2021-05-07 | John Watts
CTS-07 | CTS-07 | PI17686 | Verified | 1B GT - small bore piping and electrical conduit create triping hazard. Ground floor of turbine compartment. | D | P | Michael Law | McD | 2020-03-04 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-01-05 | Keith Pollock
CTS-07 | CTS-07 | PI17687 | Verified | 1B GT - there is an oil leak on the inlet bearing drain line. Plenum flanges have visible oil dripping to the floor. | B | M | William Mitchell | McD | 2020-03-04 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-10 | John Watts
CTS-07 | CTS-07 | PI17689 | Verified | 1B GT - Conduit LB covers are missing or swung out of the way. Turbine comparment. | C | E | Chris Colvin | McD | 2020-03-04 | Chris Colvin | Comm | 2020-07-14 | Matt Gilmore | 2021-05-07 | John Watts
CTS-07 | CTS-07 | PI17697 | Verified | 1B GT - Construction debris and combustible material in compartment needs to be removed. | B | C | Alan Huntsman | McD | 2020-03-04 | Alan Huntsman | Comm | 2020-03-12 | Alan Huntsman | 2021-04-21 | John Watts
CTS-07 | CTS-07 | PI17826 | Verified | 87G-1B-1 / Generator Protection Relay (DPR 1) - There's a target on this NERC relay. | C | E | Jonathan Donham | McD | 2020-03-16 | Jonathan Donham | Const | 2020-03-31 | Jonathan Donham | 2020-06-04 | Donovan Anderson
CTS-07 | CTS-07 | PI18114 | Verified | 1B-CTS-MBH05AT101, 1B-CTS-MBH05AC301 - The clearance between the Gas Turbine Cooling Air Filter and the TCA Cooler Feedwater inlet is small. | D | M | Michael Law | McD | 2020-03-20 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-01-05 | Keith Pollock
CTS-07 | CTS-07 | PI18174 | Verified | Mitsubishi commissioning paper work to submit after tuning and final testing are complete | C | M | James Strange | MHI | 2020-03-23 | James Strange | Comm | 2020-06-23 | James Strange | 2020-06-23 | Mike Tabbert
CTS-08 | CTS-08 | PI00514 | Verified | Complete grouting of all columns at Excitation foundation for Utility Rack. | B | C | Jessie Pipes | McD | 2019-04-05 | Jessie Pipes | Const | 2019-04-12 | Neil Simon | 2019-04-12 | Neil Simon
CTS-08 | CTS-08 | PI00528 | Verified | 1BYVAC0101, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-06-07 | Mike Tabbert | 2019-06-07 | Mike Tabbert
CTS-08 | CTS-08 | PI07462 | Verified | Need condulet drain near H2 skid | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-09 | Albert Burge
CTS-08 | CTS-08 | PI07463 | Verified | Bonding juumper on flanges off water detector / oil drain level, north and south end, ender turning gear | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-09 | Albert Burge
CTS-08 | CTS-08 | PI07464 | Verified | Generator protection panel - pour seal off conduit | B | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-09 | Michael Law
CTS-08 | CTS-08 | PI07465 | Verified | 1B-CTS-XFM-0001 - cable box north side to bolt | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-08 | CTS-08 | PI07466 | Verified | 1B-CTS-XFM-0001 - paint welding on transformer stand | C | X | Jerry Smith | McD | 2019-09-27 | Jerry Smith | Const | 2020-03-07 | Matt Gilmore | 2020-03-09 | Mike Tabbert
CTS-08 | CTS-08 | PI07467 | Verified | 1B-CTS-XFM-0001 - complete the hook up of ground to grid | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-08 | CTS-08 | PI07468 | Verified | 1B-CTS-XFM-0001 - loose bolts on AC bus transformer going to the exciter building | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-09-28 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CTS-08 | CTS-08 | PI07469 | Verified | Exciter building - complete bus installation near to the building | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-09-28 | Dustin Futrell | 2019-11-06 | Fred Michael
CTS-08 | CTS-08 | PI07470 | Verified | Exciter building - complete the grounding of DC exciter bus | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-09-28 | Dustin Futrell | 2019-11-06 | Fred Michael
CTS-08 | CTS-08 | PI07471 | Verified | Exciter building -install fixtures | B | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2020-03-10 | Chris Colvin | 2020-04-21 | Michael Law
CTS-08 | CTS-08 | PI07472 | Verified | Isophase tap box to complete grounding. To complete grounding on all flex | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-11-06 | Fred Michael
CTS-08 | CTS-08 | PI07473 | Verified | Turbine Generator - RTD 2 and 3 are not installed | B | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-11-21 | Albert Burge
CTS-08 | CTS-08 | PI07474 | Verified | Turbine Generator - complete instrumentation on bearing 3, 4, 5 | B | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-11-21 | Albert Burge
CTS-08 | CTS-08 | PI07475 | Verified | Turbine Generator - Mitsubishi cables to complete north east side of the generator | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-11-06 | Fred Michael
CTS-08 | CTS-08 | PI07476 | Verified | Turbine Generator - Mitsubishi to complete heater installation | A | E | Dustin Futrell | MHI | 2019-09-27 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-06 | Fred Michael
CTS-08 | CTS-08 | PI07477 | Verified | Turbine Generator - label missing on cables 1BCTSC0076 and 77 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-10-05 | Mike Tabbert
CTS-08 | CTS-08 | PI07478 | Verified | General - need permanent labels on all JB's | C | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CTS-08 | CTS-08 | PI07479 | Verified | Complete raceway for the turning gear | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-11-06 | Fred Michael
CTS-08 | CTS-08 | PI07480 | Verified | Complete grounding east side of the generator | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-04 | Richard Cruz | 2019-10-09 | Albert Burge
CTS-08 | CTS-08 | PI07483 | Verified | 1BCTSX0115, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-08 | CTS-08 | PI07484 | Verified | 1BCTSX0116, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-08 | CTS-08 | PI07485 | Verified | 1BCTSX0320, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-06 | Mike Tabbert
CTS-08 | CTS-08 | PI07486 | Verified | 1BCTSX0430, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07487 | Verified | 1BCTSX0431, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-11-06 | Mike Tabbert
CTS-08 | CTS-08 | PI07488 | Verified | 1BCTSC0003, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07489 | Verified | 1BCTSC0080, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07490 | Verified | 1BCTSC0081, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07491 | Verified | 1BCTSC0082, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07492 | Verified | 1BCTSC0186, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-08 | CTS-08 | PI07493 | Verified | 1BCTSC0206, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-08 | CTS-08 | PI07494 | Verified | 1BCTSK0001, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-08 | CTS-08 | PI07495 | Verified | 1BCTSK0035, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-08 | CTS-08 | PI07496 | Verified | 1BCTSK0083, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-09-28 | Mike Tabbert
CTS-08 | CTS-08 | PI07497 | Verified | 1BCTSK0152, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-08 | CTS-08 | PI07498 | Verified | 1BCTSX0115, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-11-05 | Tommy Vuong | 2019-11-06 | Mike Tabbert
CTS-08 | CTS-08 | PI07499 | Verified | 1BCTSX0116, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07500 | Verified | 1BCTSX0320, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-11-05 | Tommy Vuong | 2019-11-06 | Mike Tabbert
CTS-08 | CTS-08 | PI07501 | Verified | 1BCTSX0430, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07502 | Verified | 1BCTSX0431, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07503 | Verified | 1BYVAC0105, From Termination | B | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
CTS-08 | CTS-08 | PI07504 | Verified | 1BYVAC0106, From Termination | B | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
CTS-08 | CTS-08 | PI07505 | Verified | 1BYVAC0107, From Termination | B | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
CTS-08 | CTS-08 | PI07506 | Verified | 1BYVAC0108, From Termination | B | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
CTS-08 | CTS-08 | PI07507 | Verified | 1BCTSC0003, To Termination | B | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
CTS-08 | CTS-08 | PI07508 | Verified | 1BCTSC0014, To Termination | B | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
CTS-08 | CTS-08 | PI07509 | Verified | 1BCTSC0080, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07510 | Verified | 1BCTSC0081, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07511 | Verified | 1BCTSC0082, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07512 | Verified | 1BCTSC0100, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CTS-08 | CTS-08 | PI07513 | Verified | 1BCTSC0186, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-08 | CTS-08 | PI07514 | Verified | 1BCTSC0195, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CTS-08 | CTS-08 | PI07515 | Verified | 1BCTSC0206, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-09-28 | Mike Tabbert
CTS-08 | CTS-08 | PI07516 | Verified | 1BCTSK0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-08 | CTS-08 | PI07517 | Verified | 1BCTSK0031, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-06 | Mike Tabbert
CTS-08 | CTS-08 | PI07518 | Verified | 1BCTSK0035, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-08 | CTS-08 | PI07519 | Verified | 1BCTSK0049, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CTS-08 | CTS-08 | PI07520 | Verified | 1BCTSK0050, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07521 | Verified | 1BCTSK0058, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-04 | Dustin Futrell | 2019-10-04 | Mike Tabbert
CTS-08 | CTS-08 | PI07522 | Verified | 1BCTSK0073, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-06 | Mike Tabbert
CTS-08 | CTS-08 | PI07523 | Verified | 1BCTSK0083, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-09-28 | Mike Tabbert
CTS-08 | CTS-08 | PI07524 | Verified | 1BCTSK0087, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-05 | Mike Tabbert
CTS-08 | CTS-08 | PI07525 | Verified | 1BCTSK0088, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-11-05 | Tommy Vuong | 2019-11-06 | Mike Tabbert
CTS-08 | CTS-08 | PI07526 | Verified | 1BCTSK0152, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
CTS-08 | CTS-08 | PI07527 | Verified | 1BCTSX0115, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07528 | Verified | 1BCTSX0116, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07529 | Verified | 1BCTSX0320, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-11-05 | Tommy Vuong | 2019-11-06 | Mike Tabbert
CTS-08 | CTS-08 | PI07530 | Verified | 1BCTSX0430, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI07531 | Verified | 1BCTSX0431, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
CTS-08 | CTS-08 | PI15005 | Verified | Clean up inside 1B-CTS-CHC00GH001; GT Gen Control & Protective Relay Panel, Northeast side of GT B Control Package | C | E | Jonathan Donham | McD | 2020-01-02 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2020-04-07 | Randy Carpenter
CTS-08 | CTS-08 | PI15006 | Verified | Heat shrink cable/wire tags inside 1B-CTS-CHC00GH001; GT Gen Control & Protective Relay Panel, Northeast side GT B Control Package | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-15 | Shannon Scott
CTS-08 | CTS-08 | PI15007 | Verified | Replace cable tags that are too big to heat shrink inside 1B-CTS-CHC00GH001; GT Gen Control & Protective Relay Panel, Northeast side GT B Control Package | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-15 | Shannon Scott
CTS-08 | CTS-08 | PI15008 | Verified | 1B-CTS-CHC00GH001; GT Gen Control & Protective Relay Panel needs phenolic label, Northeast side of GT B Control Package | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-14 | Mike Tabbert | 2020-01-28 | Fred Michael
CTS-08 | CTS-08 | PI16196 | Verified | 1BBTB01GR001 (1B Battery Bank - Battery no. 15 & no. 29 connection protective covers are damaged, need to be replaced | C | E | Mike Tabbert | McD | 2020-01-20 | Mike Tabbert | Comm | 2020-05-21 | Mike Tabbert | 2020-07-29 | John Watts
CTS-08 | CTS-08 | PI16669 | Verified | 1B-CTS-GEN-0001 - There's a missing bolt on the collector brush rigging assembly. | B | E | Chris Colvin | McD | 2020-02-07 | Chris Colvin | Comm | 2020-03-26 | Chris Colvin | 2020-04-06 | Bernard Stasse
CTS-08 | CTS-08 | PI17300 | Verified | Clean up GT B generator deck on East and West side | C | C | Johnny Campbell | McD | 2020-02-28 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-04-08 | Bernard Stasse
CTS-08 | CTS-08 | PI17301 | Verified | Remove scaffolding from East generator deck | C | C | Johnny Campbell | McD | 2020-02-28 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-04-08 | Bernard Stasse
CTS-08 | CTS-08 | PI17312 | Verified | Clean up GT B East exterior grating platform | C | C | Johnny Campbell | McD | 2020-02-28 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-04-08 | Bernard Stasse
CTS-08 | CTS-08 | PI17672 | Verified | 87G-1B-1 - NERC target on Beckwith Relay for 1B Generator Protection relay (IPSL #5 IPS Logic). Active on 10 January 2020 at 1951 hours. The unit was not online at time of relay target activation. | B | E | Jonathan Donham | McD | 2020-03-04 | Jonathan Donham | Comm | 2020-03-23 | Jonathan Donham | 2020-05-06 | John Watts
CTS-08 | CTS-08 | PI17695 | Verified | 1B GT - in the turning gear comparment the shaft guard is not in place exposing generator shaft. Install shaft guard. | C | M | Shane Crowe | McD | 2020-03-04 | Shane Crowe | Comm | 2020-05-19 | Shane Crowe | 2020-12-08 | Dave Goldak
CTS-08 | CTS-08 | PI17701 | Verified | Ground excitation bus duct supports. | B | E | Chris Colvin | McD | 2020-03-05 | Chris Colvin | Comm | 2020-03-26 | Chris Colvin | 2020-03-31 | Randy Carpenter
CTS-08 | CTS-08 | PI18161 | Verified | The exicitation bus duct supports need grounding - duplicate punch item PI17701 | B | E | Mike Tabbert | McD | 2020-03-20 | Mike Tabbert | Const | 2020-03-22 | Eric Policarpio | 2020-03-22 | Eric Policarpio
CTS-08 | CTS-08 | PI18175 | Verified | Mitsubishi commissioning paper work to submit after tuning and final testing are complete | C | M | Lonnie Peters | McD | 2020-03-23 | Lonnie Peters | Comm | 2020-04-01 | Lonnie Peters | 2020-04-01 | Eric Policarpio
CTS-09 | CTS-09 | PI01060 | Verified | Remove shipping braces on lube oil return expansion joint when installed after comm. flush. | B | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-06-10 | Kelvin Cook | 2019-08-28 | Brian Ballard
CTS-09 | CTS-09 | PI01061 | Verified | Confirm design for lube oil return pipe support at the lube oil reservoir. | B | P | Kelvin Cook | McD | 2019-05-20 | Kelvin Cook | Const | 2019-06-14 | Kelvin Cook | 2019-08-28 | Brian Ballard
CTS-09 | CTS-09 | PI01062 | Verified | Clean lube oil skid. | C | C | Alan Huntsman | McD | 2019-05-20 | Alan Huntsman | Const | 2020-03-12 | Johnny Campbell | 2020-04-14 | Lonnie Peters
CTS-09 | CTS-09 | PI01063 | Verified | Torque bolts & bend tabs at the lube oil return line flange at the L.O. reservoir. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-05-22 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01064 | Verified | Clean / pump out lube oil sump. | C | M | Lonnie Peters | McD | 2019-05-20 | Lonnie Peters | Const | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-09 | CTS-09 | PI01065 | Verified | Reset lube oil reservoir LIT 1BMBVCL101. | A | I | Gonzalo Pena | McD | 2019-05-20 | Gonzalo Pena | Const | 2019-05-22 | Gonzalo Pena | 2019-05-28 | Danny Pase
CTS-09 | CTS-09 | PI01066 | Verified | Patch / repair lube oil reservoir foundation. | B | C | Logan Holland | McD | 2019-05-20 | Logan Holland | Const | 2019-06-25 | Jack Fields | 2019-07-24 | Shannon Scott
CTS-09 | CTS-09 | PI01067 | Verified | Straigten u-bolt on vapor extractor expansion joint on top of lube oil reservoir. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-05-21 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01068 | Verified | Torque bolts & bend tabs at the vapor extractor - top of lube oil reservoir. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-05-22 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01069 | Verified | Check if the lube oil reservoir ladders are per spec. | C | C | Brian Ballard | MHI | 2019-05-20 | Brian Ballard | Const | 2019-11-24 | Brian Ballard | 2019-12-20 | Bernard Stasse
CTS-09 | CTS-09 | PI01070 | Verified | Torque bolts & bend tabs on the lube oil supply at the lube oil reservoir platform. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-05-22 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01071 | Verified | Missing flange cover on lube oil supply line at the lube oil reservoir. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-07-23 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01072 | Verified | Missing flange cover at the accumulator on top of lube oil reservoir. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-06-21 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01073 | Verified | Lube oil SS line needs shim / insulator. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-06-06 | Terry Deaton | 2019-11-24 | Brian Ballard
CTS-09 | CTS-09 | PI01074 | Verified | Secure isolator on the lube oil supply line west side of the the enclosure. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-06-06 | Terry Deaton | 2019-11-24 | Brian Ballard
CTS-09 | CTS-09 | PI01075 | Verified | Clean the Seal Oil skid. | C | M | Shane Crowe | McD | 2019-05-20 | Shane Crowe | Const | 2019-11-11 | Shane Crowe | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01076 | Verified | Complete vapor extractor piping (BOP). | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-06-18 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01077 | Verified | Wrap up bus duct with plastic at the seal oil skid. | B | E | Luis Cantu | McD | 2019-05-20 | Luis Cantu | Const | 2019-05-31 | Shannon Savoy | 2019-07-15 | Fred Michael
CTS-09 | CTS-09 | PI01078 | Verified | Remove scaffolding at the seal oil skid. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-21 | Terry Deaton | 2019-05-28 | Kelvin Cook
CTS-09 | CTS-09 | PI01079 | Verified | Install plug at the oil detector - north generator wall @ seal oil skid. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-21 | Terry Deaton | 2019-05-28 | Kelvin Cook
CTS-09 | CTS-09 | PI01080 | Verified | Install 3 instruments on the seal oil tank. Instruments installed, need to terminate cables. | B | I | Dustin Futrell | MHI | 2019-05-20 | Dustin Futrell | Const | 2019-11-08 | Dustin Futrell | 2019-11-13 | Shannon Scott
CTS-09 | CTS-09 | PI01081 | Verified | Missing 2 bolts & gasket in the turning gear enclosure. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-21 | Terry Deaton | 2019-05-28 | Danny Pase
CTS-09 | CTS-09 | PI01082 | Verified | Torque bolts & bend tabs on vapor extractor line at the turning gear enclosure. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-22 | Terry Deaton | 2019-05-28 | Danny Pase
CTS-09 | CTS-09 | PI01083 | Verified | Missing u-bolt on line in the turning gear enclosure. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-05-21 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01084 | Verified | Valve missing plug in the turning gear enclosure. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-21 | Terry Deaton | 2019-05-28 | Danny Pase
CTS-09 | CTS-09 | PI01085 | Verified | Install trench cover in the turning gear enclosure. | B | M | Lonnie Peters | McD | 2019-05-20 | Lonnie Peters | Comm | 2019-06-21 | Shane Crowe | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01086 | Verified | Vapor extractor line for #3, 4 & 5 bearings not complete - generator deck east side. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-07-22 | Danny Pase
CTS-09 | CTS-09 | PI01087 | Verified | Install valve at vapor extractor line - generator deck east side. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-22 | Terry Deaton | 2019-05-28 | Danny Pase
CTS-09 | CTS-09 | PI01088 | Verified | Install inst. tubing & gauge at vapor extractor line - generator deck east side. | A | I | Gonzalo Pena | McD | 2019-05-20 | Gonzalo Pena | Const | 2019-05-24 | Gonzalo Pena | 2019-05-28 | Danny Pase
CTS-09 | CTS-09 | PI01089 | Verified | Install vapor extractor BOP piping - generator deck east side. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-07-22 | Danny Pase
CTS-09 | CTS-09 | PI01090 | Verified | Missing u-bolt at sight glass piping - generator deck east side. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-05-22 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01091 | Verified | Generator trough needs grout - generator deck (lube oil sight glass support). | B | C | Johnny Campbell | McD | 2019-05-20 | Johnny Campbell | Const | 2019-07-16 | Johnny Campbell | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01092 | Verified | Missing u-bolts on 3", 1 1/4" & 1" - east side of generator (see Kelvin). | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-05-21 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01093 | Verified | Missing grating on turbine enclosure at the access to #2 bearing. | A | S | Robert Risher | McD | 2019-05-20 | Robert Risher | Const | 2019-05-23 | Tim Gallegos | 2019-05-28 | Danny Pase
CTS-09 | CTS-09 | PI01094 | Verified | Complete all torquing & bend tabs - ground floor under turbine. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-23 | Terry Deaton | 2019-05-28 | Kelvin Cook
CTS-09 | CTS-09 | PI01095 | Verified | Verify support for 6" SS line - southeast corner of GT enclosure. | B | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-22 | Terry Deaton | 2019-05-29 | Brian Ballard
CTS-09 | CTS-09 | PI01096 | Verified | The #2 bearing return line is missing support and is in contact with column - GT turbine enclosure. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-22 | Terry Deaton | 2019-08-22 | Brian Ballard
CTS-09 | CTS-09 | PI01097 | Verified | Tighten u-bolt on the #2 bearing return line - turbine enclosure. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-05-21 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-09 | CTS-09 | PI01098 | Verified | Install shim plate at the north end of lube oil supply line where the catwalk comes in contact with pipe. | A | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-08-28 | Terry Deaton | 2019-10-24 | Brian Ballard
CTS-09 | CTS-09 | PI01109 | Verified | Tag all components on the Seal Oil skid. | C | P | Kelvin Cook | MEL | 2019-05-20 | Kelvin Cook | Const | 2020-02-04 | Kelvin Cook | 2020-02-06 | Kelvin Cook
CTS-09 | CTS-09 | PI01113 | Verified | Pipe support LC-01602-27AOA-PS-02 is missing and needs to be installed for the LO supply pipe. | B | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-22 | Terry Deaton | 2019-05-29 | Brian Ballard
CTS-09 | CTS-09 | PI01115 | Verified | Seal all conduits in the GT Control Package. | B | E | Chris Colvin | McD | 2019-05-22 | Chris Colvin | Const | 2020-01-10 | Mike Tabbert | 2020-01-13 | Fred Michael
CTS-09 | CTS-09 | PI01117 | Verified | Terminate cable 1BCTSK0061 in the GT Control Package. | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-22 | Dan Dula | 2019-05-23 | Mike Tabbert
CTS-09 | CTS-09 | PI01118 | Verified | Terminate cable 1BCTSK0041 in the GT Control Package. | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-22 | Dan Dula | 2019-05-23 | Mike Tabbert
CTS-09 | CTS-09 | PI01119 | Verified | Terminate cable 1BCTSK0032 in the GT Control Package. | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-22 | Dan Dula | 2019-05-23 | Mike Tabbert
CTS-09 | CTS-09 | PI01120 | Verified | Replace tags on 3 improperly labeled buckets in the 1B GT Control Package. | B | E | Mike Tabbert | MHI | 2019-05-22 | Mike Tabbert | Const | 2019-05-29 | Keith Mahoney | 2019-05-29 | Keith Mahoney
CTS-09 | CTS-09 | PI01121 | Verified | Install ground jumpers in 1BMKW01AG101 on the Seal Oil skid. | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-22 | Dan Dula | 2019-05-23 | Mike Tabbert
CTS-09 | CTS-09 | PI01123 | Verified | Troubleshoot light fixtures in the 1B lube oil enclosure. | B | E | Luis Cantu | McD | 2019-05-22 | Luis Cantu | Const | 2019-05-31 | Shannon Savoy | 2019-06-14 | Mike Tabbert
CTS-09 | CTS-09 | PI01124 | Verified | Grout in Lube Oil enclosure. | B | C | Johnny Campbell | McD | 2019-05-22 | Johnny Campbell | Const | 2019-06-24 | Johnny Campbell | 2019-06-24 | Neil Simon
CTS-09 | CTS-09 | PI01125 | Verified | Dry pack under pipe supports on the East side of Lube Oil enclosure. | C | C | Johnny Campbell | McD | 2019-05-22 | Johnny Campbell | Const | 2019-07-24 | Jack Fields | 2019-12-12 | Michael Law
CTS-09 | CTS-09 | PI01126 | Verified | Grout in Column bases at East side of Lube Oil Enclosure at Column line X8-XB and X8-XC | C | C | Johnny Campbell | McD | 2019-05-22 | Johnny Campbell | Const | 2019-08-19 | Jack Fields | 2019-12-12 | Michael Law
CTS-09 | CTS-09 | PI01127 | Verified | Repair concrete at pipe supports at East side of Lube Oil foundation. | C | C | Johnny Campbell | McD | 2019-05-22 | Johnny Campbell | Const | 2019-07-16 | Johnny Campbell | 2019-12-12 | Michael Law
CTS-09 | CTS-09 | PI01128 | Verified | Dry pack Pipe supports inside Lube Oil Enclosure in Containment pit. | C | C | Johnny Campbell | McD | 2019-05-22 | Johnny Campbell | Const | 2019-10-10 | Johnny Campbell | 2019-12-12 | Michael Law
CTS-09 | CTS-09 | PI01129 | Verified | Caulk Expansion Joint Between Lube Oil foundation and Cable Tray support at Northeast side. | C | C | Johnny Campbell | McD | 2019-05-22 | Johnny Campbell | Const | 2019-08-19 | Jack Fields | 2019-12-12 | Michael Law
CTS-09 | CTS-09 | PI01130 | Verified | Rub down containment curbs at Seal Oil skid. | C | C | Johnny Campbell | McD | 2019-05-22 | Johnny Campbell | Const | 2019-08-19 | Jack Fields | 2019-12-12 | Michael Law
CTS-09 | CTS-09 | PI01131 | Verified | 1BCTSK0045, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const |  |  | 2019-05-23 | Mike Tabbert
CTS-09 | CTS-09 | PI02768 | Verified | Install lube oil enclosure heaters (2). | C | M | Shane Crowe | McD | 2019-07-25 | Shane Crowe | Const | 2019-08-28 | Shane Crowe | 2019-08-28 | Joshua Sturgeon
CTS-09 | CTS-09 | PI02805 | Verified | Install GT Auxiliary Package Heaters (2). | B | M | Shane Crowe | McD | 2019-07-26 | Shane Crowe | Const | 2019-08-07 | Shane Crowe | 2019-08-07 | Joshua Sturgeon
CTS-09 | CTS-09 | PI16670 | Verified | 1BMKW01AT101 - 1B's seal oil filter is leaking oil from the top of the filter. | B | M | William Mitchell | McD | 2020-02-07 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-10 | John Watts
CTS-09 | CTS-09 | PI16671 | Verified | 1BMKW01AA007 - 1B's seal oil pressure relief valve is leaking at the top of the valve. | B | M | William Mitchell | McD | 2020-02-07 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-10 | John Watts
CTS-09 | CTS-09 | PI16936 | Verified | Remove unused uni-strut at SE corner of L.O. Tank | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-05-06 | John Watts
CTS-09 | CTS-09 | PI16937 | Verified | Clean deck, piping and components at top of L.O. skid | C | C | Johnny Campbell | McD | 2020-02-18 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-04-07 | Randy Carpenter
CTS-09 | CTS-09 | PI16938 | Verified | Missing conduit condolet cover at SE wall of L.O. enclosure | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-09 | CTS-09 | PI16939 | Verified | Raise .75 inch and 1.25 inch conduit that has been stepped on adjacent to GT L.O. Coolers A & B | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-17 | John Watts
CTS-09 | CTS-09 | PI16940 | Verified | Reinstall ground at GT L.O. Mist Seperator B; MBV03AT102 | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-02-27 | Chris Colvin | 2020-03-03 | John Watts
CTS-09 | CTS-09 | PI16941 | Verified | U-Bolt nuts loose on supply piping downstream of GT L.O. Pressure Regulating Valve; MBV01AA702 | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-08 | James Beech | 2021-05-27 | John Watts
CTS-09 | CTS-09 | PI16942 | Verified | Motor Termination Box cover is loose at GT Main L.O. Pump B Motor; MBV01AP102M01 | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-02-27 | Chris Colvin | 2020-03-03 | John Watts
CTS-09 | CTS-09 | PI16943 | Verified | Install drain plug at SE top corner of L.O. skid | C | P | Lonnie Peters | McD | 2020-02-18 | Lonnie Peters | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-09 | CTS-09 | PI16944 | Verified | Missing flange bolt at GT Lube Oil Accumulator C, 4 inch isolation valve; MBV01AA503 | B | P | Lonnie Peters | McD | 2020-02-18 | Lonnie Peters | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-09 | CTS-09 | PI16945 | Verified | Leaking isolation valve; MBV21AA808 at GT Lube Oil Purifier Level Indicator, SE end of L.O. Tank | B | P | Lonnie Peters | McD | 2020-02-18 | Lonnie Peters | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-09 | CTS-09 | PI16946 | Verified | Remove temporary light switches near North door of L.O. enclosure | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-17 | John Watts
CTS-09 | CTS-09 | PI16947 | Verified | Clean out Unit B GT Seal Oil Skid containment sump and cover with grating | B | C | Bobby Williams | McD | 2020-02-18 | Bobby Williams | Comm | 2020-02-25 | Tim Gallegos | 2020-03-03 | John Watts
CTS-09 | CTS-09 | PI16948 | Verified | Remove tape, wire, rope and old unused tags from Seal Oil skid piping and components | C | C | Johnny Campbell | McD | 2020-02-18 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-04-07 | Randy Carpenter
CTS-09 | CTS-09 | PI16949 | Verified | Clean Seal Oil skid piping and components | C | C | Johnny Campbell | McD | 2020-02-18 | Johnny Campbell | Comm | 2020-03-20 | Johnny Campbell | 2020-04-06 | Bernard Stasse
CTS-09 | CTS-09 | PI16950 | Verified | .75 inch drain line support is not bolted to skid at NE corner of Seal Oil skid | C | P | Tim Green | McD | 2020-02-18 | Tim Green | Comm | 2020-06-12 | Tim Green | 2020-12-16 | Dave Goldak
CTS-09 | CTS-09 | PI16951 | Verified | Conduit condolet cover is loose at Emergency Seal Oil Pump Motor; MKW01AP201-M01 | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-09 | CTS-09 | PI16952 | Verified | Clean and paint all Seal Oil System carbon steel piping | C | X | Jerry Smith | McD | 2020-02-18 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-04-06 | Bernard Stasse
CTS-09 | CTS-09 | PI16953 | Verified | Bend tabs at 3" Seal Oil line flange connection to GT L.O. return piping, West side, outside of GT B L.O. enclosure | B | P | Lonnie Peters | McD | 2020-02-18 | Lonnie Peters | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-09 | CTS-09 | PI16954 | Verified | Missing u-bolt nut on 8" L.O. Supply line inside enclosure, near penetration | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-19 | Tim Green | 2021-05-27 | John Watts
CTS-09 | CTS-09 | PI16955 | Verified | Missing u-bolt nut on 8" L.O. Supply line downstream of GT L.O. Pressure Regulating Valve; MBV01AA702 | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-19 | Tim Green | 2021-05-27 | John Watts
CTS-09 | CTS-09 | PI18015 | Verified | 1AMBV01AP101 - 1A 'A' GT Main lube oil pump continues to leak at seals. Please investigate and repair. | C | M | William Mitchell | McD | 2020-03-17 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2021-05-27 | John Watts
CTS-10 | CTS-10 | PI01599 | Verified | 1BCTSK0066, Pull and terminate cable | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-24 | Mike Tabbert
CTS-10 | CTS-10 | PI01600 | Verified | 1BCTS-SGY01GH001-DS001-C0001, Submit pull ticket for status | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-24 | Mike Tabbert
CTS-10 | CTS-10 | PI01601 | Verified | Complete external ground 3" seal tight to FACP at CO-2 Storage Tank | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-10 | CTS-10 | PI01602 | Verified | Install condulet covers on all conduits at CO-2 storage tank. | B | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-10 | CTS-10 | PI01603 | Verified | Trim tie raps on sealtight grounding at FACP. | B | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-10 | CTS-10 | PI01604 | Verified | Grout conduit stands at CO-2 storgae tank foundation. | C | C | Johnny Campbell | McD | 2019-06-27 | Johnny Campbell | Const | 2019-07-24 | Jack Fields | 2019-08-21 | Fred Michael
CTS-10 | CTS-10 | PI01605 | Verified | Install bushing on 3" sealtight connector inside FACP. | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-10 | CTS-10 | PI01606 | Verified | Clean FACP at CO-2 stoarage tank. | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-10 | CTS-10 | PI01607 | Verified | Install Battery at CO-2 Storage Tank | B | E | Chris Boudreaux | McD | 2019-06-27 | Chris Boudreaux | Const |  |  | 2019-11-23 | Michael Law
CTS-10 | CTS-10 | PI01621 | Verified | Complete air blows to the entire piping system. | B | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-25 | Kelvin Cook | 2019-07-25 | Kelvin Cook
CTS-10 | CTS-10 | PI01622 | Verified | Install fill connections piping to CO2 tank | A | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-11 | Eric Czajka | 2019-07-19 | Kelvin Cook
CTS-10 | CTS-10 | PI01623 | Verified | Provide pressure testing for the entire piping system | A | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-19 | Eric Czajka | 2019-07-22 | Mike Tabbert
CTS-10 | CTS-10 | PI01624 | Verified | Remove all plugs after pressure test & comm. blows & install nozzles | B | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-25 | Kelvin Cook | 2019-07-25 | Kelvin Cook
CTS-10 | CTS-10 | PI01625 | Verified | cold galve all pipe supports | C | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const |  |  | 2019-10-19 | Kelvin Cook
CTS-10 | CTS-10 | PI01626 | Verified | Make final connections to pneumatic siren in FG-PA unit after pressure test | B | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-26 | Kelvin Cook | 2019-07-26 | Kelvin Cook
CTS-10 | CTS-10 | PI01627 | Verified | remove all three temporary piggy back support & install proper support | A | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-11 | Eric Czajka | 2019-07-19 | Kelvin Cook
CTS-10 | CTS-10 | PI01628 | Verified | At south west corner of Aux enclosure install support for 3/4" pipe | A | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-11 | Eric Czajka | 2019-07-19 | Kelvin Cook
CTS-10 | CTS-10 | PI01629 | Verified | Make final connections to pneumatic siren in FG-PA unit after pressure test | A | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-26 | Kelvin Cook | 2019-07-26 | Kelvin Cook
CTS-10 | CTS-10 | PI01630 | Verified | grout all supports around CO2 tank | B | C | Johnny Campbell | McD | 2019-06-27 | Johnny Campbell | Const | 2019-07-22 | Johnny Campbell | 2019-07-26 | Kelvin Cook
CTS-10 | CTS-10 | PI01631 | Verified | Grout CO2 tank | B | C | Johnny Campbell | McD | 2019-06-27 | Johnny Campbell | Const | 2019-07-22 | Johnny Campbell | 2019-07-26 | Kelvin Cook
CTS-10 | CTS-10 | PI01632 | Verified | Install 1/4" tubing and damper pneumatic trip switches to all dampers GT enclosures | A | I | Gonzalo Pena | McD | 2019-06-27 | Gonzalo Pena | Const | 2019-08-16 | Gonzalo Pena | 2019-08-20 | Kelvin Cook
CTS-10 | CTS-10 | PI01633 | Verified | Install 1/4" tubing and damper pneumatic trip switches to all dampers Aux enclosures | A | I | Gonzalo Pena | McD | 2019-06-27 | Gonzalo Pena | Const | 2019-08-16 | Gonzalo Pena | 2019-08-20 | Kelvin Cook
CTS-10 | CTS-10 | PI01634 | Verified | Make final connections to pneumatic siren in turbine bearing enclosure after pressure test | A | P | Eric Czajka | JAN | 2019-06-27 | Eric Czajka | Const | 2019-07-26 | Gonzalo Pena | 2019-07-26 | Kelvin Cook
CTS-10 | CTS-10 | PI01636 | Verified | Install all CO2 warning signs. | B | M | Lonnie Peters | McD | 2019-06-27 | Lonnie Peters | Const | 2019-11-23 | Michael Law | 2020-01-28 | Fred Michael
CTS-10 | CTS-10 | PI01652 | Verified | Seal conduits inside the panel | B | E | Chris Colvin | McD | 2019-06-27 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2020-01-27 | Michael Law
CTS-10 | CTS-10 | PI01653 | Verified | Connect the grounding inside C02 Tank control panel | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-10 | CTS-10 | PI01654 | Verified | Ground the back panel on Pneumatic time delay cabinet | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-10 | CTS-10 | PI01655 | Verified | Ground the back panel on Refrigeration control panel | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-15 | Fred Michael
CTS-10 | CTS-10 | PI01656 | Verified | Verify if the tag number of C02 tank control panel is correct as per drawing. Tag starts at '11' | B | E | Mike Tabbert | McD | 2019-06-27 | Mike Tabbert | Const | 2019-07-19 | Mike Tabbert | 2019-08-16 | Logan Holland
CTS-10 | CTS-10 | PI03137 | Verified | 1BCTSC0293, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-10 | CTS-10 | PI03138 | Verified | 1BCTSC0301, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-10 | CTS-10 | PI03139 | Verified | 1BCTSC0312, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-10 | CTS-10 | PI03140 | Verified | 1BCTSC0316, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-10 | CTS-10 | PI03141 | Verified | 1BCTSC0290, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-10 | CTS-10 | PI03142 | Verified | 1BCTSC0293, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-10 | CTS-10 | PI03143 | Verified | 1BCTSC0299, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-10 | CTS-10 | PI03144 | Verified | 1BCTSC0301, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-10 | CTS-10 | PI03145 | Verified | 1BCTSC0312, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-10 | CTS-10 | PI03146 | Verified | 1BCTSC0313, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-08 | Fred Michael
CTS-10 | CTS-10 | PI03147 | Verified | 1BCTSC0316, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03148 | Verified | At turning gear pull and terminate vendor supplied cable to 4 heat detectors, 301, 302, 303 and 304 from terminal box 011. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-15 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03149 | Verified | At turning gear pull and terminate vendor supplied cable to two lockout valve status indicator 301 and 302 from terminal box 011. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03150 | Verified | At turning gear pull and terminate vendor supplied cable to three horn/strobe EH-301 and 302, EI-301 from terminal box 011. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-15 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03151 | Verified | At turning gear pull and terminate vendor supplied cables to two manual pull stations 301 and 302 from terminal box 011. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-15 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03152 | Verified | At turning gear pull and terminate vendor supplied cable from JBF11 to JBF12. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03153 | Verified | At GT enclosure, Install devices and conduit, pull and terminate vendor supplied cable from JBF01 to EG-102 and 104, DT-101 and 102. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-15 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03154 | Verified | At GT enclosure, install conduit, pull and terminate vendor supplied cable from JBF02 to JBF01. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03155 | Verified | At GT enclosure, install devices and conduit, pull and terminate vendor supplied cable from JBF02 to DT-104, DT-103, DT-105, DT-106, LS-104. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03156 | Verified | At GT enclosure, mount device, Install conduit, pull and terminate vendor supplied cable from JBF03 to GJ-104, GK-104EH-104, GJ-102, GK-102, and EH-102, DT-108 and DT-107. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03157 | Verified | At GT enclosure, mount device, Install conduit, pull and terminate vendor supplied cable from JBF04 to EH-106, GJ-106, GK-106, DT-111, DT-112, DT-110, DT-114, DT-113, DT-109, LS-105. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03158 | Verified | AT GT enclosure, Install conduit, pull and terminate vendor supplied cable from JBF05 to LS-103. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03159 | Verified | At GT enclosure, mount device, Install conduit, pull and terminate vendor supplied cable from JBF06 to GJ-103, GK-103, EH-103, GJ-101, GK-101, EH-101. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03160 | Verified | At GT enclosure, mount device, Install conduit, pull and terminate vendor supplied cable from JBF07 to EG-101, EG-103, EH-105, GJ-107, GK-105. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI03161 | Verified | GT enclosure fire dampers missing Pressure switches (18). | A | I | Gonzalo Pena | McD | 2019-08-05 | Gonzalo Pena | Const | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Mike Tabbert
CTS-10 | CTS-10 | PI03162 | Verified | Auxiliary Enclosure missing six fire damper pressure switches. | A | I | Gonzalo Pena | McD | 2019-08-05 | Gonzalo Pena | Const | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Mike Tabbert
CTS-10 | CTS-10 | PI04698 | Verified | Replace cable tag in 1B-CTS-SGY03GH001 (faded) - Tomco skid. | B | E | Chris Colvin | McD | 2019-08-30 | Chris Colvin | Const | 2020-03-09 | Michael Law | 2020-04-07 | Randy Carpenter
CTS-10 | CTS-10 | PI04699 | Verified | Ground seal tite at Tomco skid. | A | E | Dustin Futrell | McD | 2019-08-30 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI04700 | Verified | Check unlanded jumpers / wires terminations in 1B-CTS-SGY03GH001 - Tomco skid. | A | E | Dustin Futrell | McD | 2019-08-30 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI04701 | Verified | Clean out 1B-CTS-SGY03GH001 - Tomco skid. | B | E | Dustin Futrell | McD | 2019-08-30 | Dustin Futrell | Const |  |  | 2019-11-23 | Michael Law
CTS-10 | CTS-10 | PI04702 | Verified | Heat shrink EOL reistor (#2700) in 1B-CTS-SGY03GH001 - Tomco skid. | A | E | Dustin Futrell | McD | 2019-08-30 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI04703 | Verified | Tighten seal tite at 1BSGJ02EH108 - FGPA Horn / Strobe. | A | E | Dustin Futrell | McD | 2019-08-30 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-05 | Shannon Scott
CTS-10 | CTS-10 | PI04704 | Verified | Term. Cable for 1BSGJ02GJ108 at the FGPA. | A | E | Dustin Futrell | McD | 2019-08-30 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI04705 | Verified | Term. Cable for 1BSGJ02GK108 at the FGPA. | A | E | Dustin Futrell | McD | 2019-08-30 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI04706 | Verified | LS-108 is tagged wrong at the FGPA. | C | E | Chris Colvin | McD | 2019-08-30 | Chris Colvin | Const | 2020-04-22 | Matt Gilmore | 2020-04-29 | Mike Tabbert
CTS-10 | CTS-10 | PI04707 | Verified | LS-107 is missing tag at the FGPA. | C | E | Chris Colvin | McD | 2019-08-30 | Chris Colvin | Const | 2020-04-22 | Matt Gilmore | 2020-04-29 | Mike Tabbert
CTS-10 | CTS-10 | PI04708 | Verified | Tie in fire alarm shipping splits at the FGPA - upper level. | A | E | Dustin Futrell | McD | 2019-08-30 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI04709 | Verified | Pour all seals after commissioning. | B | E | Chris Colvin | McD | 2019-08-30 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CTS-10 | CTS-10 | PI04710 | Verified | Complete tubing for dampers in the FGPA. | A | I | Gonzalo Pena | McD | 2019-08-30 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI04711 | Verified | Ground flex on incoming cable to 1BMBY92GH033 - north side of FGPA upper level. | A | E | Dustin Futrell | McD | 2019-08-30 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI04712 | Verified | Missing condulet covers on incoming cables to 1BMBY92GH033 - north side of FGPA upper level. | B | E | Dustin Futrell | McD | 2019-08-30 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-18 | Mike Tabbert
CTS-10 | CTS-10 | PI04713 | Verified | JBF-05 - clean rust off of door - turbine enclosure. | B | E | Dustin Futrell | McD | 2019-08-30 | Dustin Futrell | Const | 2019-09-13 | Richard Cruz | 2019-09-23 | Albert Burge
CTS-10 | CTS-10 | PI04714 | Verified | Ground seal tite at all JBFs in subsystem. | A | E | Dustin Futrell | McD | 2019-08-30 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI04715 | Verified | LS-104 & LS-105 tags are swapped - GT enclosure east side. | C | E | Bobby Williams | McD | 2019-08-30 | Bobby Williams | Const | 2020-02-13 | Bobby Williams | 2020-02-14 | Mike Tabbert
CTS-10 | CTS-10 | PI04716 | Verified | Fix all damper tags on the aux. enclosure. | C | E | Bobby Williams | McD | 2019-08-30 | Bobby Williams | Const | 2020-02-13 | Bobby Williams | 2020-02-14 | Mike Tabbert
CTS-10 | CTS-10 | PI04717 | Verified | Ground seal tite at 1BSGJ02GJ202 & 1BSGJ02GK202 at the aux. enclosure. | A | E | Dustin Futrell | McD | 2019-08-30 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Mike Tabbert
CTS-10 | CTS-10 | PI04819 | Verified | Change tank fill and return lines to 304 SS. | B | P | Sheri Fritz | JAN | 2019-09-09 | Sheri Fritz | Const |  |  | 2019-11-05 | Michael Law
CTS-10 | CTS-10 | PI17680 | Verified | 1B Electrical Package - 1B Electrical Package fire alarm system has been alarming continuously. System had to be disabled to the stop alarm. Please inspect and repair. | C | E | James Strange | MHI | 2020-03-04 | James Strange | Comm | 2020-05-21 | Ron McMurtry | 2021-04-26 | Keith Pollock
CTS-11 | CTS-11 | PI03233 | Verified | Receiver valves need labels | C | M | James Strange | MHI | 2019-08-06 | James Strange | Const | 2020-04-01 | James Strange | 2020-04-01 | Eric Policarpio
CTS-11 | CTS-11 | PI03279 | Verified | LM-1373 - Connect 1BPITMBL03CP101 | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03280 | Verified | LM-1373 - Relocate support to southside of 90 PS-06 23BOA | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03283 | Verified | LM-1373 - 1B-CTS-PD-P41-130-01 install stainless wrap and U-bolt at both supports | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03284 | Verified | LM-1373 - SRV valve needs tubing to ground, Air Tank drain valve tubing to ground | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Gonzalo Pena | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03285 | Verified | LM-1373 - PS-09 Close up gap at bottom of shoe | A | I | Gonzalo Pena | McD | 2019-08-07 | Gonzalo Pena | Const | 2019-08-20 | Gonzalo Pena | 2019-08-28 | Kelvin Cook
CTS-11 | CTS-11 | PI03286 | Verified | LM-1373 - PS-10 loose nut | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03287 | Verified | LM-1373 - PS-11 not installed | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03288 | Verified | LM-1373 - PS-12 complete installation | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03289 | Verified | LM-1373 - PS-13 not installed | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03290 | Verified | LM-1381 - Install proper flexitallic gaskets to seal air kid - Spool 11 & 16 | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-19 | Kelvin Cook
CTS-11 | CTS-11 | PI03291 | Verified | LM-1362 - Remove shipping braces from expansion joints | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-19 | Kelvin Cook
CTS-11 | CTS-11 | PI03292 | Verified | LM-1364 - Remove shipping braces from expansion joints | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-19 | Kelvin Cook
CTS-11 | CTS-11 | PI03293 | Verified | LM-1365 - Remove shipping braces from expansion joints | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-20 | Kelvin Cook
CTS-11 | CTS-11 | PI03294 | Verified | LM-1365 - Test blind removed from LP line north of expansion at 23-AOJ connection | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-15 | Terry Deaton | 2019-08-16 | Kelvin Cook
CTS-11 | CTS-11 | PI03295 | Verified | LM-1365 - LP line remove PFB bolt and install B7/B16 stude bolts at 23-AO1 connection | A | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-08-19 | Terry Deaton | 2019-09-18 | Kelvin Cook
CTS-11 | CTS-11 | PI03296 | Verified | Install bolts at west flange * See Kelvin | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-27 | Kelvin Cook
CTS-11 | CTS-11 | PI03297 | Verified | LM-1381 - Seal air line west side ground level north end center shoes PS-06 | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-27 | Kelvin Cook
CTS-11 | CTS-11 | PI03298 | Verified | LM-1381 - Seal air line west side ground level north end center shoes PS-07 | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-27 | Kelvin Cook
CTS-11 | CTS-11 | PI03299 | Verified | LM-1367 - Blind flange on test port even up the bolts properly | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-28 | Kelvin Cook
CTS-11 | CTS-11 | PI03300 | Verified | LM-1381 - Remove all blinds after pressure test | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03301 | Verified | LM-1374 - Loose U-bolt, torque flanges, hi-point vent missing plug | A | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-09-05 | Damon Turner | 2019-09-18 | Kelvin Cook
CTS-11 | CTS-11 | PI03302 | Verified | LM-1373 - PS-22 not installed | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03303 | Verified | LM-1373 - PS-21 complete installation | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-15 | Terry Deaton | 2019-08-19 | Kelvin Cook
CTS-11 | CTS-11 | PI03304 | Verified | LM-1373 - PS-20 complete installation | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03305 | Verified | LM-1373 - PS-18 complete installation | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-15 | Terry Deaton | 2019-08-19 | Kelvin Cook
CTS-11 | CTS-11 | PI03306 | Verified | LM-1373 - PS-17 complete installation | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-15 | Terry Deaton | 2019-08-19 | Kelvin Cook
CTS-11 | CTS-11 | PI03307 | Verified | LM-1373 - PS-16 complete installation | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03308 | Verified | LM-1373 - PS-13 close gap | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03309 | Verified | 1BMBL03AA923 & 1BMBL03AA924 missing plug, low point drain | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-28 | Kelvin Cook
CTS-11 | CTS-11 | PI03310 | Verified | 1BMBL03AA921 & 1BMBL03AA922 missing plug, low point drain | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-28 | Kelvin Cook
CTS-11 | CTS-11 | PI03311 | Verified | LM-1373 - PS-24 complete installation | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-11 | CTS-11 | PI03312 | Verified | LM-1383 - Restore system after air blows and torque flanges | B | P | Lonnie Peters | McD | 2019-08-07 | Lonnie Peters | Const |  |  | 2019-12-04 | Kelvin Cook
CTS-11 | CTS-11 | PI03313 | Verified | LM-1385 - Rotate actuator and install handwheel | A | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
CTS-11 | CTS-11 | PI03314 | Verified | LM-1383 - PS-04 plum and center support with shoe | B | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-08-16 | Terry Deaton | 2019-09-18 | Kelvin Cook
CTS-11 | CTS-11 | PI03315 | Verified | LM-1366 - Install flex gasket at spool 23BOG-02 to 03 and 23BOG-03 to 23AOG-06 | A | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-08-16 | Terry Deaton | 2019-09-18 | Kelvin Cook
CTS-11 | CTS-11 | PI04251 | Verified | Perform clean & close on Air Inlet Filter House and duct work. | A | S | Bobby Williams | McD | 2019-08-14 | Bobby Williams | Const |  |  | 2019-11-27 | Joshua Sturgeon
CTS-11 | CTS-11 | PI04253 | Verified | Perform clean & close on Inlet Filter House duct work. | A | S | Robert Risher | McD | 2019-08-14 | Robert Risher | Const | 2019-08-16 | Ed Gober | 2019-08-16 | Ed Gober
CTS-11 | CTS-11 | PI04255 | Verified | Torque the inlet duct expansion joint. | A | M | Shane Crowe | McD | 2019-08-15 | Shane Crowe | Const | 2019-08-16 | Shane Crowe | 2019-08-20 | Joshua Sturgeon
CTS-11 | CTS-11 | PI04348 | Verified | MBL02AP202 - 1B evaporative cooler pump coupling guard is damaged. Needs repair. | B | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-08-28 | Joshua Sturgeon | 2019-08-29 | Shannon Scott
CTS-11 | CTS-11 | PI08172 | Verified | Panel 1BMBL30GH001 - complete tubing inside panel. | A | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2020-01-01 | Albert Burge
CTS-11 | CTS-11 | PI08173 | Verified | Panel 1BMBL30GH001 - ground panel. | A | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-10-03 | Dustin Futrell | 2020-01-13 | Fred Michael
CTS-11 | CTS-11 | PI08174 | Verified | Panel 1BMBL30GH001 - seal conduits. | A | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-10-04 | Richard Cruz | 2020-01-13 | Fred Michael
CTS-11 | CTS-11 | PI08175 | Verified | Panel 1BMBL30GH002 - complete tubing inside panel. | A | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2020-01-01 | Albert Burge
CTS-11 | CTS-11 | PI08176 | Verified | Panel 1BMBL30GH002 - ground panel. | A | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-10-03 | Dustin Futrell | 2020-01-13 | Fred Michael
CTS-11 | CTS-11 | PI08177 | Verified | Panel 1BMBL30GH002 - seal conduits. | A | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-10-04 | Richard Cruz | 2020-01-13 | Fred Michael
CTS-11 | CTS-11 | PI08178 | Verified | At Panel 1BMBL30GH002 platform on west side of inlet filter house - repair platform gate. | B | S | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-11-05 | Albert Burge
CTS-11 | CTS-11 | PI08179 | Verified | Replace broken porcelin sockets in the inlet filter house enclosures. | A | E | Mike Tabbert | McD | 2019-09-30 | Mike Tabbert | Const | 2019-11-25 | Brad Stanford | 2019-12-10 | Mike Tabbert
CTS-11 | CTS-11 | PI08180 | Verified | Panel 1BCNC00GZ001 - ground panel. | A | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-10-03 | Dustin Futrell | 2020-01-13 | Fred Michael
CTS-11 | CTS-11 | PI08181 | Verified | Panel 1BCNC00GZ001 - seal conduits. | A | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-10-04 | Richard Cruz | 2020-01-13 | Fred Michael
CTS-11 | CTS-11 | PI08182 | Verified | Panel 1BCNC00GZ001 - dress cables in panel (shields). | A | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-10-04 | Richard Cruz | 2020-01-27 | Michael Law
CTS-11 | CTS-11 | PI08183 | Verified | Install instrument hood on east side of top level of the inlet filter house. | B | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const | 2019-12-02 | James Tanner | 2019-12-13 | Albert Burge
CTS-11 | CTS-11 | PI08184 | Verified | 1BMBL02AP201M01 - ground seal tite. | A | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-10-04 | Richard Cruz | 2020-01-13 | Fred Michael
CTS-11 | CTS-11 | PI08185 | Verified | 1BMBL02AP201M02 - ground seal tite. | A | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-10-04 | Randy Carpenter | 2020-01-13 | Fred Michael
CTS-11 | CTS-11 | PI08186 | Verified | 1BMBL02AP201M01 & 02 - tag motors. | C | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2020-04-16 | Chris Colvin | 2020-04-21 | Michael Law
CTS-11 | CTS-11 | PI08187 | Verified | 1BMBL02AP201M01 & 02 - change motor grounds to #8 wire. | A | E | Dustin Futrell | McD | 2019-09-30 | Dustin Futrell | Const | 2019-10-04 | Richard Cruz | 2019-10-15 | Fred Michael
CTS-11 | CTS-11 | PI08188 | Verified | Install 1BMBL02CL201 - east side of top level of the inlet filter house. | A | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2019-12-01 | Albert Burge
CTS-11 | CTS-11 | PI08189 | Verified | Panel 1BMBL02AC301 - repair panel door. | A | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-10-04 | Richard Cruz | 2020-01-13 | Fred Michael
CTS-11 | CTS-11 | PI08190 | Verified | Panel 1BMBL02AC301 - seal conduits. | A | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-10-04 | Richard Cruz | 2020-01-13 | Fred Michael
CTS-11 | CTS-11 | PI08191 | Verified | Panel 1BMBL02AC301 - ground seal tite. | A | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-11-11 | Brad Stanford | 2020-01-13 | Fred Michael
CTS-11 | CTS-11 | PI08192 | Verified | At Panel 1BMBL02AC301 - missing condulet covers (under grating). | C | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-13 | Mike Tabbert
CTS-11 | CTS-11 | PI08193 | Verified | Panel 1BMBL02AC301 - complete non-scheduled cable. | A | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2019-11-25 | Brad Stanford | 2019-12-13 | Mike Tabbert
CTS-11 | CTS-11 | PI08194 | Verified | Valve 1BMBL03AA707 - ty-wrap grounds on seal tite. | C | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2020-04-16 | Chris Colvin | 2020-04-29 | Mike Tabbert
CTS-11 | CTS-11 | PI08195 | Verified | Valve 1BMBL03AA712 - missing condulet covers. | C | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2020-04-16 | Chris Colvin | 2020-04-29 | Mike Tabbert
CTS-11 | CTS-11 | PI08196 | Verified | Valve 1BMBL03AA712 - ground seal tite. | A | E | Dustin Futrell | McD | 2019-09-30 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-09 | Albert Burge
CTS-11 | CTS-11 | PI08197 | Verified | Valve 1BMBH05AA752 - ground seal tite. | A | E | Dustin Futrell | McD | 2019-09-30 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-09 | Albert Burge
CTS-11 | CTS-11 | PI08198 | Verified | Valve 1BMBH05AA751 - ground seal tite. | A | E | Dustin Futrell | McD | 2019-09-30 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-28 | Albert Burge
CTS-11 | CTS-11 | PI08199 | Verified | 1BMBH05CL202, 203, 204, 205 - ground seal tite. | A | E | Dustin Futrell | McD | 2019-09-30 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-09 | Albert Burge
CTS-11 | CTS-11 | PI09789 | Verified | Test Package CTS-T-1B-AF09 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
CTS-11 | CTS-11 | PI12597 | Verified | Replace evap. cooler pump motor A. | B | M | Michael Law | McD | 2019-10-29 | Michael Law | Const | 2019-12-02 | Joshua Sturgeon | 2020-01-09 | Kelvin Cook
CTS-11 | CTS-11 | PI13165 | Verified | Clean paint off llast chance screen | A | X | Sheri Fritz | PCI | 2019-11-20 | Sheri Fritz | Const |  |  | 2019-11-23 | Michael Law
CTS-11 | CTS-11 | PI16971 | Verified | Clean up inside 1BMBL30GH001; Air Intake System Power Distribution / Instrument Panel, GT B Inlet Air Filter House grating platform, East side | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-06 | Bernard Stasse
CTS-11 | CTS-11 | PI16972 | Verified | Panel ON / OFF Switch broken at 1BMBL30GH001; Air Intake System Power Distribution / Instrument Panel, GT B Inlet Air Filter House grating platform, West side | B | E | Mike Tabbert | McD | 2020-02-18 | Mike Tabbert | Comm | 2020-02-21 | Mike Tabbert | 2020-02-26 | John Watts
CTS-11 | CTS-11 | PI16973 | Verified | Two cables missing tags inside 1BMBL30GH001; Air Intake System Power Distribution / Instrument Panel, GT B Inlet Air Filter House grating platform, West side | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-05 | Chris Colvin | 2020-03-11 | John Watts
CTS-11 | CTS-11 | PI16974 | Verified | Heat shrink tags inside 1BMBL30GH001; Air Intake System Power Distribution / Instrument Panel, GT B Inlet Air Filter House grating platform, West side | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-06 | Bernard Stasse
CTS-11 | CTS-11 | PI16975 | Verified | Cable shields not insulated inside 1BMBL30GH001; Air Intake System Power Distribution / Instrument Panel, GT B Inlet Air Filter House grating platform, West side | B | E | Jonathan Donham | McD | 2020-02-18 | Jonathan Donham | Comm | 2020-03-26 | Jonathan Donham | 2020-04-06 | Bernard Stasse
CTS-11 | CTS-11 | PI16976 | Verified | Need panel schedule and wiring schematic for 1BMBL30GH001; Air Intake System Power Distribution / Instrument Panel, GT B Inlet Air Filter House grating platform, East side | C | E | Mike Tabbert | McD | 2020-02-18 | Mike Tabbert | Comm | 2020-02-21 | Mike Tabbert | 2020-04-06 | Bernard Stasse
CTS-11 | CTS-11 | PI16977 | Verified | Last conduit needs seal after cable is pulled at 1BMBL30GH001; Air Intake System Power Distribution / Instrument Panel, GT B Inlet Air Filter House grating platform, East side | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
CTS-11 | CTS-11 | PI16978 | Verified | Ground cables need to be dressed up, too close to 480V circuits at 1BMBL30GH001; Air Intake System Power Distribution / Instrument Panel, GT B Inlet Air Filter House grating platform, West side | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
CTS-11 | CTS-11 | PI16979 | Verified | Reinstall plastic circuit breaker covers inside 1BMBL30GH001; Air Intake System Power Distribution / Instrument Panel, GT B Inlet Air Filter House grating platform, West side | C | E | Jonathan Donham | McD | 2020-02-18 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-06 | Bernard Stasse
CTS-11 | CTS-11 | PI16980 | Verified | Adjust panel door, does not close properly at 1BMBL30GH001; Air Intake System Power Distribution / Instrument Panel, GT B Inlet Air Filter House grating platform, West side | C | E | Jonathan Donham | McD | 2020-02-18 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-06 | Bernard Stasse
CTS-11 | CTS-11 | PI16981 | Verified | Wires not terminated inside 1BMBL30GH001; Air Intake System Power Distribution / Instrument Panel, GT B Inlet Air Filter House grating platform, West side | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-05 | Fred Michael | 2020-03-11 | John Watts
CTS-11 | CTS-11 | PI16982 | Verified | Bottom door open / close mechanism is broken at Inlet Air Filter House North door at bottom level | B | M | Bobby Williams | McD | 2020-02-18 | Bobby Williams | Comm | 2020-02-25 | Tim Gallegos | 2020-03-06 | Nelson Eichelberger
CTS-11 | CTS-11 | PI16983 | Verified | Bottom door open / close mechanism is broken at Inlet Air Filter House North door at top level | B | M | Bobby Williams | McD | 2020-02-18 | Bobby Williams | Comm | 2020-02-25 | Tim Gallegos | 2020-03-06 | Nelson Eichelberger
CTS-11 | CTS-11 | PI16984 | Verified | 1BMBL30GH002; Air Intake Duct Differential Pressure Instrument Panel needs new label | C | I | Gonzalo Pena | McD | 2020-02-18 | Gonzalo Pena | Comm | 2020-02-24 | James Tanner | 2020-04-07 | Randy Carpenter
CTS-11 | CTS-11 | PI16985 | Verified | Two cables not tagged inside 1BMBL02AC301; Evaporator Cooler Control Panel, GT B Inlet Air Filter House grating platform, East side | B | E | Jonathan Donham | McD | 2020-02-18 | Jonathan Donham | Comm | 2020-03-26 | Jonathan Donham | 2020-04-07 | Randy Carpenter
CTS-11 | CTS-11 | PI16986 | Verified | Heat shrink tags inside 1BMBL02AC301; Evaporator Cooler Control Panel, GT B Inlet Air Filter House grating platform, East side | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-07 | Randy Carpenter
CTS-11 | CTS-11 | PI16987 | Verified | Dress up cables inside 1BMBL02AC301; Evaporator Cooler Control Panel, GT B Inlet Air Filter House grating platform, East side | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-06 | Bernard Stasse
CTS-11 | CTS-11 | PI16988 | Verified | Interior light does not work inisde 1BMBL02AC301; Evaporator Cooler Control Panel, GT B Inlet Air Filter House grating platform, East side | B | E | Jonathan Donham | McD | 2020-02-18 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-06 | Bernard Stasse
CTS-11 | CTS-11 | PI16989 | Verified | Need panel schedule inside 1BMBL02AC301; Evaporator Cooler Control Panel, GT B Inlet Air Filter House grating platform, East side | C | E | Mike Tabbert | McD | 2020-02-18 | Mike Tabbert | Comm | 2020-02-21 | Mike Tabbert | 2020-04-06 | Bernard Stasse
CTS-11 | CTS-11 | PI16990 | Verified | Adjust 1BMBL02AC301; Evaporator Cooler Control Panel door, does not close properly at Evaporator Cooler Control Panel, GT B Inlet Air Filter House grating platform, East side | C | E | Jonathan Donham | McD | 2020-02-18 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-06 | Bernard Stasse
CTS-11 | CTS-11 | PI16994 | Verified | Remove all scaffolding, boards, trash from GT B Inlet Air Filter House grating platform, West side | C | C | Alan Huntsman | McD | 2020-02-18 | Alan Huntsman | Comm | 2020-03-18 | Johnny Campbell | 2020-04-06 | Bernard Stasse
CTS-11 | CTS-11 | PI16995 | Verified | Adjust 1BMBL02AC301; Evaporator Cooler Control Panel door ground, currently getting pinched wearing off insulation, GT B Inlet Air Filter House grating platform, East side | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-03-06 | Nelson Eichelberger
CTS-11 | CTS-11 | PI16996 | Verified | 1BMBL02CF304; Flow Indicator is broken, Flow Indicator manifold, West side of Evap Cooler Skid, GT B Inlet Air Filter House grating platform, East side | B | I | Gonzalo Pena | McD | 2020-02-18 | Gonzalo Pena | Comm | 2020-03-04 | Tim Green | 2020-04-06 | Bernard Stasse
CTS-11 | CTS-11 | PI16997 | Verified | 1BMBL02CL201; Sump Level Transmitter flex cable is kinked, Evap Cooler Skid, GT B Inlet Air Filter House grating platform, East side | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2020-07-29 | John Watts
CTS-11 | CTS-11 | PI16998 | Verified | Tags missing on pumps, motors and valves at Evap Cooler Pump skid, GT B Inlet Air Filter House grating platform, East side | C | P | James Strange | MHI | 2020-02-18 | James Strange | Comm | 2020-04-08 | James Strange | 2020-07-29 | John Watts
CTS-11 | CTS-11 | PI16999 | Verified | Loose U-bolt nuts on MBL02AP202; Evap Cooler Pump B discharge, Evap Cooler Skid, GT B Inlet Air Filter House grating platform, East side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-01 | James Beech | 2020-07-29 | John Watts
CTS-11 | CTS-11 | PI17000 | Verified | Reinstall metal weather cover for 1BMBL02CF301; Flow Indicator at North side of Evap Cooler Skid, GT B Inet Air Filter House grating platform, East side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-01 | James Beech | 2020-07-29 | John Watts
CTS-11 | CTS-11 | PI17001 | Verified | Reinstall metal weather cover for 1BMBL02CF310; Flow Indicator Evap Cooler Skid, GT B Inet Air Filter House grating platform, East side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-08 | James Beech | 2020-07-29 | John Watts
CTS-11 | CTS-11 | PI17002 | Verified | PI-004; Evap Cooler Pump Discharge Pressure Gauge missing, West side of Evap Cooler skid, GT B Inet Air Filter House grating platform, East side | B | I | Gonzalo Pena | McD | 2020-02-18 | Gonzalo Pena | Comm | 2020-02-24 | James Tanner | 2020-02-26 | John Watts
CTS-11 | CTS-11 | PI17003 | Verified | Plug open ended conduit at Northwest corner of Evap Cooler skid, GT B Inet Air Filter House grating platform, East side | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-11 | CTS-11 | PI17004 | Verified | MBL02AP201; Evap Cooler Pump A Motor needs ground | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-14 | Mike Tabbert | 2020-04-07 | Randy Carpenter
CTS-11 | CTS-11 | PI17005 | Verified | MBL02AP202; Evap Cooler Pump B Motor needs ground | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-14 | Mike Tabbert | 2020-04-07 | Randy Carpenter
CTS-11 | CTS-11 | PI17006 | Verified | Vertical Evap Cooler piping alongside GT B Inlet Filter House missing u-bolt at first horizontal support, West side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-27 | James Beech | 2020-07-29 | John Watts
CTS-11 | CTS-11 | PI17007 | Verified | Loose bolt on PVC blind flange under Grat 21 (1st Filter House grating platform), GT B Inlet Filter House grating platform West side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-01 | James Beech | 2020-07-29 | John Watts
CTS-11 | CTS-11 | PI17008 | Verified | Vertical Evap Cooler piping alongside GT B Inlet Filter House at Grat 21 (1st Filter House grating platform) missing u-bolt at horizontal support, West side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-27 | James Beech | 2020-07-29 | John Watts
CTS-11 | CTS-11 | PI17009 | Verified | Vertical Evap Cooler piping alongside GT B Inlet Filter House at top grating platform missing u-bolt at horizontal support, West side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-27 | James Beech | 2020-08-14 | Nelson Eichelberger
CTS-11 | CTS-11 | PI18099 | Verified | 1B-CTS-MBL03, 1B-CTS-MBA01AE101, 1B-CTS-MNL01AT101 - SCPS ran both GTs to base load and did an inspection that showed hot spots on the evap cooler drift eliminators. This was due to the anti-icing air system that runs at all times below 95% base load. | C | M | James Strange | MHI | 2020-03-18 | James Strange | Comm | 2020-04-14 | James Strange | 2020-06-02 | Cintrel Spears
CTS-12 | CTS-12 | PI03164 | Verified | Grout 1B GT Casing Cooling Air Fan Unit Skid 1B-CTS-QEF13. | B | C | Johnny Campbell | McD | 2019-08-05 | Johnny Campbell | Const | 2019-08-14 | Johnny Campbell | 2019-08-20 | Joshua Sturgeon
CTS-12 | CTS-12 | PI03166 | Verified | Complete eng. Pipe rework. ISO 1B-CTS-PD-P40-0206-01. | A | P | Terry Deaton | McD | 2019-08-05 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-14 | Kelvin Cook
CTS-12 | CTS-12 | PI03168 | Verified | LM 13-72 internal - install SS wrap & hose clamp. ISO 1B-CTS-PS-7A0A-01. | B | P | Terry Deaton | McD | 2019-08-05 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-16 | Kelvin Cook
CTS-12 | CTS-12 | PI03170 | Verified | LM 13-72 internal - Torque all flanges & bend tabs. | A | P | Terry Deaton | McD | 2019-08-05 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-12 | CTS-12 | PI03172 | Verified | LM 13-72 external Install & tighten u-bolts. | B | P | Terry Deaton | McD | 2019-08-05 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-12 | CTS-12 | PI03175 | Verified | LM 13-72 external - Torque all flanges & bend tabs. | A | P | Terry Deaton | McD | 2019-08-05 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-12 | CTS-12 | PI03177 | Verified | Set spring can to cold setting 1B-CTS-PS-7A0A-03 | B | P | Damon Turner | McD | 2019-08-05 | Damon Turner | Const | 2019-08-16 | Terry Deaton | 2019-09-18 | Kelvin Cook
CTS-12 | CTS-12 | PI03199 | Verified | 1BCTSC0252, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-13 | Mike Tabbert
CTS-12 | CTS-12 | PI03200 | Verified | 1BCTSC0253, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-13 | Mike Tabbert
CTS-12 | CTS-12 | PI03201 | Verified | 1BCTSC0254, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-13 | Mike Tabbert
CTS-12 | CTS-12 | PI03202 | Verified | 1BCTSC0255, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-16 | Mike Tabbert
CTS-12 | CTS-12 | PI03203 | Verified | 1BCTSC0256, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-13 | Mike Tabbert
CTS-12 | CTS-12 | PI03204 | Verified | 1BCTSC0257, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-16 | Mike Tabbert
CTS-12 | CTS-12 | PI03205 | Verified | 1BCTSK0020, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-13 | Mike Tabbert
CTS-12 | CTS-12 | PI03206 | Verified | 1BCTSK0042, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-08 | Dustin Futrell | 2019-08-13 | Mike Tabbert
CTS-12 | CTS-12 | PI03207 | Verified | 1BCTSX0353, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Michael Law
CTS-12 | CTS-12 | PI03208 | Verified | 1BCTSX0354, Terminate Cable | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Michael Law
CTS-12 | CTS-12 | PI03209 | Verified | Install tubing going to valves 1B-CTS-QEF13AA701KA01 and 1B-CTS-QEF13AA702KA02 | A | I | Gonzalo Pena | McD | 2019-08-05 | Gonzalo Pena | Const | 2019-08-07 | Gonzalo Pena | 2019-08-14 | Mike Tabbert
CTS-12 | CTS-12 | PI03210 | Verified | Tail in cables going to valves 1B-CTS-QEF13AA701KA01 and 1B-CTS-QEF13AA702KA02 | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-16 | Mike Tabbert
CTS-12 | CTS-12 | PI03211 | Verified | Seal tight and conduit need to be completed going to valves 1B-CTS-QEF13AA701KA01 and 1B-CTS-QEF13AA702KA02 | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-16 | Mike Tabbert
CTS-12 | CTS-12 | PI03212 | Verified | 1BCTSK0020, terminate motor space heater after temporary power is removed. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
CTS-12 | CTS-12 | PI03213 | Verified | Ground Case Cooling fan skid to ground grid. | B | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-14 | Mike Tabbert
CTS-12 | CTS-12 | PI03214 | Verified | Install all sealtight grounds and tighten sealtight connectors at case cooling fan skid. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-14 | Mike Tabbert
CTS-12 | CTS-12 | PI03215 | Verified | Turn in all completion paperwork. | A | E | Dustin Futrell | McD | 2019-08-05 | Dustin Futrell | Const | 2019-08-15 | Dustin Futrell | 2019-08-16 | Mike Tabbert
CTS-12 | CTS-12 | PI03281 | Verified | LM-1373 - Relocate support to southside of 90 PS-05 23BOA | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-12 | CTS-12 | PI03319 | Verified | LM-1372 - Install proper gasket at 2nd flange for turbine connection. After air blows. | B | P | Damon Turner | McD | 2019-08-07 | Damon Turner | Const | 2019-08-16 | Terry Deaton | 2019-09-18 | Kelvin Cook
CTS-12 | CTS-12 | PI03822 | Verified | Complete pipe test & submit CCFs to turnover. | A | P | Terry Deaton | McD | 2019-08-13 | Terry Deaton | Const | 2019-08-15 | Terry Deaton | 2019-08-16 | Ed Gober
CTS-13 | CTS-13 | PI03107 | Verified | Disconnect handle needs to be replaced on GT Compressor Blade Washing Control Panel | B | E | Mike Tabbert | McD | 2019-08-03 | Mike Tabbert | Const | 2019-08-20 | Mike Tabbert | 2019-09-04 | Logan Holland
CTS-13 | CTS-13 | PI03108 | Verified | Seal conduits of GT Compressor Blade Washing Control Panel | A | E | Dustin Futrell | McD | 2019-08-03 | Dustin Futrell | Const | 2019-08-09 | Dustin Futrell | 2019-08-16 | Logan Holland
CTS-13 | CTS-13 | PI03109 | Verified | 1ASDD01AA702KA01 and 1BSDD01AA702KA01 solenoids cracked | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-13 | Michael Law
CTS-13 | CTS-13 | PI03110 | Verified | 1ASDD01AA702KA01 tubing support issue and tubing bent | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-07 | Gonzalo Pena | 2019-08-20 | Albert Burge
CTS-13 | CTS-13 | PI03111 | Verified | 1BSDD01AA702KA01 valve interferring with regulator | A | I | Gonzalo Pena | McD | 2019-08-03 | Gonzalo Pena | Const | 2019-08-07 | Gonzalo Pena | 2019-08-20 | Albert Burge
CTS-13 | CTS-13 | PI03218 | Verified | LM-01376 sheet 2 torque flange at both A & B | A | P | Terry Deaton | McD | 2019-08-06 | Terry Deaton | Const | 2019-08-07 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-13 | CTS-13 | PI03219 | Verified | LM-01368 sheet 2 torque all the flanges at ring for both A & B | A | P | Terry Deaton | McD | 2019-08-06 | Terry Deaton | Const | 2019-08-07 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-13 | CTS-13 | PI03220 | Verified | LM-01368 sheet 2 torque all the flanges on PS-02 | A | P | Terry Deaton | McD | 2019-08-06 | Terry Deaton | Const | 2019-08-07 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-13 | CTS-13 | PI03221 | Verified | LM-01368 sheet 2 torque all the flanges on PS-01 | A | P | Terry Deaton | McD | 2019-08-06 | Terry Deaton | Const | 2019-08-07 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-13 | CTS-13 | PI03222 | Verified | *CTS-PD-P41-0201-01 install hose clamps at all pipe supports | B | P | Terry Deaton | McD | 2019-08-06 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-20 | Kelvin Cook
CTS-13 | CTS-13 | PI03223 | Verified | *CTS-PD-P41-0202-01 install hose clamps at all pipe supports | B | P | James Beech | McD | 2019-08-06 | James Beech | Const | 2019-09-24 | Damon Turner | 2019-11-04 | Kelvin Cook
CTS-13 | CTS-13 | PI03224 | Verified | LM-01389 sheet 2 torque all flanges for both A & B | A | P | Terry Deaton | McD | 2019-08-06 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-13 | CTS-13 | PI03225 | Verified | LM-01361 sheet 2 torque all flanges for both A & B | A | P | Terry Deaton | McD | 2019-08-06 | Terry Deaton | Const | 2019-08-07 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-13 | CTS-13 | PI03226 | Verified | LM-01361 sheet 2 fix all supports | A | P | Terry Deaton | McD | 2019-08-06 | Terry Deaton | Const | 2019-08-07 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-13 | CTS-13 | PI03227 | Verified | LM-01375 sheet 2 torque all flanges for both A & B | A | P | Terry Deaton | McD | 2019-08-06 | Terry Deaton | Const | 2019-08-07 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-13 | CTS-13 | PI03228 | Verified | LM-01375 sheet 2 need to get back drain pot from Saint Charles Power station | B | P | Kelvin Cook | McD | 2019-08-06 | Kelvin Cook | Const | 2019-09-06 | Kelvin Cook | 2019-09-06 | Kelvin Cook
CTS-13 | CTS-13 | PI03282 | Verified | LM-1373 - Relocate support to southside of 90 PS-11 23BOA | B | P | Terry Deaton | McD | 2019-08-07 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-15 | Kelvin Cook
CTS-13 | CTS-13 | PI03539 | Verified | Remove garlock gasket and restore the row 4 blade washing water drain flange per LC-01626-45AOA-23, items G3, B4/5/6 are required. | A | P | Terry Deaton | McD | 2019-08-09 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-13 | Michael Law
CTS-13 | CTS-13 | PI03823 | Verified | Complete pipe test & submit CCFs to turnover. | A | P | Terry Deaton | McD | 2019-08-13 | Terry Deaton | Const | 2019-08-14 | Terry Deaton | 2019-08-14 | Ed Gober
CTS-13 | CTS-13 | PI04377 | Verified | Complete the water wash nozzle air blow per LC-01649. Restore system and complete tie wire. | B | M | Dillion Starkey | McD | 2019-08-21 | Dillion Starkey | Comm |  |  | 2019-10-24 | Brian Ballard
CTS-13 | CTS-13 | PI15892 | Verified | 10SDD01AP101 (GT Water Wash Pump) - Packing glands are not guarded for rotating equipment | C | M | Shane Crowe | McD | 2020-01-13 | Shane Crowe | Comm | 2020-02-05 | Shane Crowe | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16055 | Verified | Blade Wash Skid needs safety gate on platform | C | C | Tim Gallegos | McD | 2020-01-16 | Tim Gallegos | Comm | 2020-04-29 | Tim Gallegos | 2020-08-07 | Dave Goldak
CTS-13 | CTS-13 | PI16056 | Verified | Need concrete pad at bottom of Blade Wash Skid platform ladder | D | C | Alan Huntsman | McD | 2020-01-16 | Alan Huntsman | Comm | 2020-02-19 | Alan Huntsman | 2020-02-25 | John Watts
CTS-13 | CTS-13 | PI16058 | Verified | Complete insulation at Line No. 1-1A-CTS-0115, 1" drain line at GT Blade Wash Drain, north end, outside of GT A enclosure | C | Q | Josh Koerner | PCI | 2020-01-16 | Josh Koerner | Comm | 2020-06-18 | Josh Koerner | 2020-07-30 | Nelson Eichelberger
CTS-13 | CTS-13 | PI16059 | Verified | Cold gal all Unit A & B Online and Offline pipe supports | C | X | Jerry Smith | McD | 2020-01-16 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-04-08 | Bernard Stasse
CTS-13 | CTS-13 | PI16060 | Verified | Penetration plate has under flush nut at GT A Online and Offline pipe penetration to enclosure, East Side | C | M | Shane Crowe | McD | 2020-01-16 | Shane Crowe | Comm | 2020-03-27 | Shane Crowe | 2020-04-08 | Bernard Stasse
CTS-13 | CTS-13 | PI16061 | Verified | Complete all piping insulation Unit A & B Online and Offline piping | C | Q | Josh Koerner | PCI | 2020-01-16 | Josh Koerner | Comm | 2020-06-18 | Josh Koerner | 2020-07-30 | Nelson Eichelberger
CTS-13 | CTS-13 | PI16062 | Verified | Remove carbon contamination from Blade Wash Skid tank and control panel | C | C | Alan Huntsman | McD | 2020-01-16 | Alan Huntsman | Comm | 2020-03-11 | Alan Huntsman | 2020-04-08 | Bernard Stasse
CTS-13 | CTS-13 | PI16063 | Verified | Clean up Blade Wash Skid | C | C | Alan Huntsman | McD | 2020-01-16 | Alan Huntsman | Comm | 2020-03-18 | Johnny Campbell | 2020-04-08 | Bernard Stasse
CTS-13 | CTS-13 | PI16064 | Verified | Need touch up paint on GT Compressor Blade Washing Pump Motor | C | X | Jerry Smith | McD | 2020-01-16 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-04-06 | Bernard Stasse
CTS-13 | CTS-13 | PI16065 | Verified | Tags missing on 1" drain valves MBA01AA931 and MBA01AA932, 1" drain to A GT Compressor Wash Drain Header, inside enclosure | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16066 | Verified | Tags missing on 1" drain valves MBA01AA916 and MBA01AA917, 1" drain to A GT Compressor Wash Drain Header, inside enclosure | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16067 | Verified | Tags missing on 1" drain valves MBA01AA913 and MBA01AA914, 1" drain to A GT Compressor Wash Drain Header, inside enclosure | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16068 | Verified | Tags missing on 1" drain valves MBH01AA903 and MBH01AA904, 1" drain to A GT Compressor Wash Drain Header, inside enclosure | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16069 | Verified | Tags missing on 2" drain valves MBR01AA901 and MBR01AA903 Exhaust Duct Drain to GT A Compressor Washing Drain Pit | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16070 | Verified | Tag missing on 1" drain valve MBA02AA915, 1" drain to B GT Compressor Wash Drain Header, inside enclosure | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16071 | Verified | Tag missing on 1" drain valve MBA02AA906, 1" drain to B GT Compressor Wash Drain Header, inside enclosure | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16072 | Verified | Tag missing on 1" drain valve MBA02AA923, 1" drain to B GT Compressor Wash Drain Header, inside enclosure | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16073 | Verified | Tags missing on 1" drain valves MBA02AA909 and MBA02AA910 , 1" drain to B GT Compressor Wash Drain Header, inside enclosure | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16074 | Verified | Tag missing on 1" drain valve MBA02AA931, 1" drain to B GT Compressor Wash Drain Header, inside enclosure | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16075 | Verified | Tag missing on 1" drain valve MBA02AA916, 1" drain to B GT Compressor Wash Drain Header, inside enclosure | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16076 | Verified | Tag missing on 1" drain valve MBA02AA913, 1" drain to B GT Compressor Wash Drain Header, inside enclosure | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16077 | Verified | Tag missing on 1" drain valve MBA02AA904, 1" drain to B GT Compressor Wash Drain Header, inside enclosure | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16078 | Verified | Tag missing on 1" drain valve MBA02AA914, 1" drain to B GT Compressor Wash Drain Header, inside enclosure | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16079 | Verified | Tag missing on 2" drain valve MBA02AA901, 2" drain to B GT Compressor Wash Drain Header, Exhaust Duct Drain to GT B Compressor Washing Drain Pit | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16080 | Verified | Tag missing on 2" drain valve MBA02AA903, 2" drain to B GT Compressor Wash Drain Header, Exhaust Duct Drain to GT B Compressor Washing Drain Pit | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-13 | CTS-13 | PI16081 | Verified | Remove all tape, rope, wire, tie wraps and old unused tags throughout system | C | C | Johnny Campbell | McD | 2020-01-16 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2021-04-21 | John Watts
CTS-14 | CTS-14 | PI04985 | Verified | SFC transformer 10-CTS-MKE01GT0001 - Repair bottom vents on north & south sides of enclosure. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-09-23 | Dustin Futrell | 2019-12-12 | Fred Michael
CTS-14 | CTS-14 | PI04986 | Verified | SFC transformer 10-CTS-MKE01GT0001 - Clean inside & outside, remote duct tape. | C | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2020-04-14 | Chris Colvin | 2020-04-21 | Mike Tabbert
CTS-14 | CTS-14 | PI04987 | Verified | SFC transformer 10-CTS-MKE01GT0001 - Make up braids. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-10-07 | Mike Tabbert
CTS-14 | CTS-14 | PI04988 | Verified | SFC transformer 10-CTS-MKE01GT0001 - Weld conduit support on east side of enclosure. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-14 | CTS-14 | PI04989 | Verified | SFC transformer 10-CTS-MKE01GT0001 - Condulet covers missing on east side of enclosure. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CTS-14 | CTS-14 | PI04990 | Verified | SFC transformer 10-CTS-MKE01GT0001 - Grout conduit supports. | C | C | Johnny Campbell | McD | 2019-09-12 | Johnny Campbell | Const | 2019-12-09 | Jack Fields | 2019-12-12 | Fred Michael
CTS-14 | CTS-14 | PI04991 | Verified | SFC transformer 10-CTS-MKE01GT0001 - Ground transformer in 2 corners. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-20 | Dustin Futrell | 2019-09-26 | Logan Holland
CTS-14 | CTS-14 | PI04992 | Verified | SFC Enclosure 10-CTS-MKEGH0021 - Penetrations need edge guards. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-23 | Mike Tabbert
CTS-14 | CTS-14 | PI04993 | Verified | SFC Enclosure 10-CTS-MKEGH0021 - Seal pentrations after commissioning. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2020-03-24 | Chris Colvin | 2020-03-27 | Mike Tabbert
CTS-14 | CTS-14 | PI04994 | Verified | SFC Enclosure 10-CTS-MKEGH0021 - Remove blue plastic on top of SFC cubicle. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-23 | Mike Tabbert
CTS-14 | CTS-14 | PI04995 | Verified | SFC Enclosure 10-CTS-MKEGH0021 - Clean inside of all cabinets. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-23 | Mike Tabbert
CTS-14 | CTS-14 | PI04996 | Verified | SFC Enclosure 10-CTS-MKEGH0021 - Clean top of SFC bldg. including the air handling units. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-11-20 | Fred Michael
CTS-14 | CTS-14 | PI05753 | Verified | 10CTSH0003A1, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05754 | Verified | 10CTSH0003A2, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05755 | Verified | 10CTSH0003A3, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05756 | Verified | 10CTSH0003A4, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05757 | Verified | 10CTSH0003B1, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05758 | Verified | 10CTSH0003B2, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05759 | Verified | 10CTSH0003B3, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05760 | Verified | 10CTSH0003B4, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05761 | Verified | 10CTSH0003C1, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05762 | Verified | 10CTSH0003C2, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05763 | Verified | 10CTSH0003C3, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05764 | Verified | 10CTSH0003C4, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05765 | Verified | 10CTSH0003G1, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05766 | Verified | 10CTSH0003G2, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05767 | Verified | 10CTSH0003G3, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05768 | Verified | 10CTSH0003G4, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05769 | Verified | 10CTSH0004A1, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05770 | Verified | 10CTSH0004A2, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05771 | Verified | 10CTSH0004A3, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05772 | Verified | 10CTSH0004A4, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05773 | Verified | 10CTSH0004B1, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05774 | Verified | 10CTSH0004B2, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05775 | Verified | 10CTSH0004B3, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05776 | Verified | 10CTSH0004B4, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05777 | Verified | 10CTSH0004C1, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05778 | Verified | 10CTSH0004C2, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05779 | Verified | 10CTSH0004C3, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05780 | Verified | 10CTSH0004C4, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05781 | Verified | 10CTSH0004G1, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI16111 | Verified | Replace all panel covers after testing is complete inside the SFC Control Building | C | E | Jonathan Donham | McD | 2020-01-16 | Jonathan Donham | Comm | 2020-03-02 | Jonathan Donham | 2020-04-06 | Bernard Stasse
CTS-14 | CTS-14 | PI16112 | Verified | Clean up inside the SFC Control Building | C | C | Johnny Campbell | McD | 2020-01-16 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-04-07 | Randy Carpenter
CTS-14 | CTS-14 | PI16113 | Verified | Four empty conduit penetrations under SFC Control Building needs to be sealed, E side of bldg | C | E | Chris Colvin | McD | 2020-01-16 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-04-07 | Randy Carpenter
CTS-14 | CTS-14 | PI16114 | Verified | Clean and touch up paint all four lifting lugs on SFC Control Building | C | X | Jerry Smith | McD | 2020-01-16 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-04-06 | Bernard Stasse
CTS-14 | CTS-14 | PI16115 | Verified | Clean off roof of SFC Control Building | C | C | Johnny Campbell | McD | 2020-01-16 | Johnny Campbell | Comm | 2020-03-20 | Johnny Campbell | 2020-04-06 | Bernard Stasse
CTS-14 | CTS-14 | PI18176 | Verified | Mitsubishi commissioning paper work to submit after tuning and final testing are complete | C | M | Lonnie Peters | McD | 2020-03-23 | Lonnie Peters | Comm | 2020-04-01 | Lonnie Peters | 2020-04-01 | Eric Policarpio
CTS-15 | CTS-15 | PI01310 | Verified | Ground wire missing on the north east corner of Control Oil Skid | B | E | Luis Cantu | McD | 2019-05-31 | Luis Cantu | Const | 2019-05-31 | Shannon Savoy | 2019-06-14 | Mike Tabbert
CTS-15 | CTS-15 | PI01311 | Verified | Clean metal shavings out of Control Oil skid junction box | B | E | Luis Cantu | McD | 2019-05-31 | Luis Cantu | Const | 2019-05-31 | Shannon Savoy | 2019-06-17 | Shannon Scott
CTS-15 | CTS-15 | PI01312 | Verified | Clean the whole Control Oil Skid | B | E | Luis Cantu | McD | 2019-05-31 | Luis Cantu | Const | 2019-05-31 | Shannon Savoy | 2019-06-13 | Mike Tabbert
CTS-15 | CTS-15 | PI01313 | Verified | Condulet covers missing outside of the Control Oil Skid Enclosure near cable tray | B | E | Luis Cantu | McD | 2019-05-31 | Luis Cantu | Const | 2019-05-31 | Shannon Savoy | 2019-06-26 | Logan Holland
CTS-15 | CTS-15 | PI01314 | Verified | Clean metal shavings out of Control Oil Reservoir junction box | B | E | Luis Cantu | McD | 2019-05-31 | Luis Cantu | Const | 2019-05-31 | Shannon Savoy | 2019-06-26 | Logan Holland
CTS-15 | CTS-15 | PI01315 | Verified | Dress out wires in Control Oil Reservoir junction box | B | E | Luis Cantu | McD | 2019-05-31 | Luis Cantu | Const | 2019-05-31 | Shannon Savoy | 2019-06-17 | Shannon Scott
CTS-15 | CTS-15 | PI01316 | Verified | Too many grounds connected to one lug in Control Oil Reservoir junction box | B | E | Luis Cantu | McD | 2019-05-31 | Luis Cantu | Const | 2019-05-31 | Shannon Savoy | 2019-06-17 | Shannon Scott
CTS-15 | CTS-15 | PI01318 | Verified | Control oil tank needs plug. | A | M | Shane Crowe | McD | 2019-05-31 | Shane Crowe | Const | 2019-06-13 | Shane Crowe | 2019-07-22 | Danny Pase
CTS-15 | CTS-15 | PI01319 | Verified | Clean the control oil skid, tank, components. | C | M | Shane Crowe | McD | 2019-05-31 | Shane Crowe | Const | 2019-06-14 | Joshua Sturgeon | 2020-01-01 | Lonnie Peters
CTS-15 | CTS-15 | PI01320 | Verified | Control oil supply line needs u-bolt at tube steel inside enclosure. | B | P | James Beech | McD | 2019-05-31 | James Beech | Const | 2019-06-03 | Terry Deaton | 2020-01-01 | Lonnie Peters
CTS-15 | CTS-15 | PI01321 | Verified | Control oil supply to fuel gas purge air - split ring flange missing. | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-03 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-15 | CTS-15 | PI01322 | Verified | Restore all control oil piping at the fuel gas purge air unit. | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-15 | CTS-15 | PI01381 | Verified | MBX01BR214: Torque flange connection to FG/PA unit after pressure test. | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-15 | CTS-15 | PI01382 | Verified | MBX01BR161: Sheet 1: Pipe support 28AOC-PS-01 is not installed | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-15 | CTS-15 | PI01383 | Verified | MBX01BR161: Sheet 1: Pipe support 28AOC-PS-02 is not installed | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-15 | CTS-15 | PI01384 | Verified | MBX01BR161: Sheet 1: Pipe support 28AOC-PS-03 is not installed | A | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-06 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-15 | CTS-15 | PI01385 | Verified | MBX01BR098: Pipe support 28BOA-PS-01 Ubolt set as an anchor, no anchor bolts ss wrap on clamp installed. | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-07 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-15 | CTS-15 | PI01386 | Verified | MBX01BR203: Ubolt set as a guide, ss wrap is to short no clamp is installed | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-07 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-15 | CTS-15 | PI01387 | Verified | MBX01BR207: Pipe support 27BOB-PS-03 missing SS wrap, pipe clamps and u bolt. | B | P | Terry Deaton | McD | 2019-05-31 | Terry Deaton | Const | 2019-06-07 | Terry Deaton | 2019-06-10 | Kelvin Cook
CTS-15 | CTS-15 | PI01407 | Verified | 1ACTSK0137, Pull Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-04 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-15 | CTS-15 | PI01408 | Verified | 1ACTSK0025, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-04 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-15 | CTS-15 | PI01409 | Verified | 1ACTSK0074, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-04 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-15 | CTS-15 | PI01410 | Verified | 1ACTSK0090, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-04 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-15 | CTS-15 | PI01411 | Verified | 1ACTSK0093, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-07 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-15 | CTS-15 | PI01412 | Verified | 1ACTSK0094, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-07 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-15 | CTS-15 | PI01413 | Verified | 1ACTSK0150, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-04 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-14 | CTS-14 | PI05804 | Verified | 1ACTSC0218, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-17 | Mike Tabbert
CTS-14 | CTS-14 | PI05803 | Verified | 10CTSK0007, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-17 | Mike Tabbert
CTS-14 | CTS-14 | PI05802 | Verified | 10CTSK0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-18 | Mike Tabbert
CTS-14 | CTS-14 | PI05801 | Verified | 10CTSC0106, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-18 | Mike Tabbert
CTS-14 | CTS-14 | PI05800 | Verified | 10CTSC0102, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-18 | Mike Tabbert
CTS-14 | CTS-14 | PI05799 | Verified | 10CTSC0006, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-18 | Mike Tabbert
CTS-14 | CTS-14 | PI05798 | Verified | 10CTSC0005, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-18 | Mike Tabbert
CTS-14 | CTS-14 | PI05797 | Verified | 10CTSC0002, To Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-17 | Mike Tabbert
CTS-14 | CTS-14 | PI05796 | Verified | 1BCTSC0218, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-23 | Mike Tabbert
CTS-14 | CTS-14 | PI05795 | Verified | 1BCTSC0185, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-18 | Mike Tabbert
CTS-14 | CTS-14 | PI05794 | Verified | 1ACTSC0218, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-23 | Mike Tabbert
CTS-14 | CTS-14 | PI05793 | Verified | 1ACTSC0203, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-09-17 | Mike Tabbert
CTS-14 | CTS-14 | PI05792 | Verified | 1ACTSC0202, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-23 | Mike Tabbert
CTS-14 | CTS-14 | PI05791 | Verified | 1ACTSC0201, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-23 | Mike Tabbert
CTS-14 | CTS-14 | PI05790 | Verified | 10CTSK0007, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-23 | Mike Tabbert
CTS-14 | CTS-14 | PI05789 | Verified | 10CTSK0001, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-14 | CTS-14 | PI05788 | Verified | 10CTSC0106, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-14 | CTS-14 | PI05787 | Verified | 10CTSC0102, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-17 | Dustin Futrell | 2019-09-17 | Mike Tabbert
CTS-14 | CTS-14 | PI05786 | Verified | 10CTSC0006, From Termination | B | E | Chris Boudreaux | McD | 2019-09-12 | Chris Boudreaux | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
CTS-14 | CTS-14 | PI05785 | Verified | 10CTSC0004, From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-23 | Mike Tabbert
CTS-14 | CTS-14 | PI05784 | Verified | 10CTSH0004G4, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05783 | Verified | 10CTSH0004G3, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-14 | CTS-14 | PI05782 | Verified | 10CTSH0004G2, Terminate both ends | B | E | Logan Holland | McD | 2019-09-12 | Logan Holland | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Michael Law
CTS-15 | CTS-15 | PI01414 | Verified | 1ACTSX0308, Terminate Cable | A | E | Shannon Savoy | McD | 2019-06-03 | Shannon Savoy | Const | 2019-06-04 | Shannon Savoy | 2019-06-07 | Mike Tabbert
CTS-15 | CTS-15 | PI01415 | Verified | 1ACTSX0309, Terminate Cable | A | E | Luis Cantu | McD | 2019-06-03 | Luis Cantu | Const | 2019-06-04 | Shannon Savoy | 2019-06-13 | Mike Tabbert
CTS-15 | CTS-15 | PI01416 | Verified | Control Oil Skid needs grout. | A | C | Johnny Campbell | McD | 2019-06-03 | Johnny Campbell | Const | 2019-06-03 | Johnny Campbell | 2019-06-03 | Joshua Sturgeon
CTS-15 | CTS-15 | PI01417 | Verified | Remove excess grout and concrete and seal oil skid. | B | C | Johnny Campbell | McD | 2019-06-03 | Johnny Campbell | Const | 2019-06-03 | Johnny Campbell | 2019-06-14 | Neil Simon
CTS-15 | CTS-15 | PI03533 | Verified | Secure all CO return pipe support hardware and tie wire all CO supply flanges inside the GT enclosure | B | P | Dillion Starkey | McD | 2019-08-09 | Dillion Starkey | Const |  |  | 2019-11-08 | Brian Ballard
CTS-15 | CTS-15 | PI04431 | Verified | Install missing bolt for the CO supply flange. | B | M | Dillion Starkey | McD | 2019-08-21 | Dillion Starkey | Comm |  |  | 2019-10-24 | Brian Ballard
CTS-15 | CTS-15 | PI04481 | Verified | Bend all lock washers for the CO return flanges and complete tie-wire for all the CO supply flanges inside the FGPA unit. | B | M | Lonnie Peters | McD | 2019-08-21 | Lonnie Peters | Comm | 2020-01-09 | Lonnie Peters | 2020-01-15 | Ron McMurtry
CTS-15 | CTS-15 | PI16082 | Verified | Bend flange bolt tabs at PGG02AA011; Safety Relief Valve discharge line, outside of GT A Lube Oil Enclosure, W side of enclosure at penetration | B | P | Bobby Williams | McD | 2020-01-16 | Bobby Williams | Comm | 2020-01-23 | Charlie English | 2020-02-02 | Shannon Scott
CTS-15 | CTS-15 | PI16083 | Verified | PGG02AA011; Safety Relief Valve discharge line needs to be extended to centerline of floor drain, outside of GT A Lube Oil Enclosure, W side of enclosure | B | P | Bobby Williams | McD | 2020-01-16 | Bobby Williams | Comm | 2020-02-07 | Kelvin Cook | 2020-02-10 | Kelvin Cook
CTS-15 | CTS-15 | PI16084 | Verified | Double nut all U-Bolts on Control Oil Piping outside of GT A Lube Oil Enclosure | C | P | Bobby Williams | McD | 2020-01-16 | Bobby Williams | Comm | 2020-02-11 | Charlie English | 2020-02-15 | Shannon Scott
CTS-15 | CTS-15 | PI16085 | Verified | Clean out GT A Lube Oil sump | C | C | Johnny Campbell | McD | 2020-01-16 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-04-07 | Randy Carpenter
CTS-15 | CTS-15 | PI16086 | Verified | Hang existing tags on each respective GT Control Oil Return Filter housing, tags currently wire tied together | C | P | James Beech | McD | 2020-01-16 | James Beech | Comm | 2020-05-19 | Tim Green | 2021-04-21 | John Watts
CTS-15 | CTS-15 | PI16087 | Verified | Need flange guard at outlet flange of GT Control Oil Cooler | C | P | Bobby Williams | McD | 2020-01-16 | Bobby Williams | Comm | 2020-02-06 | Charlie English | 2020-02-15 | Shannon Scott
CTS-15 | CTS-15 | PI16088 | Verified | Repair Control Oil piping penetration seals at West side GT A Lube Oil Enclosure | C | C | Tim Gallegos | McD | 2020-01-16 | Tim Gallegos | Comm | 2020-05-07 | Tim Gallegos | 2020-08-14 | Nelson Eichelberger
CTS-15 | CTS-15 | PI16089 | Verified | 1.25" GT A Control Oil Supply line U-Bolt missing nuts, first horizontal pipe support outside of GT A Lube Oil Enclosure, East side | C | P | Bobby Williams | McD | 2020-01-16 | Bobby Williams | Comm | 2020-02-06 | Charlie English | 2020-02-10 | Shannon Scott
CTS-15 | CTS-15 | PI16090 | Verified | Tag all components at MBX11AT101; GT Control Oil Cleaning Unit | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-04 | Kelvin Cook | 2020-04-06 | Bernard Stasse
CTS-15 | CTS-15 | PI16091 | Verified | Finish lock wiring flange bolts at 1.25" Control Oil Supply line and install splash guard, W side of Control Oil Skid | B | P | Bobby Williams | McD | 2020-01-16 | Bobby Williams | Comm | 2020-02-06 | Charlie English | 2020-02-10 | Shannon Scott
CTS-15 | CTS-15 | PI16092 | Verified | Finish lock wiring flange bolts at 2" Control Oil Supply line and install splash guard, W side of Control Oil Skid | B | P | Bobby Williams | McD | 2020-01-16 | Bobby Williams | Comm | 2020-02-06 | Charlie English | 2020-02-10 | Shannon Scott
CTS-15 | CTS-15 | PI16093 | Verified | Move tags to each individual component at GT Control Oil Accumulator A-C, tags currently wire tied together at each Accumulator | C | P | James Beech | McD | 2020-01-16 | James Beech | Comm | 2020-05-19 | Tim Green | 2021-04-21 | John Watts
CTS-15 | CTS-15 | PI16094 | Verified | Move Emergency Trip Valve tag from valve handle to back wall of panel | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-04 | Kelvin Cook | 2020-02-10 | Shannon Scott
CTS-15 | CTS-15 | PI16095 | Verified | Replace all tag holders with twisted wire to briaded wire throughout system | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-07 | Randy Carpenter
CTS-15 | CTS-15 | PI16096 | Verified | Clean up grating under Fuel Gas Control Valve Enclosure, GT A Fuel Gas Control Valve enclosure, West side of GT A | C | C | Johnny Campbell | McD | 2020-01-16 | Johnny Campbell | Comm | 2020-04-30 | Johnny Campbell | 2021-04-21 | John Watts
CTS-15 | CTS-15 | PI16097 | Verified | Change out condolet cover that does not match other existing condolets, below GT Fuel Gas Main A Control Valve, GT A Fuel Gas Control Valve enclosure, West side of GT A | D | E | Chris Colvin | McD | 2020-01-16 | Chris Colvin | Comm | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
CTS-15 | CTS-15 | PI16098 | Verified | Straighten flange rubber boot at MBX01AA135; Inlet Isolation Valve to GT A Inlet Guide Vane | C | P | James Beech | McD | 2020-01-16 | James Beech | Comm | 2020-05-26 | James Beech | 2021-05-27 | John Watts
CTS-15 | CTS-15 | PI16099 | Verified | Return valve from GT A Inlet Guide Van needs tag | C | P | Tim Green | McD | 2020-01-16 | Tim Green | Comm | 2020-06-15 | Tim Green | 2021-04-21 | John Watts
CTS-15 | CTS-15 | PI16100 | Verified | Clean up Control Oil Skid | C | P | Johnny Campbell | McD | 2020-01-16 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-04-07 | Randy Carpenter
CTS-15 | CTS-15 | PI16101 | Verified | Repair oil leak at MBX01CP253; Pressure Switch at North end of Control Oil Skid | B | P | William Mitchell | McD | 2020-01-16 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-10 | John Watts
CTS-15 | CTS-15 | PI16102 | Verified | Remove all tape, wire, rope, unused wire tires, and unused tags and signs from system piping and components | C | C | Johnny Campbell | McD | 2020-01-16 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-04-07 | Randy Carpenter
CTS-15 | CTS-15 | PI16103 | Verified | Need touch up paint throughout system | C | X | Jerry Smith | McD | 2020-01-16 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-04-06 | Bernard Stasse
CTS-15 | CTS-15 | PI16104 | Verified | Tag all system components | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-06 | Bernard Stasse
CTS-16 | CTS-16 | PI01099 | Verified | Check for any missing flange covers on the control oil skid. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-05-23 | Terry Deaton | 2019-11-04 | Kelvin Cook
CTS-16 | CTS-16 | PI01100 | Verified | Replace dessicant after initial fill. | B | M | Lonnie Peters | McD | 2019-05-20 | Lonnie Peters | Const |  |  | 2020-01-13 | Fred Michael
CTS-16 | CTS-16 | PI01101 | Verified | Replace plastic plug with NPT plug on the control oil tank. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-22 | Terry Deaton | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01102 | Verified | Restore all piping. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-23 | Terry Deaton | 2019-08-28 | Kelvin Cook
CTS-16 | CTS-16 | PI01103 | Verified | Clean the control oil skid. | B | C | Johnny Campbell | McD | 2019-05-20 | Johnny Campbell | Const | 2019-07-17 | Michael Law | 2020-01-01 | Lonnie Peters
CTS-16 | CTS-16 | PI01104 | Verified | Remove all control oil skid forms. | B | C | Johnny Campbell | McD | 2019-05-20 | Johnny Campbell | Const | 2019-06-25 | Jack Fields | 2020-01-01 | Lonnie Peters
CTS-16 | CTS-16 | PI01105 | Verified | All control oil supply lines need lock wires. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-06-06 | Terry Deaton | 2019-11-24 | Brian Ballard
CTS-16 | CTS-16 | PI01106 | Verified | Connect control oil supply & return piping in the fuel gas purge air compartment. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-28 | Terry Deaton | 2019-08-22 | Brian Ballard
CTS-16 | CTS-16 | PI01107 | Verified | Install shim plates on supports outside of the fuel gas purge air unit. | B | P | James Beech | McD | 2019-05-20 | James Beech | Const | 2019-06-06 | Terry Deaton | 2019-11-24 | Brian Ballard
CTS-16 | CTS-16 | PI01108 | Verified | Fuel gas purge air emergency trip flange connection has wrong bolts installed. Need hex head. | A | P | Terry Deaton | McD | 2019-05-20 | Terry Deaton | Const | 2019-05-28 | Terry Deaton | 2019-06-03 | Kelvin Cook
CTS-16 | CTS-16 | PI01110 | Verified | Sheet 2: 27BOA-PS-01 needs grout | C | C | Johnny Campbell | McD | 2019-05-20 | Johnny Campbell | Const | 2019-05-22 | Johnny Campbell | 2019-06-17 | Kelvin Cook
CTS-16 | CTS-16 | PI01111 | Verified | Sheet 2: 28BOA-PS-01 needs grout | C | C | Johnny Campbell | McD | 2019-05-20 | Johnny Campbell | Const | 2019-05-22 | Johnny Campbell | 2019-06-17 | Kelvin Cook
CTS-16 | CTS-16 | PI01114 | Verified | Control Oil Skid needs grout. | A | C | Johnny Campbell | McD | 2019-05-22 | Johnny Campbell | Const | 2019-05-24 | Johnny Campbell | 2019-06-21 | Joshua Sturgeon
CTS-16 | CTS-16 | PI01116 | Verified | Seal all conduits in the GT Control Package. | B | E | Chris Colvin | McD | 2019-05-22 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
CTS-16 | CTS-16 | PI01122 | Verified | Replace the self-tapping screws with nuts & bolts (or cover with rubber grommets) in the Control Oil Cleaning Unit box 1BMBX11AT101. Screws protrude too high inside box. | B | E | Keith Mahoney | MHI | 2019-05-22 | Keith Mahoney | Const | 2019-09-06 | Keith Mahoney | 2019-09-06 | Keith Mahoney
CTS-16 | CTS-16 | PI01132 | Verified | 1BCTSX0308, Pull Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01133 | Verified | 1BCTSC0180, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01134 | Verified | 1BCTSC0292, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01135 | Verified | 1BCTSC0300, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01136 | Verified | 1BCTSC0311, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01137 | Verified | 1BCTSK0041, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01139 | Verified | 1BCTSK0059, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01140 | Verified | 1BCTSK0074, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01141 | Verified | 1BCTSK0089, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01142 | Verified | 1BCTSK0090, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01143 | Verified | 1BCTSK0091, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01144 | Verified | 1BCTSK0130, Terminate Cable | A | E | Luis Cantu | McD | 2019-05-22 | Luis Cantu | Const | 2019-06-21 | Luis Cantu | 2019-06-24 | Mike Tabbert
CTS-16 | CTS-16 | PI01145 | Verified | 1BCTSK0131, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01146 | Verified | 1BCTSK0136, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01147 | Verified | 1BCTSK0137, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01148 | Verified | 1BCTSK0150, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01149 | Verified | 1BCTSX0308, Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-22 | Shannon Savoy | Const | 2019-05-23 | Shannon Savoy | 2019-05-23 | Mike Tabbert
CTS-16 | CTS-16 | PI01150 | Verified | 1BCTSK0093, Terminate Cable. | B | E | Dustin Futrell | McD | 2019-05-22 | Dustin Futrell | Const | 2019-09-09 | Dustin Futrell | 2019-09-18 | Mike Tabbert
CTS-16 | CTS-16 | PI01151 | Verified | 1BCTSK0094, Terminate Cable. | B | E | Dustin Futrell | McD | 2019-05-22 | Dustin Futrell | Const | 2019-08-01 | Dustin Futrell | 2019-09-18 | Mike Tabbert
CTS-16 | CTS-16 | PI16858 | Verified | Remove tape from Unit B GT Control Oil Pump A; MBX01AP101 coupling guard | C | M | Shane Crowe | McD | 2020-02-18 | Shane Crowe | Comm | 2020-03-19 | Shane Crowe | 2020-04-06 | Bernard Stasse
CTS-16 | CTS-16 | PI16859 | Verified | Check all B GT Control Oil Pressure Indicators and associated valves for leaks | B | I | Lonnie Peters | McD | 2020-02-18 | Lonnie Peters | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-16 | CTS-16 | PI16860 | Verified | Replace desicant at B GT Control Oil Supply Filter A; MBX01AT102 - on order 3/26 | C | P | Lonnie Peters | McD | 2020-02-18 | Lonnie Peters | Comm | 2020-04-14 | Lonnie Peters | 2020-07-29 | John Watts
CTS-16 | CTS-16 | PI16861 | Verified | Hold down fasteners missing in enclosure sump grating, grating is loose, North West side of Control Oil Skid | C | C | Tim Gallegos | McD | 2020-02-18 | Tim Gallegos | Comm | 2020-05-07 | Tim Gallegos | 2020-11-25 | Dave Goldak
CTS-16 | CTS-16 | PI16862 | Verified | B GT Control Oil Supply Filter A; MBX01AT102 leaks during operation | B | P | Lonnie Peters | McD | 2020-02-18 | Lonnie Peters | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-16 | CTS-16 | PI16863 | Verified | B GT Control Oil Supply Filter ; MBX01AT103 leaks during operation | B | P | Lonnie Peters | McD | 2020-02-18 | Lonnie Peters | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-16 | CTS-16 | PI16864 | Verified | Place all grouped tags on individual components at Control Oil Skid | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-28 | James Beech | 2020-11-25 | Dave Goldak
CTS-16 | CTS-16 | PI16865 | Verified | Need plastic cover on end of electrical uni-strut support at North East corner of Control Oil skid | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-04-29 | Matt Gilmore | 2020-11-25 | Dave Goldak
CTS-16 | CTS-16 | PI16866 | Verified | Missing screw in condolet cover at Control Oil Trip Valve Junction Box at Control Oil skid | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-04-29 | Matt Gilmore | 2020-11-25 | Dave Goldak
CTS-16 | CTS-16 | PI16867 | Verified | Temperature Control Valve; 1BPGG01AA701 leaks during operation | B | I | Lonnie Peters | McD | 2020-02-18 | Lonnie Peters | Comm | 2020-03-10 | Lonnie Peters | 2020-03-10 | John Watts
CTS-16 | CTS-16 | PI16868 | Verified | Tighten Control Oil Trip Valve Junction Box cover | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-04-29 | Matt Gilmore | 2020-11-25 | Dave Goldak
CWC-01 | CWC-01 | PI04275 | Verified | 10-CWC-CP-0300 - ground back plate in panel. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
CWC-01 | CWC-01 | PI04276 | Verified | 10-CWC-CP-0500 - ground back plate in panel. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
CWC-01 | CWC-01 | PI04277 | Verified | 10-CWC-CP-0500 - Change literature on wire tags 10CWCX0005-1, -2, -3 & -4 in panel. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-21 | Fred Michael
CWC-01 | CWC-01 | PI04278 | Verified | 10-CWC-CP-0200 - ground back plate in panel. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
CWC-01 | CWC-01 | PI04279 | Verified | 10-CWC-CP-0200 - Change literature on wire tags 10CWCX0002-1, -2, -3 & -4 in panel. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-21 | Fred Michael
CWC-01 | CWC-01 | PI04280 | Verified | 10-CWC-CP-0200 - missing fuse. | A | E | Mike Tabbert | McD | 2019-08-16 | Mike Tabbert | Const | 2019-08-26 | Mike Tabbert | 2020-01-16 | Michael Law
CWC-01 | CWC-01 | PI04281 | Verified | Duct seal all conduits in all panels. | B | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Fred Michael
CWC-01 | CWC-01 | PI04282 | Verified | 10-CWC-CP-0400 - ground back plate in panel. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
CWC-01 | CWC-01 | PI04283 | Verified | 10-CWC-CP-0400 - Change literature on wire tags 10CWCX0004-1, -2, -3 & -4 in panel. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-21 | Fred Michael
CWC-01 | CWC-01 | PI04284 | Verified | 10-DCS-CAB-0301 in PDC - 10CWCX0004-3 & 4-4 are tagged wrong. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-21 | Fred Michael
CWC-01 | CWC-01 | PI04285 | Verified | All flex on skids needs to be changed. | D | E | Michael Law | McD | 2019-08-16 | Michael Law | Const | 2020-02-04 | Michael Law | 2020-02-04 | Michael Law
CWC-01 | CWC-01 | PI04286 | Verified | 10-CWC-M-0400B missing motor cover bolt. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
CWC-01 | CWC-01 | PI04287 | Verified | 10-CWC-CP-0100 - ground back plate in panel. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
CWC-01 | CWC-01 | PI04288 | Verified | 10-CWC-CP-0100 - Change literature on wire tags 10CWCX0001-1, -2, -3 & -4 in panel. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-21 | Fred Michael
CWC-01 | CWC-01 | PI04289 | Verified | Ground skid 10-CWC-SKD-0100. | A | E | Chris Colvin | McD | 2019-08-16 | Chris Colvin | Const | 2019-08-28 | Dustin Futrell | 2020-01-13 | Fred Michael
CWC-01 | CWC-01 | PI04290 | Verified | 10-CWC-CP-0100 - 10CWCK0001-1, -2, -3 not termed to breakers. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
CWC-01 | CWC-01 | PI04291 | Verified | 10-CWC-LI-0100 - local display- not installed. | A | I | Mike Tabbert | McD | 2019-08-16 | Mike Tabbert | Const | 2019-09-26 | Gonzalo Pena | 2019-10-09 | Albert Burge
CWC-01 | CWC-01 | PI04292 | Verified | 10-CWC-PI-0202 - PVC broke, re-install PI. | A | I | James Beech | McD | 2019-08-16 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-09 | Kelvin Cook
CWC-01 | CWC-01 | PI04293 | Verified | 10-CWC-BPV-0401 - PVC broke, re-install PV. | A | I | Gonzalo Pena | McD | 2019-08-16 | Gonzalo Pena | Const |  |  | 2019-11-09 | Kelvin Cook
CWC-01 | CWC-01 | PI04294 | Verified | 10-CWC-DMP-0401 not installed. | A | I | Gonzalo Pena | McD | 2019-08-16 | Gonzalo Pena | Const | 2019-11-01 | Gonzalo Pena | 2019-12-12 | Fred Michael
CWC-01 | CWC-01 | PI04295 | Verified | 10CWC-LIT-0100 - Re-locate from nozzle L1 to nozzle L2. | A | I | Gonzalo Pena | McD | 2019-08-16 | Gonzalo Pena | Const | 2019-09-11 | Gonzalo Pena | 2019-09-16 | Albert Burge
CWC-01 | CWC-01 | PI04296 | Verified | 10-CWC-LI-0300 not installed. | B | I | Mike Tabbert | McD | 2019-08-16 | Mike Tabbert | Const |  |  | 2019-10-18 | Mike Tabbert
CWC-01 | CWC-01 | PI04297 | Verified | 10-CWC-LIT-0300 not installed. | A | I | Gonzalo Pena | McD | 2019-08-16 | Gonzalo Pena | Const | 2019-09-06 | Gonzalo Pena | 2019-09-20 | Mike Tabbert
CWC-01 | CWC-01 | PI04298 | Verified | 10-CWC-SRV-0102A & 0102B are incorrectly tagged as 101A & 101B. | B | I | Gonzalo Pena | McD | 2019-08-16 | Gonzalo Pena | Const | 2019-09-06 | Gonzalo Pena | 2019-09-20 | Martin Perry
CWC-01 | CWC-01 | PI04299 | Verified | Tie duct bank grounds to grid ground. | B | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-28 | Mike Tabbert
CWC-01 | CWC-01 | PI04300 | Verified | Bond conduits at duct bank. | B | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-11 | Fred Michael
CWC-01 | CWC-01 | PI04301 | Verified | Terminate 10CWCX0012, from & to. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const |  |  | 2019-10-04 | Michael Law
CWC-01 | CWC-01 | PI04302 | Verified | Terminate 10CWCX0014, from & to. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const |  |  | 2019-10-04 | Michael Law
CWC-01 | CWC-01 | PI04303 | Verified | Terminate 10CWX0002, To termination. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CWC-01 | CWC-01 | PI04304 | Verified | Terminate 10CWX0003, To termination. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CWC-01 | CWC-01 | PI04305 | Verified | Terminate 10CWX0004, To termination. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CWC-01 | CWC-01 | PI04306 | Verified | Terminate 10CWX0005, To termination. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-11 | Mike Tabbert
CWC-01 | CWC-01 | PI04307 | Verified | Terminate 10CWX0011, To termination. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const |  |  | 2019-10-04 | Michael Law
CWC-01 | CWC-01 | PI04308 | Verified | Terminate 10CWX0013, To termination. | A | E | Dustin Futrell | McD | 2019-08-16 | Dustin Futrell | Const |  |  | 2019-10-04 | Michael Law
CWC-01 | CWC-01 | PI06786 | Verified | Complete CWC line 0035 - connection at cooling tower basin, north side. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-16 | James Beech | 2020-01-21 | Michael Law
CWC-01 | CWC-01 | PI08064 | Verified | On ISO 10-CWC-PD-P40-0100-01 pipe spool 0100-2 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-04 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08065 | Verified | On ISO 10-CWC-PD-P40-0100-01 flange connection 10-CWC-T-0100/A1 missing hardware | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-16 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08066 | Verified | On ISO 10-CWC-PD-P40-0100-01 pipe support 10-CWC-PD-HGR-0009 is not connected | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08067 | Verified | On ISO 10-CWC-PD-P40-0120-01 pipe support 10-CWC-PD-HGR-0025 & 0026 are not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08068 | Verified | On ISO 10-CWC-PD-P40-0120-01 missing hardware at 10-CWC-T-0100/D1 | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08069 | Verified | On ISO 10-CWC-PD-P40-0120-01 trim length at grating to allow min slope | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08070 | Verified | ISO 10-CWC-PD-P41-0110-01 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08071 | Verified | ISO 10-CWC-PD-P41-0130-01 fix bend, out of plumb needs full threaded engagement | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08072 | Verified | ISO 10-CWC-PD-P41-0130-01 connection to 10-CWC-T-0100/V1 missing hardware | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08073 | Verified | ISO 10-CWC-PD-P41-0130-02 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08074 | Verified | ISO 10-CWC-PD-P41-0140-01 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-09 | Kelvin Cook
CWC-01 | CWC-01 | PI08075 | Verified | ISO 10-CWC-PD-P41-0140-02 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-09 | Kelvin Cook
CWC-01 | CWC-01 | PI08076 | Verified | On ISO 10-CWC-PD-P41-150-01 pipe support 10-CWC-PD-HGR-0053 & 0049 is not connected | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08077 | Verified | On ISO 10-CWC-PD-P41-150-01 pipe support 10-CWC-PD-HGR-0052 is out of plumb | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08078 | Verified | On ISO 10-CWC-PD-P41-150-01 missing hardware at connection 10-CWC-SKD-01000/TP-26 | A | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08079 | Verified | On ISO 10-CWC-PD-P41-150-01 remove tape from vent to the containment | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08080 | Verified | On ISO 10-CWC-PD-P41-150-02 pipe spool 0150-1 needs pipe strap down to tray every 6" | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08081 | Verified | On ISO 10-CWC-PD-P41-150-02 pipe spool 0150-1 2 pipe is sitting on unistrut requires platic sleeve and unistrut clamps. | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08082 | Verified | On ISO 10-CWC-PD-P41-150-03 pipe support 10-CWC-PD-HGR-0800 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08083 | Verified | On ISO 10-CWC-PD-P41-150-03 field weld connecting to ISO 10-CWC-PD-P41-0150-02 is not made yet | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08084 | Verified | On ISO 10-CWC-PD-P41-150-03 item 3 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08085 | Verified | On ISO 10-CWC-PD-P41-150-03 remove tape from spool 0150-4 | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08086 | Verified | On ISO 10-CWC-PD-P41-0210-01 missing hardware at connection to 10-CWC-SKD-0200/ TP-30 | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08087 | Verified | On ISO 10-CWC-PD-P41-0210-01 spool that valve 10-CWC-V-0240 is located is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08088 | Verified | On ISO 10-CWC-PD-P41-0210-01 spool connecting to ISO 10-CWC-PD-P41-0210-02 is not connected | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08089 | Verified | On ISO 10-CWC-PD-P41-0210-02 item 3 is not connected | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08090 | Verified | On ISO 10-CWC-PD-P41-0210-02 just item 3 at the 90 shorten pipe run so it is not on top of ss pipe | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08091 | Verified | On ISO 10-CWC-PD-P41-0210-02 strap pipe down to tray every 6" | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08092 | Verified | On ISO 10-CWC-PD-P41-0210-03 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08093 | Verified | On ISO 10-CWC-PD-P41-0300-01 is not installed | B | P | Shannon Scott | ENT | 2019-09-30 | Shannon Scott | Const |  |  | 2019-12-09 | Shannon Scott
CWC-01 | CWC-01 | PI08094 | Verified | On ISO 10-CWC-PD-P41-0300-02 is not installed | A | P | Kelvin Cook | McD | 2019-09-30 | Kelvin Cook | Const |  |  | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08095 | Verified | On ISO 10-CWC-PD-P41-0310-01 is not installed | A | P | Kelvin Cook | McD | 2019-09-30 | Kelvin Cook | Const |  |  | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08096 | Verified | On ISO 10-CWC-PD-P41-0310-02 is not installed | A | P | Kelvin Cook | McD | 2019-09-30 | Kelvin Cook | Const |  |  | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08097 | Verified | On ISO 10-CWC-PD-P41-0320-01 is not installed | A | P | Kelvin Cook | McD | 2019-09-30 | Kelvin Cook | Const |  |  | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08098 | Verified | On ISO 10-CWC-PD-P41-0322-01 is not installed | A | P | Kelvin Cook | McD | 2019-09-30 | Kelvin Cook | Const |  |  | 2019-11-09 | Kelvin Cook
CWC-01 | CWC-01 | PI08099 | Verified | On ISO 10-CWC-PD-P41-0322-02 is not installed | A | P | Kelvin Cook | McD | 2019-09-30 | Kelvin Cook | Const |  |  | 2019-11-09 | Kelvin Cook
CWC-01 | CWC-01 | PI08100 | Verified | On ISO 10-CWC-PD-P41-0322-03 is not installed | A | P | Kelvin Cook | McD | 2019-09-30 | Kelvin Cook | Const |  |  | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08101 | Verified | On ISO 10-CWC-PD-P41-0322-04 is not installed | A | P | Kelvin Cook | McD | 2019-09-30 | Kelvin Cook | Const |  |  | 2019-11-09 | Kelvin Cook
CWC-01 | CWC-01 | PI08102 | Verified | On ISO 10-CWC-PD-P41-0325-01 missing hardware at connection to 10-CWC-T-0300/V1 | A | P | Kelvin Cook | McD | 2019-09-30 | Kelvin Cook | Const |  |  | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08103 | Verified | On ISO 10-CWC-PD-P41-0325-01 missing hardware at flange to flange connection | A | P | Kelvin Cook | McD | 2019-09-30 | Kelvin Cook | Const |  |  | 2019-11-09 | Kelvin Cook
CWC-01 | CWC-01 | PI08104 | Verified | On ISO 10-CWC-PD-P41-0325-02 verify 1" clearance from top of grating | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08105 | Verified | On ISO 10-CWC-PD-P41-0325-02 remove rope from CPVC pipe | B | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08106 | Verified | On ISO 10-CWC-PD-P41-0325-02 remove anchor bolts from ubolt | B | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08107 | Verified | On ISO 10-CWC-PD-P41-0330-01 rework the whole ISO per detail | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08108 | Verified | On ISO 10-CWC-PD-P41-0330-01 missing hardware to connection to 10-CWC-SKD-0300/TP-34 | A | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08109 | Verified | On ISO 10-CWC-PD-P41-0330-02 shorten pipe run so it is not on top of SS pipe | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08110 | Verified | On ISO 10-CWC-PD-P41-0330-02 square up pipe | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08111 | Verified | On ISO 10-CWC-PD-P41-0330-02 sloping down at the 90 el | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08112 | Verified | On ISO 10-CWC-PD-P41-0330-03 straighten up pipe in tray | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08113 | Verified | On ISO 10-CWC-PD-P41-0330-04 straighten up pipe in tray | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08114 | Verified | On ISO 10-CWC-PD-P41-0330-05 straighten up pipe in tray | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08115 | Verified | On ISO 10-CWC-PD-P41-0330-05 is not connected to the T | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08116 | Verified | On ISO 10-CWC-PD-P41-0330-05 missing hardware to connection 10-CWC-PD-P41-0413-03 | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08117 | Verified | On ISO 10-CWC-PD-P41-0330-06 Note 1 is not installed | B | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-23 | Kelvin Cook
CWC-01 | CWC-01 | PI08118 | Verified | On ISO 10-CWC-PD-P41-0330-06 pipe is not leveled | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08119 | Verified | On ISO 10-CWC-PD-P41-0330-07 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08120 | Verified | On ISO 10-CWC-PD-P41-0335-01 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08121 | Verified | On ISO 10-CWC-PD-P41-0410-01 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08122 | Verified | On ISO 10-CWC-PD-P41-0410-02 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08123 | Verified | On ISO 10-CWC-PD-P41-0410-03 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08124 | Verified | On ISO 10-CWC-PD-P41-0410-04 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08125 | Verified | On ISO 10-CWC-PD-P41-0410-05 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWC-01 | CWC-01 | PI08126 | Verified | On ISO 10-CWC-PD-P41-0510-01 missing hardware at connection to 10-CWC-SKD-0500/TP-42 | A | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
CWC-01 | CWC-01 | PI08127 | Verified | On ISO 10-CWC-PD-P41-0510-01 spool that valve 10-CWC-V-0540 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-04 | Kelvin Cook
CWC-01 | CWC-01 | PI08128 | Verified | On ISO 10-CWC-PD-P41-0510-03 strap pipe to tray every 6" | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08129 | Verified | On ISO 10-CWC-PD-P41-0510-03 shorten run so it not on top of SS pipe | A | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
CWC-01 | CWC-01 | PI08130 | Verified | On ISO 10-CWC-PD-P41-0510-03 item 3 is not connected | A | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
CWC-01 | CWC-01 | PI08131 | Verified | On ISO 10-CWC-PD-P41-0510-04 connection to 10-CWC-PD-P41-0510-03 is not completed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
CWC-01 | CWC-01 | PI08132 | Verified | On ISO 10-CWC-PD-P41-0510-05 is not installed | A | P | James Beech | McD | 2019-09-30 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-08 | Kelvin Cook
CWC-01 | CWC-01 | PI08133 | Verified | Relocate LIT-0100 to L2 | A | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-03 | Kelvin Cook
CWC-01 | CWC-01 | PI08134 | Verified | 10-CWC-FXH-0200 is not installed | B | P | William Mitchell | McD | 2019-09-30 | William Mitchell | Const | 2019-12-07 | Michael Law | 2019-12-15 | Kelvin Cook
CWC-01 | CWC-01 | PI08135 | Verified | 10-CWC-T-0200 Circ water dispersant/inhibitor storage tote is not installed | B | P | William Mitchell | McD | 2019-09-30 | William Mitchell | Const |  |  | 2019-12-07 | Michael Law
CWC-01 | CWC-01 | PI08136 | Verified | 10-CWC-FXH-0310 is not installed | B | P | William Mitchell | McD | 2019-09-30 | William Mitchell | Const | 2019-12-07 | Michael Law | 2019-12-15 | Kelvin Cook
CWC-01 | CWC-01 | PI08137 | Verified | 10-CWC-T-0400 cir water non Oxidizing Biocide storage tank is not installed | B | P | William Mitchell | McD | 2019-09-30 | William Mitchell | Const |  |  | 2019-12-07 | Michael Law
CWC-01 | CWC-01 | PI08138 | Verified | 10-CWC-T-0500 cir water sodium bisulfite storage tote is not installed | B | P | William Mitchell | McD | 2019-09-30 | William Mitchell | Const |  |  | 2019-12-07 | Michael Law
CWC-01 | CWC-01 | PI08459 | Verified | On ISO 10-CWC-PD-P41-0150-01 materials required. | A | P | Kelvin Cook | McD | 2019-10-02 | Kelvin Cook | Const |  |  | 2019-11-09 | Kelvin Cook
CWC-01 | CWC-01 | PI08460 | Verified | On ISO 10-CWC-PD-P41-0150-02 materials required. | A | P | Kelvin Cook | McD | 2019-10-02 | Kelvin Cook | Const |  |  | 2019-11-09 | Kelvin Cook
CWC-01 | CWC-01 | PI08884 | Verified | 10-CWC-T-0300 - The fittings for the offload line connectionfor both bulk sodium hypochlorite storage tanks need the Aluminum fittings replaced with material that will not corrode when exposed to sodium hypochlorite. CPVC or HDPE. | B | P | Shannon Scott | McD | 2019-10-04 | Shannon Scott | Const | 2020-01-14 | Shannon Scott | 2020-01-14 | Shannon Scott
CWC-01 | CWC-01 | PI12858 | Verified | Provide static head test for Tank 300. | B | M | William Mitchell | McD | 2019-11-09 | William Mitchell | Const |  |  | 2020-01-10 | William Mitchell
CWC-01 | CWC-01 | PI12864 | Verified | 10-CWC-PD-P41-0130-01: 1C-DRV-0100 is not installed | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-11-15 | James Beech | 2019-11-15 | Kelvin Cook
CWC-01 | CWC-01 | PI12865 | Verified | Cut holes in grating to prevent splash back during operations at 10-CWC-T-0100 | B | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-14 | Kelvin Cook
CWC-01 | CWC-01 | PI12888 | Verified | 10-CWC-SKD-0500: replace all broken components on this skid. | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-11-15 | James Beech | 2019-11-15 | Kelvin Cook
CWC-01 | CWC-01 | PI15172 | Verified | Conduit for 10-CWC-CP-0400 is trapezed to cable tray - not per V2 spec. | B | E | Chris Colvin | McD | 2020-01-05 | Chris Colvin | Const |  |  | 2020-02-07 | Fred Michael
CWC-01 | CWC-01 | PI15565 | Verified | 10-CWC-V-0100/10-CWC-V-0200 - Valves at CWC Sulfuric Acid Tank are not labeled with equipment numbers. | C | P | Tim Green | McD | 2020-01-08 | Tim Green | Comm |  |  | 2020-10-06 | Dave Goldak
CWC-01 | CWC-01 | PI15893 | Verified | 10-CWC-T-0300 - Missing vent on top of tank. | B | P | James Beech | McD | 2020-01-13 | James Beech | Comm | 2020-03-10 | William Mitchell | 2020-04-06 | Bernard Stasse
CWC-01 | CWC-01 | PI17155 | Verified | Complete insulation as required | C | Q | Sheri Fritz | PCI | 2020-02-22 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
CWC-01 | CWC-01 | PI17469 | Verified | Platform safety gate needs cold gal at Sodium Hypochlorite Injection Pump skid platform | C | X | Jerry Smith | McD | 2020-03-03 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-08-17 | Dave Goldak
CWC-01 | CWC-01 | PI17470 | Verified | Chemical tote not hooked up at Circ Water Non-Oxidizing Biocide Feed Pumps | B | P | William Mitchell | McD | 2020-03-03 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-04-16 | Keith Pollock
CWC-01 | CWC-01 | PI17471 | Verified | Resurface all bush hammered injection skid concrete pads | C | C | Alan Huntsman | McD | 2020-03-03 | Alan Huntsman | Comm | 2020-03-12 | Johnny Campbell | 2020-08-17 | Dave Goldak
CWC-01 | CWC-01 | PI17472 | Verified | Repair damaged epoxy coating at Sodium Bisulfite Skid containment | C | C | Sheri Fritz | BRA | 2020-03-03 | Sheri Fritz | Comm | 2020-04-28 | Johnny Campbell | 2020-08-17 | Dave Goldak
CWC-01 | CWC-01 | PI18009 | Verified | 10-CWC-P-0500B - There's a small drip on the discharge piping. | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-26 | James Beech | 2021-01-05 | Keith Pollock
CWC-01 | CWC-01 | PI18106 | Verified | 10-CWC-V-0310 - The suction valve (10-CWC-V-0310) of the sodium hypochlorite pumps woudn't close due to insulation around discharge piping. The orientation of the pipe needs to be changed. | C | P | Tim Green | McD | 2020-03-20 | Tim Green | Comm | 2020-06-30 | Mike Tabbert | 2021-04-21 | John Watts
CWC-01 | CWC-01 | PI18118 | Verified | Sulfuric acid connection needs to be placed on the other side of the containment. This is due to a possible leak running out and over the edge of the containment or the connection and disconnection putting the operator in an unsafe position. | C | P | Charles Worthington | McD | 2020-03-20 | Charles Worthington | Comm | 2020-04-28 | James Beech | 2021-04-21 | John Watts
CWC-01 | CWC-01 | PI18153 | Verified | Chemical injections don't work in AUTO | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2020-06-05 | Tanner Hillman
CWS-01 | CWS-01 | PI04607 | Verified | Install stilling well for 10-CWS-LIT-0101 & 0102A & 0102B at Cir water/cooling tower basin | A | I | Gonzalo Pena | McD | 2019-08-24 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
CWS-01 | CWS-01 | PI06742 | Verified | Grout all supports. | C | C | Johnny Campbell | McD | 2019-09-21 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2019-12-12 | Joshua Sturgeon
CWS-01 | CWS-01 | PI06743 | Verified | Tag all valves. | C | P | Bobby Williams | McD | 2019-09-21 | Bobby Williams | Const | 2020-02-27 | Bobby Williams | 2020-02-27 | Kelvin Cook
CWS-01 | CWS-01 | PI06744 | Verified | 10-CWS-V-0014 - valve handle missing. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06745 | Verified | 10-CWS-V-0014 - missing cap screws. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI06746 | Verified | ISO 10-CWS-PD-P41-0010-04 not installed. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06747 | Verified | ISO 10-CWS-PD-P41-0020-04 not installed. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06748 | Verified | 10-CWS-MOV-0106 - actuator not installed at CW pump A. | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-10-09 | Damon Turner | 2019-10-09 | Alex Isaac
CWS-01 | CWS-01 | PI06749 | Verified | 10-CWS-V-0108A missing handle. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06750 | Verified | 10-CWS-V-0108A missing cap screws. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06751 | Verified | 10-CWS-V-0108B missing handle. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06752 | Verified | 10-CWS-V-0108B missing cap screws. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-21 | Tim Green | 2020-01-24 | Kelvin Cook
CWS-01 | CWS-01 | PI06753 | Verified | Install 10-CWS-FE-0015. | B | P | William Mitchell | McD | 2019-09-21 | William Mitchell | Const | 2020-01-13 | Michael Law | 2020-01-21 | Michael Law
CWS-01 | CWS-01 | PI06754 | Verified | Rotate valve 10-CWS-V-0108A for operator access. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-02 | Shannon Scott
CWS-01 | CWS-01 | PI06755 | Verified | ISO 10-CWS-PD-P41-0180-01 not installed. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06756 | Verified | 10-CWS-V-0021 missing handle. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI06757 | Verified | 10-CWS-V-0021 missing cap screws. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI06758 | Verified | 10-CWS-V-0022 missing handle. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-19 | Kelvin Cook
CWS-01 | CWS-01 | PI06759 | Verified | 10-CWS-V-0022 missing cap screws. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI06760 | Verified | 10-CWS-V-0023 missing handle. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-19 | Kelvin Cook
CWS-01 | CWS-01 | PI06761 | Verified | 10-CWS-V-0023 missing cap screws. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI06762 | Verified | ISO 10-CWS-P40-0180-02, spool 2 not installed. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06763 | Verified | 10-CWS-FV-0016 not installed. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06764 | Verified | ISO 10-CWS-P40-0180-02, spool 1 - roll 180 deg. for olet on on bottom. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06765 | Verified | 10-CWS-QUIL-0180 not installed. | A | I | Gonzalo Pena | McD | 2019-09-21 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-10-03 | Kelvin Cook
CWS-01 | CWS-01 | PI06766 | Verified | 10-CWS-LIT-0102B - flange bolts missing. | A | I | Gonzalo Pena | McD | 2019-09-21 | Gonzalo Pena | Const | 2019-10-10 | Gonzalo Pena | 2019-10-10 | Kelvin Cook
CWS-01 | CWS-01 | PI06767 | Verified | 10-CWS-LIT-0102A - flange bolts missing. | A | I | Gonzalo Pena | McD | 2019-09-21 | Gonzalo Pena | Const | 2019-10-10 | Gonzalo Pena | 2019-10-10 | Kelvin Cook
CWS-01 | CWS-01 | PI06768 | Verified | 10-CWS-V-0019 handle missing. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-29 | James Beech | 2019-10-30 | Kelvin Cook
CWS-01 | CWS-01 | PI06769 | Verified | 10-CWS-V-0019 cap screws missing. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-21 | Tim Green | 2020-01-24 | Kelvin Cook
CWS-01 | CWS-01 | PI06770 | Verified | ISO 10-CWS-PD-P41-0180-04 not installed. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06771 | Verified | ISO 10-CWS-PD-P41-0180-03 - HGR 41 - loose u-bolts. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06772 | Verified | ISO 10-CWS-PD-P41-0180-03 - HGR 42 - loose u-bolts. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06773 | Verified | ISO 10-CWS-PD-P41-0180-02 - HGR 43 - not installed. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06774 | Verified | Complete bolting at U/G connection - 10-CWS-PD-P40-0180-03. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06775 | Verified | Crack in stair tread on south side CW pump platform. | C | S | Tim Gallegos | McD | 2019-09-21 | Tim Gallegos | Const | 2020-01-02 | Tim Gallegos | 2020-02-02 | Shannon Scott
CWS-01 | CWS-01 | PI06776 | Verified | 10-CWS-PI-0105 not installed. | A | I | Gonzalo Pena | McD | 2019-09-21 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-10-03 | Kelvin Cook
CWS-01 | CWS-01 | PI06777 | Verified | Ground CW pump motors. | A | E | Dustin Futrell | McD | 2019-09-21 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-24 | Shannon Scott
CWS-01 | CWS-01 | PI06778 | Verified | 10-CWS-M-0001A - vendor supplied drain piping not installed. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-16 | James Beech | 2019-11-04 | Kelvin Cook
CWS-01 | CWS-01 | PI06779 | Verified | 10-CWS-M-0001B - vendor supplied drain piping not installed. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-16 | James Beech | 2019-11-04 | Kelvin Cook
CWS-01 | CWS-01 | PI06780 | Verified | Adjust expansion joint restraining bars at CW pump A. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06781 | Verified | Adjust expansion joint restraining bars at CW pump B. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06782 | Verified | 10-CWS-ARV-0109A missing gasket. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-19 | Kelvin Cook
CWS-01 | CWS-01 | PI06783 | Verified | 10-CWS-ARV-0109B missing gasket. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-19 | Kelvin Cook
CWS-01 | CWS-01 | PI06784 | Verified | Trim cable tray on north side of CW pump/motor A to be able to pull grease tray out. | A | E | Dustin Futrell | McD | 2019-09-21 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-11-02 | Fred Michael
CWS-01 | CWS-01 | PI06785 | Verified | Perform clean & close on cooling tower basin. | A | M | Carlos Wallen | McD | 2019-09-21 | Carlos Wallen | Const | 2019-10-09 | Mike Harris | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06787 | Verified | Provide signage at cooling tower manway access ladders - top of cooling tower. | C | M | Shane Crowe | McD | 2019-09-21 | Shane Crowe | Const | 2020-04-03 | Shane Crowe | 2020-04-07 | Randy Carpenter
CWS-01 | CWS-01 | PI06788 | Verified | Clean CT fan enclosure access panels (greasy). | C | C | Alan Huntsman | McD | 2019-09-21 | Alan Huntsman | Const | 2020-01-10 | Alan Huntsman | 2020-01-14 | Alan Huntsman
CWS-01 | CWS-01 | PI06789 | Verified | Install chain operators (2) on CT discharge lines on south side. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI06790 | Verified | Tighten all discharge line pipe support hardware. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06791 | Verified | 10-CWS-0413 - connection to vendor supplied pipe at 10-CWS-V-0001K - not complete. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06792 | Verified | Remove dunnage under valve 10-CWS-MOV-0404, CT south side. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06793 | Verified | Install high point vent bird screens (10) at cooling tower. | B | P | Sheri Fritz | ICT | 2019-09-21 | Sheri Fritz | Const | 2019-12-02 | James Beech | 2019-12-14 | Kelvin Cook
CWS-01 | CWS-01 | PI06794 | Verified | 10-CWS-V-0155A missing valve handle. North side of STG bldg. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06795 | Verified | 10-CWS-V-0155A missing cap screws. North side of STG bldg. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06796 | Verified | 10-CWS-V-0155B missing valve handle. North side of STG bldg. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-21 | Charlie English | 2020-01-24 | Kelvin Cook
CWS-01 | CWS-01 | PI06797 | Verified | 10-CWS-V-0155B missing cap screws. North side of STG bldg. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06798 | Verified | 10-CWS-V-0080A missing valve handle. North side of STG bldg. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06799 | Verified | 10-CWS-V-0080 missing cap screws. North side of STG bldg. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06800 | Verified | 10-CWS-V-0080B missing valve handle. North side of STG bldg. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06801 | Verified | 10-CWS-V-0080B missing cap screws. North side of STG bldg. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06802 | Verified | 10-CWS-PD-P40-0220-03, install proper stud bolts. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06803 | Verified | 10-CWS-PD-P40-0220-03, U/G flange - replace full gasket with proper gasket. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-02-10 | Kelvin Cook
CWS-01 | CWS-01 | PI06804 | Verified | 10-CWS-PD-P41-0200-01, install proper stud bolts. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI06805 | Verified | 10-CWS-PD-P40-0220-03, U/G flange - replace full gasket with proper gasket. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-02-10 | Kelvin Cook
CWS-01 | CWS-01 | PI06806 | Verified | 10-CWS-PD-P40-0200-01, stud bolts missing at flange connection, spool 4. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI06807 | Verified | Condenser south & north side manway doors (8) missing hardware. | A | P | Bobby Williams | McD | 2019-09-21 | Bobby Williams | Const | 2019-11-04 | Bobby Williams | 2019-11-04 | Kelvin Cook
CWS-01 | CWS-01 | PI06808 | Verified | ISO 10-CWS-0222 - incomplete hardware at heat exchanger connection. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-01-22 | Kelvin Cook
CWS-01 | CWS-01 | PI06809 | Verified | 10-CWS-V-212B - locate valve stop for operator friendly, at heat exchanger. | B | P | William Mitchell | McD | 2019-09-21 | William Mitchell | Const | 2019-12-23 | Michael Law | 2020-01-17 | Kelvin Cook
CWS-01 | CWS-01 | PI06810 | Verified | 10-CWS-V-0202B - rotate valve handle for operator friendly, at heat exchanger. | B | P | William Mitchell | McD | 2019-09-21 | William Mitchell | Const | 2019-12-23 | Michael Law | 2020-01-17 | Kelvin Cook
CWS-01 | CWS-01 | PI06811 | Verified | 10-CWS-V-0225B missing cap screws, at heat exchanger. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-22 | Tim Green | 2020-01-24 | Kelvin Cook
CWS-01 | CWS-01 | PI06812 | Verified | 10-CWS-V-0222 - rotate valve handle, at heat exchanger. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-27 | Bobby Williams | 2020-01-27 | Kelvin Cook
CWS-01 | CWS-01 | PI06813 | Verified | 10-CWS-V-0225A missing cap screws, at heat exchanger. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-22 | Tim Green | 2020-01-24 | Kelvin Cook
CWS-01 | CWS-01 | PI06814 | Verified | ISO 10-CWS-0202 - inclomplete hardware at heat exchanger. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-01-25 | Kelvin Cook
CWS-01 | CWS-01 | PI06815 | Verified | 10-CWS-V-0225B - install chain operator, at heat exchanger. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-22 | Tim Green | 2020-01-24 | Kelvin Cook
CWS-01 | CWS-01 | PI06816 | Verified | 10-CWS-V-0225A - install chain operator, at heat exchanger. | B | P | Kelvin Cook | McD | 2019-09-21 | Kelvin Cook | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI06817 | Verified | ISO 10-CWS-02020 - missing hardware at heat exchanger. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-02-07 | James Beech | 2020-02-10 | Kelvin Cook
CWS-01 | CWS-01 | PI06818 | Verified | 10-CWS-V-0201A - valve handle bent, repair or replace, at heat exchanger. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-02-07 | James Beech | 2020-02-10 | Kelvin Cook
CWS-01 | CWS-01 | PI06819 | Verified | 10-CWS-V-0201A - locate stop for operator friendly. | B | P | William Mitchell | McD | 2019-09-21 | William Mitchell | Const | 2019-12-23 | Michael Law | 2020-01-17 | Kelvin Cook
CWS-01 | CWS-01 | PI06820 | Verified | 10-CWS-V-0202A - locate stop for operator friendly. | B | P | William Mitchell | McD | 2019-09-21 | William Mitchell | Const | 2019-12-23 | Michael Law | 2020-01-17 | Kelvin Cook
CWS-01 | CWS-01 | PI06821 | Verified | 10-CWS-V-0210A missing cap screws, at heat exchanger. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-22 | Tim Green | 2020-01-24 | Kelvin Cook
CWS-01 | CWS-01 | PI06822 | Verified | 10-CWS-V-0210B missing cap screws, at heat exchanger. | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-03-05 | Tim Green | 2020-03-09 | Michael Law
CWS-01 | CWS-01 | PI06823 | Verified | ISO 10-CWS-PD-40-0256-02 not installed, STG north side. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06824 | Verified | ISO 10-CWS-PD-P41-0220-04 not installed, STG north side. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06825 | Verified | ISO 10-CWS-PD-40-0256-01 not installed, STG north side. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06826 | Verified | ISO-PD-P40=PD-0255-01 not installed, STG north side. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
CWS-01 | CWS-01 | PI06827 | Verified | 10-CWS-LG-0100A not installed. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06828 | Verified | 10-CWS-LG-0100B not installed. | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06829 | Verified | Install all ARVs (STG bldg.) (24) | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI06830 | Verified | 1C-CNM-CND-0100 - Verify quantity of Level Gauges required. | A | P | Kelvin Cook | McD | 2019-09-21 | Kelvin Cook | Const | 2019-09-25 | Kelvin Cook | 2019-09-25 | Kelvin Cook
CWS-01 | CWS-01 | PI06831 | Verified | .75" connection port is not installed on 30" Fiberglass pipe feeding to 10-CWS-FN-0100K | A | P | Sheri Fritz | ICT | 2019-09-23 | Sheri Fritz | Const |  |  | 2019-10-19 | Kelvin Cook
CWS-01 | CWS-01 | PI06832 | Verified | 10-CWS-0413-01 is not installed | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06833 | Verified | 10-CWS-PD-P40-0256-02 HGR-0035 loose pipe clamp and missing a nut | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06834 | Verified | 10-CWS-PD-P40-0256-02 HGR-0033 loose ubolt | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06835 | Verified | 10-CWS-PD-P40-0256-02 HGR-0031 loose ubolt | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06836 | Verified | 10-CWS-PD-P40-0256-01 HGR-0028 loose ubolt | B | P | James Beech | McD | 2019-09-23 | James Beech | Const |  |  | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06837 | Verified | 10-CWS-PD-P40-0250-01 HGR-0038 support is incomplete | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06838 | Verified | 10-CWS-PD-P40-0250-01 HGR-0019 missing a u bolt | B | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2020-01-08 | Bobby Williams | 2020-01-09 | Kelvin Cook
CWS-01 | CWS-01 | PI06839 | Verified | 10-CWS-PD-P40-0250-01 HGR-0020 loose u bolt | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI06840 | Verified | 10-CWS-PD-P40-0250-02 HGR-0022 support is incomplete | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI08206 | Verified | Ground cable raceway at the circ. water motors. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-11-02 | Fred Michael
CWS-01 | CWS-01 | PI08207 | Verified | Ground conduit nipple at CW motors termination enclosure. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-11-02 | Fred Michael
CWS-01 | CWS-01 | PI08208 | Verified | Ground duct bank stub ups. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-11-02 | Fred Michael
CWS-01 | CWS-01 | PI08209 | Verified | Replace plastic plugs & valves at 10-CWS-PI-0105A & B. | A | I | Gonzalo Pena | McD | 2019-10-01 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-09 | Albert Burge
CWS-01 | CWS-01 | PI08210 | Verified | Missing condulet covers at the CW pumps. | B | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-15 | Fred Michael | 2019-11-02 | Fred Michael
CWS-01 | CWS-01 | PI08211 | Verified | Ground the grounding bushings - between the CW pumps. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-22 | Mike Tabbert
CWS-01 | CWS-01 | PI08212 | Verified | Conduit between CW pumps missing low point drains. | B | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-24 | Brad Stanford | 2019-11-02 | Fred Michael
CWS-01 | CWS-01 | PI08213 | Verified | Circulating water motors A & B - covers missing hardware. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-15 | Fred Michael | 2019-10-15 | Fred Michael
CWS-01 | CWS-01 | PI08214 | Verified | 10-CWS-PI-0105B is showing pressure. | B | I | Albert Burge | McD | 2019-10-01 | Albert Burge | Const |  |  | 2019-12-18 | Blake Boudreaux
CWS-01 | CWS-01 | PI08215 | Verified | Protect medium voltage cable from CT screws in the cooling tower PDC. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-11-02 | Brad Stanford | 2019-11-02 | Fred Michael
CWS-01 | CWS-01 | PI08216 | Verified | Tag all instruments. | C | I | Gonzalo Pena | McD | 2019-10-01 | Gonzalo Pena | Const | 2019-12-14 | James Tanner | 2019-12-19 | Albert Burge
CWS-01 | CWS-01 | PI08217 | Verified | Heat shrink the instrument tube bundles. | B | I | Gonzalo Pena | McD | 2019-10-01 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2019-11-21 | Randy Carpenter
CWS-01 | CWS-01 | PI08218 | Verified | Ground flex at instrumentation. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-11-02 | Shannon Scott
CWS-01 | CWS-01 | PI08219 | Verified | Complete IA tubing at 10-CWS-FV-0016. | A | I | Gonzalo Pena | McD | 2019-10-01 | Gonzalo Pena | Const | 2019-10-10 | Gonzalo Pena | 2019-11-04 | Albert Burge
CWS-01 | CWS-01 | PI08220 | Verified | Trim ty-wraps in cable trays. | B | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const | 2019-11-11 | Brad Stanford | 2019-12-13 | Mike Tabbert
CWS-01 | CWS-01 | PI08221 | Verified | Install 10-CWS-AE-0017 & 0018. | A | I | James Beech | McD | 2019-10-01 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI08222 | Verified | Ground seal tite on 10-CWS-LI101, 102A & 102B, and 10-CWS-TI-0019. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Brad Stanford | 2019-11-02 | Fred Michael
CWS-01 | CWS-01 | PI08223 | Verified | Cable tray on the north side of CW pump A needs rework. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-22 | Mike Tabbert
CWS-01 | CWS-01 | PI08224 | Verified | Ground cable tray from CT PDC to cooling tower. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Brad Stanford | 2019-10-23 | Mike Tabbert
CWS-01 | CWS-01 | PI08225 | Verified | Vertical riser on cooling tower cable tray needs support. | B | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const | 2019-11-11 | Brad Stanford | 2019-12-13 | Mike Tabbert
CWS-01 | CWS-01 | PI08227 | Verified | Need supports at 2 top trays below the 90's between the CT PDC & the cooling tower. | B | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-31 | Brad Stanford | 2019-11-04 | Fred Michael
CWS-01 | CWS-01 | PI08228 | Verified | Cable tray hold down clamps missing at ground level and top of cooling tower. | B | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const | 2019-11-13 | Brad Stanford | 2019-12-13 | Mike Tabbert
CWS-01 | CWS-01 | PI08229 | Verified | Ground flex on 10-CWS-M-001B and 001J. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Brad Stanford | 2019-11-02 | Fred Michael
CWS-01 | CWS-01 | PI08230 | Verified | Ground motors 10-CWS-M-001E and 001F. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-11-02 | Fred Michael
CWS-01 | CWS-01 | PI08231 | Verified | Label all control boxes at CT fan motors. | C | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const | 2020-03-31 | Matt Gilmore | 2020-04-28 | Michael Law
CWS-01 | CWS-01 | PI08233 | Verified | Jump conduit grounding bushings to cable tray ground - top of cooling tower. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Brad Stanford | 2019-10-22 | Mike Tabbert
CWS-01 | CWS-01 | PI08234 | Verified | Gasket not installed on 10-CWS-M-0100J termination box. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-11-02 | Fred Michael | 2019-11-02 | Fred Michael
CWS-01 | CWS-01 | PI08235 | Verified | Gasket not installed on 10-CWS-M-0100D termination box. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-11-02 | Fred Michael | 2019-11-02 | Fred Michael
CWS-01 | CWS-01 | PI08236 | Verified | Gasket not installed on 10-CWS-M-0100F termination box. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-11-02 | Fred Michael | 2019-11-02 | Fred Michael
CWS-01 | CWS-01 | PI08237 | Verified | All cables at fan motors to cable tray - need triplex configuration, ty-wrap and organized in an orderly manner. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
CWS-01 | CWS-01 | PI08238 | Verified | Check for support under top floor of cooling tower on north side of all access hatches. | C | M | Josh Koerner | ICT | 2019-10-01 | Josh Koerner | Const | 2020-06-18 | Jason Ezell | 2020-06-18 | John Watts
CWS-01 | CWS-01 | PI08239 | Verified | Replace latch on bucket for 10-CWS-M-0100J in the cooling tower PDC. | B | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const | 2020-01-28 | Jared Stimpson | 2020-01-28 | Mike Tabbert
CWS-01 | CWS-01 | PI08240 | Verified | Clean all 10 CT fan motor buckets in the cooling tower PDC. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Brad Stanford | 2019-10-23 | Mike Tabbert
CWS-01 | CWS-01 | PI08241 | Verified | Seal conduits in the cooling tower PDC. | B | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-31 | Randy Carpenter
CWS-01 | CWS-01 | PI08303 | Verified | 10CWSX0008, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08304 | Verified | 10CWSX0011, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08305 | Verified | 10CWSX0014, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08306 | Verified | 10CWSX0017, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08307 | Verified | 10CWSX0020, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08308 | Verified | 10CWSX0023, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08309 | Verified | 10CWSX0026, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08310 | Verified | 10CWSX0029, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08311 | Verified | 10CWSX0032, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08312 | Verified | 10CWSX0035, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08313 | Verified | 10CWSX0054, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08314 | Verified | 10CWSX0061, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-02 | Mike Tabbert
CWS-01 | CWS-01 | PI08315 | Verified | 10CWSX0062, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-02 | Mike Tabbert
CWS-01 | CWS-01 | PI08316 | Verified | 10CWSX0063, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-02 | Mike Tabbert
CWS-01 | CWS-01 | PI08341 | Verified | 10CWSX0007, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08342 | Verified | 10CWSX0008, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08343 | Verified | 10CWSX0009, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08344 | Verified | 10CWSX0010, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08345 | Verified | 10CWSX0011, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08346 | Verified | 10CWSX0013, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08347 | Verified | 10CWSX0014, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08348 | Verified | 10CWSX0015, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08349 | Verified | 10CWSX0016, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08350 | Verified | 10CWSX0017, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08351 | Verified | 10CWSX0018, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CWS-01 | CWS-01 | PI08352 | Verified | 10CWSX0019, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08353 | Verified | 10CWSX0020, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08354 | Verified | 10CWSX0021, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08355 | Verified | 10CWSX0022, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08356 | Verified | 10CWSX0023, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
CWS-01 | CWS-01 | PI08357 | Verified | 10CWSX0024, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08358 | Verified | 10CWSX0025, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08359 | Verified | 10CWSX0026, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08360 | Verified | 10CWSX0027, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08361 | Verified | 10CWSX0028, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08362 | Verified | 10CWSX0029, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08363 | Verified | 10CWSX0030, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08364 | Verified | 10CWSX0031, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08365 | Verified | 10CWSX0032, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08366 | Verified | 10CWSX0033, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08367 | Verified | 10CWSX0034, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08368 | Verified | 10CWSX0035, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08369 | Verified | 10CWSX0036, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08370 | Verified | 10CWSX0038, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CWS-01 | CWS-01 | PI08371 | Verified | 10CWSX0043, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08372 | Verified | 10CWSX0044, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08373 | Verified | 10CWSX0045, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08340 | Verified | 10CWSX0006, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08339 | Verified | 10CWSX0005, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
CWS-01 | CWS-01 | PI08338 | Verified | 10CWSX0002, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08337 | Verified | 10CWSX0001, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08336 | Verified | 10CWSL0006C2, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08335 | Verified | 10CWSK0033, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08334 | Verified | 10CWSK0032, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08333 | Verified | 10CWSK0028, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08332 | Verified | 10CWSK0027, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08331 | Verified | 10CWSK0026, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-02 | Mike Tabbert
CWS-01 | CWS-01 | PI08330 | Verified | 10CWSK0005, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08329 | Verified | 10CWSK0004, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-02 | Mike Tabbert
CWS-01 | CWS-01 | PI08328 | Verified | 10CWSK0003, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08327 | Verified | 10CWSK0002, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08326 | Verified | 10CWSK0001, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08325 | Verified | 10CWSC0026, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08324 | Verified | 10CWSC0025, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08323 | Verified | 10CWSC0024, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08322 | Verified | 10CWSC0002, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08321 | Verified | 10CWSC0001, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08320 | Verified | 10CWSX0067, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08319 | Verified | 10CWSX0066, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-02 | Mike Tabbert
CWS-01 | CWS-01 | PI08318 | Verified | 10CWSX0065, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08317 | Verified | 10CWSX0064, Pull cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-02 | Mike Tabbert
CWS-01 | CWS-01 | PI08374 | Verified | 10CWSX0046, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08375 | Verified | 10CWSX0047, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08376 | Verified | 10CWSX0048, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08377 | Verified | 10CWSX0050, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08378 | Verified | 10CWSX0051, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08379 | Verified | 10CWSX0054, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08380 | Verified | 10CWSX0055, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08381 | Verified | 10CWSX0056, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CWS-01 | CWS-01 | PI08382 | Verified | 10CWSX0057, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08383 | Verified | 10CWSX0061, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CWS-01 | CWS-01 | PI08384 | Verified | 10CWSX0062, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CWS-01 | CWS-01 | PI08385 | Verified | 10CWSX0063, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CWS-01 | CWS-01 | PI08386 | Verified | 10CWSX0064, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
CWS-01 | CWS-01 | PI08387 | Verified | 10CWSX0065, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08388 | Verified | 10CWSX0066, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
CWS-01 | CWS-01 | PI08389 | Verified | 10CWSX0067, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08390 | Verified | 10CWSC0001, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08391 | Verified | 10CWSC0002, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08392 | Verified | 10CWSC0003, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08393 | Verified | 10CWSC0010, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
CWS-01 | CWS-01 | PI08394 | Verified | 10CWSC0017, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08395 | Verified | 10CWSC0018, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08396 | Verified | 10CWSC0019, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08397 | Verified | 10CWSC0020, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-21 | Mike Tabbert
CWS-01 | CWS-01 | PI08398 | Verified | 10CWSC0021, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08399 | Verified | 10CWSC0022, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08400 | Verified | 10CWSC0023, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08401 | Verified | 10CWSC0024, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08402 | Verified | 10CWSC0025, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08403 | Verified | 10CWSC0026, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08404 | Verified | 10CWSK0001, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08405 | Verified | 10CWSK0002, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08406 | Verified | 10CWSK0003, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08407 | Verified | 10CWSK0009, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08408 | Verified | 10CWSK0011, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08409 | Verified | 10CWSK0021, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08410 | Verified | 10CWSK0027, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08411 | Verified | 10CWSK0032, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08412 | Verified | 10CWSK0033, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08413 | Verified | 10CWSL0006C1, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08414 | Verified | 10CWSX0002, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08415 | Verified | 10CWSX0008, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08416 | Verified | 10CWSX0011, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08417 | Verified | 10CWSX0014, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08418 | Verified | 10CWSX0017, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08419 | Verified | 10CWSX0020, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08420 | Verified | 10CWSX0021, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08421 | Verified | 10CWSX0022, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
CWS-01 | CWS-01 | PI08422 | Verified | 10CWSX0023, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08423 | Verified | 10CWSX0026, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08424 | Verified | 10CWSX0029, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08425 | Verified | 10CWSX0032, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08426 | Verified | 10CWSX0035, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08427 | Verified | 10CWSX0043, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08428 | Verified | 10CWSX0044, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-01 | Michael Law
CWS-01 | CWS-01 | PI08429 | Verified | 10CWSX0045, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08430 | Verified | 10CWSX0046, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-01 | Michael Law
CWS-01 | CWS-01 | PI08431 | Verified | 10CWSX0047, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CWS-01 | CWS-01 | PI08432 | Verified | 10CWSX0048, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CWS-01 | CWS-01 | PI08433 | Verified | 10CWSX0049, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
CWS-01 | CWS-01 | PI08434 | Verified | 10CWSX0050, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-01 | Michael Law
CWS-01 | CWS-01 | PI08435 | Verified | 10CWSX0051, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-01 | Michael Law
CWS-01 | CWS-01 | PI08436 | Verified | 10CWSX0054, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08437 | Verified | 10CWSX0055, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08438 | Verified | 10CWSX0056, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08439 | Verified | 10CWSX0057, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-19 | Mike Tabbert
CWS-01 | CWS-01 | PI08440 | Verified | 10CWSX0061, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08441 | Verified | 10CWSX0062, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-25 | Mike Tabbert
CWS-01 | CWS-01 | PI08442 | Verified | 10CWSX0063, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
CWS-01 | CWS-01 | PI08443 | Verified | 10CWSX0064, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
CWS-01 | CWS-01 | PI08444 | Verified | 10CWSX0065, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI08445 | Verified | 10CWSX0066, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
CWS-01 | CWS-01 | PI08446 | Verified | 10CWSX0067, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-14 | Michael Law
CWS-01 | CWS-01 | PI09790 | Verified | Test Package CWS-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI10248 | Verified | 5 of the 10 gangways are in the wrong location preventing the gangways being permanently fastened down. The parabellum cone was erected incorrectly. The access should be at the motor side not on the opposing side. The attaching hardware is not there. | B | S | Sheri Fritz | ICT | 2019-10-23 | Sheri Fritz | Const | 2020-02-05 | Sheri Fritz | 2020-02-07 | Tom Noble
CWS-01 | CWS-01 | PI12482 | Verified | On ISO 10-CWS-PD-P40-0010-02 missing gasket on flange connection to 10-CWS-ARV-0109A. | A | P | James Beech | McD | 2019-10-28 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI12483 | Verified | On ISO 10-CWS-PD-P40-0020-02 missing gasket on flange connection to 10-CWS-ARV-0109B. | A | P | James Beech | McD | 2019-10-28 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI12484 | Verified | Bolts not installed on flange for 10-CWS-LIT-0102A & LIT-0102B at Cooling Tower Basin Intake. | A | P | James Beech | McD | 2019-10-28 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI12485 | Verified | Uneven bolts on flange connection for 10-CWS-LIT-0101 at Cooling Tower Basin Intake. | A | P | James Beech | McD | 2019-10-28 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI12486 | Verified | At the Cooling Tower Basin instake, drain piping coming off 10-CWS-P-0001A & 10-CWS-P-0001B is not installed. | A | P | James Beech | McD | 2019-10-28 | James Beech | Const |  |  | 2019-11-01 | Kelvin Cook
CWS-01 | CWS-01 | PI12487 | Verified | On ISO 10-CWS-PD-P41-0133-01 install birdscreen. | B | P | James Beech | McD | 2019-10-28 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI12488 | Verified | On ISO 10-CWS-PD-P41-0126-01 install birdscreen. | B | P | James Beech | McD | 2019-10-28 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI12489 | Verified | On ISO 10-CWS-PD-P41-0124-01 install birdscreen. | B | P | James Beech | McD | 2019-10-28 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI12490 | Verified | On ISO 10-CWS-PD-P41-0131-01 install birdscreen. | B | P | James Beech | McD | 2019-10-28 | James Beech | Const |  |  | 2019-11-02 | Kelvin Cook
CWS-01 | CWS-01 | PI12491 | Verified | On ISO 10-CWS-PD-P40-0202-01 valve 10-CWS-V-0210B is missing valve handle. | B | P | James Beech | McD | 2019-10-28 | James Beech | Const |  |  | 2020-01-20 | Kelvin Cook
CWS-01 | CWS-01 | PI12609 | Verified | Repair leaks in tower basin after fill. | B | C | Johnny Campbell | McD | 2019-10-29 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2020-01-27 | Michael Law
CWS-01 | CWS-01 | PI12611 | Verified | Paint on fan needs repaired, coming off (E cell). | B | X | Sheri Fritz | ICT | 2019-10-29 | Sheri Fritz | Const | 2020-02-27 | Michael Law | 2020-03-03 | Michael Law
CWS-01 | CWS-01 | PI12612 | Verified | C cell vibration readings were well above the other 4 cells test run (1.5 - others from .2 to .5). | B | M | Sheri Fritz | ICT | 2019-10-29 | Sheri Fritz | Const | 2020-03-09 | Sheri Fritz | 2020-03-09 | Michael Law
CWS-01 | CWS-01 | PI12613 | Verified | Uncoupled for motor run, pump missing guard. | B | M | Shane Crowe | McD | 2019-10-29 | Shane Crowe | Const | 2020-01-13 | Michael Law | 2020-01-21 | Michael Law
CWS-01 | CWS-01 | PI12614 | Verified | Main condenser water box - perform clean & close. | A | M | Shane Crowe | McD | 2019-10-29 | Shane Crowe | Const | 2019-11-04 | Michael Law | 2019-11-04 | John Schanno
CWS-01 | CWS-01 | PI12616 | Verified | Complete automatic vents - missing air release vents. | A | P | James Beech | McD | 2019-10-29 | James Beech | Const | 2019-11-01 | James Beech | 2020-01-21 | Michael Law
CWS-01 | CWS-01 | PI12706 | Verified | Re-install 10-CWS-PDI-0200A & B after comm. re-installs pipe spool. (in enclosure). | B | I | Albert Burge | McD | 2019-11-02 | Albert Burge | Const | 2020-01-16 | Albert Burge | 2020-01-22 | Albert Burge
CWS-01 | CWS-01 | PI12712 | Verified | Replace 10-CWS-TE-0152B2. | B | I | Gonzalo Pena | McD | 2019-11-04 | Gonzalo Pena | Const | 2019-12-02 | James Tanner | 2019-12-03 | James Tanner
CWS-01 | CWS-01 | PI12866 | Verified | Modify the ladder on the north side of the pump containment so there is at least 7" clearence from rungs to the pipe and conduit. Install a plate across the top of last rung to top of concrete to prevent someone from slipping through the enlarged opening. | B | S | Bobby Williams | McD | 2019-11-11 | Bobby Williams | Const | 2020-01-09 | Tim Gallegos | 2020-01-25 | Kelvin Cook
CWS-01 | CWS-01 | PI14362 | Verified | Inspect and repair cracks in Cooling Tower Pump Bay. | C | C | Michael Law | McD | 2019-12-05 | Michael Law | Const |  |  | 2019-12-07 | Michael Law
CWS-01 | CWS-01 | PI14367 | Verified | Inspect and repair cracks in cooling tower pump bay | C | C | Michael Law | McD | 2019-12-05 | Michael Law | Const |  |  | 2020-01-13 | Michael Law
CWS-01 | CWS-01 | PI14732 | Verified | 1C-CNM-PD-P40-0241-01: 1C-CNM-HGR-0046 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-13 | Bobby Williams | 2019-12-15 | Kelvin Cook
CWS-01 | CWS-01 | PI15579 | Verified | Repair crack on cooling tower pump bay | B | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Comm | 2020-02-07 | Michael Law | 2020-02-18 | Michael Law
CWS-01 | CWS-01 | PI15894 | Verified | 10-CWS-V-0007 - valve is not accessible and water splashes up from concrete, need to reroute drain line & valve to ground level | D | P | Michael Law | McD | 2020-01-13 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
CWS-01 | CWS-01 | PI15895 | Cleared | 10-FWS-FE-0015 - Orifice is improperly sized and has the cooling tower blowdown gpm limited to 0 gpm - 1046 gpm before the transmitter becomes oversaturated. The orifice needs to be sized for 10-CWS-FV-0016 max flow of 1500 gpm, however, the orifice is sized for the valve's normal flow of 1046 gpm. When the orifice is resized/changed, the DCS and transmitter configuration will need to be edited. | C | P | Charles Worthington | McD | 2020-01-13 | Charles Worthington | Comm | 2020-05-11 | Michael Law
CWS-01 | CWS-01 | PI15896 | Verified | 10-CWS-V-0220A, 10-CWS-V-0220B, 10-CWS-SRV-0224A, 10-CWS-SRV-0224B - Cannot access valves | D | P | Kevin Leppert | McD | 2020-01-13 | Kevin Leppert | Comm |  |  | 2020-02-19 | Keith Pollock
CWS-01 | CWS-01 | PI16672 | Verified | 10-CWS-MOV-0402 - This MOV is not working properly in remote or local. Operators must close with MOV handwheel. | B | E | Jonathan Donham | McD | 2020-02-07 | Jonathan Donham | Comm | 2020-03-09 | Jonathan Donham | 2020-04-06 | Bernard Stasse
CWS-01 | CWS-01 | PI17149 | Verified | Cooling Tower Fan A keeps tripping on vibration | A | I | Sheri Fritz | ICT | 2020-02-22 | Sheri Fritz | Comm | 2020-03-09 | Michael Law | 2020-03-31 | Bernard Stasse
CWS-01 | CWS-01 | PI17150 | Verified | Cooling Tower Fan F keeps tripping on vibration | A | I | Sheri Fritz | ICT | 2020-02-22 | Sheri Fritz | Comm | 2020-03-09 | Michael Law | 2020-03-31 | Bernard Stasse
CWS-01 | CWS-01 | PI17151 | Verified | Coating falling off of all Cooling Tower Fan blades | C | C | Josh Koerner | ICT | 2020-02-22 | Josh Koerner | Comm | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CWS-01 | CWS-01 | PI17152 | Verified | Sparging line PVC Vent at East end of Cooling Tower Basin needs to be replaced with metal, PVC Vent does not hold during operation | D | P | Sheri Fritz | ICT | 2020-02-22 | Sheri Fritz | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
CWS-01 | CWS-01 | PI17359 | Verified | CWT Fan Cell G, there is excessive water coming from spray nozzle area. Check if nozzle is broken and repair as necessary. | B | M | William Mitchell | McD | 2020-02-28 | William Mitchell | Comm | 2020-03-09 | Michael Law | 2020-04-15 | Keith Pollock
CWS-01 | CWS-01 | PI17668 | Verified | The 2 inch PVC coming off the circ water bypass is broken on both bypasses. Pipe is inside the basin. Basin will have to be drained to resolve this issue. | B | P | Sheri Fritz | ICT | 2020-03-04 | Sheri Fritz | Comm | 2020-03-19 | Sheri Fritz | 2020-06-08 | John Watts
CWS-01 | CWS-01 | PI17691 | Verified | On suction vent valves, the vent valve hood screen is stuffed with packing material/debris, and one is falling apart. | B | M | William Mitchell | McD | 2020-03-04 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2021-07-06 | John Watts
CWS-01 | CWS-01 | PI17846 | Verified | There's a hose draped over the cement wall that broke part of the metal wall. Location: Plant southwest side of the cooling tower | C | M | William Mitchell | McD | 2020-03-16 | William Mitchell | Const | 2020-04-20 | William Mitchell | 2021-01-15 | Dave Goldak
CWS-01 | CWS-01 | PI18020 | Verified | 10-CCW-HEX-0200A and 10-CCW-HEX-0200B - Inspect the plate and frame heat exhangers A&B and clean, if required. Inspect the equipment on the circulating water system for iron after the Jan 21, 2020 upset to the system. Clean equipment for full efficiency. | D | P | Michael Law | McD | 2020-03-17 | Michael Law | Comm | 2020-05-07 | Michael Law | 2021-04-21 | John Watts
CWS-01 | CWS-01 | PI18021 | Verified | 10-CWS-CLT-0001 - Cooling Tower fill inspection. Weigh a coupon to ensure fill did not get plugged up during commissioning. Inspect the equipment on the circulating water system for iron after the Jan 21, 2020 upset to the system. Clean equipment for efficiency. | D | M | Alan Joiner | McD | 2020-03-17 | Alan Joiner | Comm | 2020-07-24 | Tim Gallegos | 2021-04-21 | John Watts
CWS-01 | CWS-01 | PI18027 | Verified | The hand valves on the gearboxes need to be changed to yellow so we can visually verify the valve is open and know that we are getting an accurate oil level reading on the cooling tower fan motors. | D | M | Josh Koerner | ICT | 2020-03-17 | Josh Koerner | Comm | 2020-07-20 | Jason Ezell | 2020-07-20 | Jason Ezell
CWS-01 | CWS-01 | PI18032 | Verified | 10-CWS-AI-0020 Circ Water pH does not work and reads bad quality - 3/27 ETA 01-Apr | C | E | Albert Burge | McD | 2020-03-18 | Albert Burge | Comm | 2020-04-14 | Albert Burge | 2020-05-05 | Keith Pollock
CWS-01 | CWS-01 | PI18033 | Verified | 10-CWS-AI-0021 Circ Water ORP does not work and reads bad quality - 3/27 ETA 01-Apr | C | E | Albert Burge | McD | 2020-03-18 | Albert Burge | Comm | 2020-04-14 | Albert Burge | 2020-05-05 | Keith Pollock
CWS-01 | CWS-01 | PI18034 | Verified | 10-CWS-AI-0018 Cooling Tower Blowdown pH does not read correctly | B | E | Albert Burge | McD | 2020-03-18 | Albert Burge | Comm | 2020-03-19 | Albert Burge | 2020-03-26 | Keith Pollock
CWS-01 | CWS-01 | PI18035 | Verified | 10-CWS-FN-0100A Cooling Tower Fan 1A vibration keeps coming in and out of alarm. Approx 1,500 times per day | B | E | William Mitchell | McD | 2020-03-18 | William Mitchell | Comm | 2020-03-26 | William Mitchell | 2020-07-28 | Keith Pollock
CWS-01 | CWS-01 | PI18036 | Verified | 10-CWS-FN-0100B Cooling Tower Fan 1B will not run and trips on high vibration - 3/27 4-6 weeks delivery of gearbox (under warranty) | C | E | Alan Joiner | McD | 2020-03-18 | Alan Joiner | Comm | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
CWS-01 | CWS-01 | PI18037 | Verified | 10-CWS-FN-0100C Cooling Tower Fan 1C will not run and trips on high vibration - 3/27 gearbox change in progress | C | E | William Mitchell | McD | 2020-03-18 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2020-07-28 | Keith Pollock
CWS-01 | CWS-01 | PI18038 | Verified | 10-CWS-FN-0100E Cooling Tower Fan 1E vibration keeps coming in and out of alarm. Approx 260 times per day. | B | E | William Mitchell | McD | 2020-03-18 | William Mitchell | Comm | 2020-03-26 | William Mitchell | 2020-07-28 | Keith Pollock
CWS-01 | CWS-01 | PI18039 | Verified | 10-CWS-FN-0100H Cooling Tower Fan 1E vibration keeps coming in and out of alarm. Approx 260 times per day. | B | E | William Mitchell | McD | 2020-03-18 | William Mitchell | Comm | 2020-03-26 | William Mitchell | 2021-04-21 | John Watts
CWS-01 | CWS-01 | PI18117 | Verified | All probe locations on the CWS need to be relocated to the lower horizontal section of piping. The probes require monthly calibrations. | D | I | Charles Worthington | McD | 2020-03-20 | Charles Worthington | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
CWS-01 | CWS-01 | PI18136 | Verified | Cooling Tower pH and ORP does not work. | C | M | Albert Burge | McD | 2020-03-20 | Albert Burge | Comm | 2020-05-04 | Albert Burge | 2020-05-05 | Keith Pollock
CWS-01 | CWS-01 | PI18137 | Verified | Cooling tower blowdown CHLORINE PPM does not work. This is an environmental concern. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-14 | William Mitchell | 2020-04-14 | John Watts
CWS-01 | CWS-01 | PI18138 | Verified | 10-CWS-AE-0018 - Cooling tower blowdown pH does not work. This is an environmental concern. | C | I | Albert Burge | McD | 2020-03-20 | Albert Burge | Comm | 2020-04-14 | Albert Burge | 2020-05-05 | Keith Pollock
DCS-01 | DCS-01 | PI00356 | Verified | Pull & terminate 10DCSX0001. | A | E | Sheri Fritz | ITS | 2019-04-01 | Sheri Fritz | Const | 2019-04-08 | Mike Tabbert | 2019-04-08 | Mike Tabbert
DCS-01 | DCS-01 | PI00370 | Verified | Confirm grounding is complete at Network Cabinets, 1001, 1002, 1000. | A | E | Shannon Savoy | McD | 2019-04-01 | Shannon Savoy | Const | 2019-04-08 | Shannon Savoy | 2019-04-09 | Mike Tabbert
DCS-01 | DCS-01 | PI00371 | Verified | 10DCSK0027, Terminate one end of cable. | A | E | Shannon Savoy | McD | 2019-04-01 | Shannon Savoy | Const | 2019-04-09 | Shannon Savoy | 2019-04-09 | Mike Tabbert
DCS-01 | DCS-01 | PI00372 | Verified | 10DCSX0082, Terminate Fiber | A | E | Sheri Fritz | ITS | 2019-04-01 | Sheri Fritz | Const | 2019-04-10 | Mike Tabbert | 2019-04-10 | Mike Tabbert
DCS-01 | DCS-01 | PI00373 | Verified | 10DCSX0083, Terminate Fiber | A | E | Sheri Fritz | ITS | 2019-04-01 | Sheri Fritz | Const | 2019-04-10 | Mike Tabbert | 2019-04-10 | Mike Tabbert
DCS-01 | DCS-01 | PI00374 | Verified | 10DCSX0084, Terminate Fiber | A | E | Sheri Fritz | ITS | 2019-04-01 | Sheri Fritz | Const | 2019-04-10 | Mike Tabbert | 2019-04-10 | Mike Tabbert
DCS-01 | DCS-01 | PI00375 | Verified | 10DCSX0085, Terminate Fiber | A | E | Sheri Fritz | ITS | 2019-04-01 | Sheri Fritz | Const | 2019-04-10 | Mike Tabbert | 2019-04-10 | Mike Tabbert
DCS-01 | DCS-01 | PI00376 | Verified | 10DCSX0196, Terminate Fiber | A | E | Sheri Fritz | ITS | 2019-04-01 | Sheri Fritz | Const | 2019-04-03 | Mike Tabbert | 2019-04-03 | Mike Tabbert
DCS-01 | DCS-01 | PI00377 | Verified | 10DCSX0197, Terminate Fiber | A | E | Sheri Fritz | ITS | 2019-04-01 | Sheri Fritz | Const | 2019-04-03 | Mike Tabbert | 2019-04-03 | Mike Tabbert
DCS-01 | DCS-01 | PI00378 | Verified | 10DCSX0198, Terminate Fiber | A | E | Sheri Fritz | ITS | 2019-04-01 | Sheri Fritz | Const | 2019-04-03 | Mike Tabbert | 2019-04-03 | Mike Tabbert
DCS-01 | DCS-01 | PI00379 | Verified | 10DCSX0199, Terminate Fiber | A | E | Sheri Fritz | ITS | 2019-04-01 | Sheri Fritz | Const | 2019-04-03 | Mike Tabbert | 2019-04-03 | Mike Tabbert
DCS-01 | DCS-01 | PI02792 | Verified | Install in Control Room at Control Console, Mitsubishi Color Lazar Printer, 10-CTS-10CKC00GK901. | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-26 | Luis Cantu | 2019-07-26 | Mike Tabbert
DCS-01 | DCS-01 | PI02793 | Verified | 10DCSX0064, Pull Cable. | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-26 | Luis Cantu | 2019-07-26 | Mike Tabbert
DCS-01 | DCS-01 | PI02794 | Verified | 10DCSX0078, Pull Cable | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-27 | Mike Tabbert | 2019-07-27 | Mike Tabbert
DCS-01 | DCS-01 | PI02796 | Verified | 10DCSX0064, Terminate Cable | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-26 | Luis Cantu | 2019-07-26 | Mike Tabbert
DCS-01 | DCS-01 | PI02797 | Verified | 10DCSX0078, Terminate Cable | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-27 | Mike Tabbert | 2019-07-27 | Mike Tabbert
DCS-01 | DCS-01 | PI02800 | Verified | Dress out cables under all consoles in control room | B | E | Sheri Fritz | ITS | 2019-07-25 | Sheri Fritz | Const | 2019-08-08 | Mike Tabbert | 2019-08-08 | Mike Tabbert
DCS-01 | DCS-01 | PI02801 | Verified | Fix ground cables in HRSG 1B DCS | B | E | Dustin Futrell | McD | 2019-07-25 | Dustin Futrell | Const | 2019-07-31 | Ken Mundy | 2019-08-07 | Mike Tabbert
DCS-01 | DCS-01 | PI02802 | Verified | Fix ground cables in HRSG 1A DCS | B | E | Dustin Futrell | McD | 2019-07-25 | Dustin Futrell | Const | 2019-07-31 | Ken Mundy | 2019-08-07 | Mike Tabbert
DCS-01 | DCS-01 | PI02954 | Verified | Ground needs to be 4/0 cable going from drop 4, 5 and 6 and 7. | B | E | Dustin Futrell | McD | 2019-07-31 | Dustin Futrell | Const | 2019-08-02 | Ken Mundy | 2019-09-04 | James Wooley
DCS-01 | DCS-01 | PI16663 | Verified | 10-MWS-AIT-0152 - The clarifier settler turbidity (10-MWS-AIT-0152) range is 0-15 NTU so it routinely flatlines when the turbidity transmitter in the field reads higher. Increase the upper end of the DCS to match the settings on the field transmitter. | D | I | Mike Wilferd | McD | 2020-02-06 | Mike Wilferd | Comm | 2020-04-01 | Mike Wilferd | 2020-04-07 | Randy Carpenter
DCS-01 | DCS-01 | PI16664 | Verified | 10-GSC-T-0001 - Information on the Bulk CO2 tank is incorrect in the DCS. The signal diagram does not match the tank capacity listed in the spec sheet (drawing C-11642957 from Chart). | C | I | Mike Wilferd | McD | 2020-02-06 | Mike Wilferd | Comm | 2020-05-26 | Mike Wilferd | 2021-05-07 | John Watts
DCS-01 | DCS-01 | PI17832 | Verified | Unable to read any voltage on the 6.9kV bus. | C | E | Mike Wilferd | McD | 2020-03-16 | Mike Wilferd | Const | 2020-04-02 | Mike Wilferd | 2020-04-02 | Mike Wilferd
DCS-01 | DCS-01 | PI17853 | Verified | Ovation Enterprise Data Server (EDS) does not work properly. Logic does not update when changes are made. Macro's show up purple and should be red or green. Pop-ups have no data. Update EDS Resources button on the desktop does not work. This needs onsite support from Emerson to fix. | C | E | Mike Wilferd | McD | 2020-03-16 | Mike Wilferd | Comm | 2020-04-09 | Mike Wilferd | 2020-04-09 | Keith Pollock
DCS-01 | DCS-01 | PI17854 | Verified | Emerson Server's OPC 190 and OPC 191 were bypassed during commissioning and control system network drawings need to be updated to reflect the change in design. | C | E | Mike Wilferd | McD | 2020-03-16 | Mike Wilferd | Comm | 2020-04-02 | Mike Wilferd | 2020-07-28 | Keith Pollock
DCS-01 | DCS-01 | PI18127 | Verified | MVAR indication on 1B Unit is 10x the actual amount. | C | I | Mike Wilferd | McD | 2020-03-20 | Mike Wilferd | Comm | 2020-04-14 | Mike Wilferd | 2020-04-15 | Keith Pollock
DCS-01 | DCS-01 | PI18130 | Verified | 6.9 bus volt/amp indications do not work/not reading. | C | E | Mike Wilferd | McD | 2020-03-20 | Mike Wilferd | Comm | 2020-04-14 | Mike Wilferd | 2020-04-15 | Keith Pollock
DCS-01 | DCS-01 | PI18142 | Verified | 1A-FWS-M-0100B - 1A “B” BFP Motor has vibration issues. Stays at alarm point. 3.1 mils on X Motor inboard and outboard bearing. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-14 | William Mitchell | 2020-05-06 | John Watts
DCS-01 | DCS-01 | PI18143 | Verified | D04-ELC-213-R4 alarm is coming in 30000 times a day. | C | I | Mike Wilferd | McD | 2020-03-20 | Mike Wilferd | Comm | 2020-04-02 | Mike Wilferd | 2021-01-05 | Keith Pollock
DCS-01 | DCS-01 | PI18146 | Verified | Clarifier control loop needs to be tuned. | C | I | Mike Wilferd | McD | 2020-03-20 | Mike Wilferd | Comm | 2020-04-30 | Alan Joiner | 2020-04-30 | Michael Law
DCS-01 | DCS-01 | PI18148 | Verified | Drum 3-element control is not working in AUTO | C | I | Mike Wilferd | McD | 2020-03-20 | Mike Wilferd | Comm | 2020-04-20 | Mike Wilferd | 2021-07-22 | John Watts
DCS-01 | DCS-01 | PI18155 | Verified | RWS/Clarifier Logic - Prevents auto startup of the standby pump (10-RWS-P-0001A/B). | C | M | Mike Wilferd | McD | 2020-03-20 | Mike Wilferd | Comm | 2020-04-02 | Mike Wilferd | 2020-04-30 | John Watts
DCS-01 | DCS-01 | PI18156 | Verified | RWS Flocculant System has no DCS indication. | C | I | Mike Wilferd | McD | 2020-03-20 | Mike Wilferd | Comm | 2020-04-01 | Mike Wilferd | 2020-04-30 | John Watts
DCS-01 | DCS-01 | PI18160 | Verified | Ammonia dilution fans low flow switches are forced | C | M | Mike Wilferd | McD | 2020-03-20 | Mike Wilferd | Comm | 2020-04-14 | Albert Burge | 2020-04-17 | John Watts
DCS-01 | DCS-01 | PI18180 | Verified | 1C STG Shaft Current (1C-GMS-II-9002) continues to come into alarm at 20 AMPs. Note: McDermott Electrical Commissioning was notified. | C | I | Mike Wilferd | McD | 2020-03-24 | Mike Wilferd | Comm | 2020-04-20 | Mike Wilferd | 2021-01-05 | Keith Pollock
DCS-01 | DCS-01 | PI18191 | Verified | Fiber optic cables in the field did not match NET Drawings, all NET drawings need to be red-lined | C | I | Mike Tabbert | McD | 2020-03-27 | Mike Tabbert | Comm | 2020-05-26 | Mike Tabbert | 2020-05-26 | Randy Carpenter
DEM-01 | DEM-01 | PI00967 | Verified | "Install and test Cooling Tower Chem Storage Unloading Drain to CB. LK-10-DEM-PD-P42-0521-01, LK-10-DEM-PD-P42-0522-01 (90234-TP-DEM-01)" | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-17 | Terry Deaton | 2019-06-10 | Justin Houdeshell
DEM-01 | DEM-01 | PI00969 | Verified | "Install and test Clarifier Caustic Sump Drain to CB LK-10-DEM-PD-P42-0820-01, LK-10-DEM-PD-P42-0821-01 (90236-TP-DEM-01)" | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-17 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI00970 | Verified | Confirm all cleanouts accesible by chipping concrete as needed | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-16 | Terry Deaton | 2019-06-21 | Justin Houdeshell
DEM-01 | DEM-01 | PI00971 | Verified | Add drainage rocks to all valve boxes prior to backfill | B | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-06-07 | Terry Deaton | 2019-06-14 | Justin Houdeshell
DEM-01 | DEM-01 | PI00972 | Verified | Tag all valves / valve boxes | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-20 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI00973 | Verified | Repair Valve Box 1C-DEM-V-0531 | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-15 | Terry Deaton | 2019-05-15 | Justin Houdeshell
DEM-01 | DEM-01 | PI00974 | Verified | Repair Valve Box 10-DEM-V-0533 | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-15 | Terry Deaton | 2019-05-15 | Justin Houdeshell
DEM-01 | DEM-01 | PI00975 | Verified | Install Valve Box 10-DEM-V-0800 | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-15 | Terry Deaton | 2019-05-15 | Justin Houdeshell
DEM-01 | DEM-01 | PI00976 | Verified | Install Valve Box 10-DEM-V-0801 | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-15 | Terry Deaton | 2019-05-15 | Justin Houdeshell
DEM-01 | DEM-01 | PI00977 | Verified | Install Valve Box 10-DEM-V-0802 | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-15 | Terry Deaton | 2019-05-15 | Justin Houdeshell
DEM-01 | DEM-01 | PI00978 | Verified | Install Valve Box 10-DEM-V-0804 | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-17 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI00979 | Verified | Install Valve Box 10-DEM-V-0521 | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-17 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI00980 | Verified | Install Debris Screen LK-10-DEM-PD-P42-0620-01 | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-15 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI00981 | Verified | Install Debris Screen LK-10-DEM-PD-P42-0800-01 | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-08 | Terry Deaton | 2019-05-08 | Justin Houdeshell
DEM-01 | DEM-01 | PI00982 | Verified | Install Debris Screen LK-10-DEM-PD-P42-0805-01 | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-08 | Terry Deaton | 2019-05-08 | Justin Houdeshell
DEM-01 | DEM-01 | PI00983 | Verified | Install Debris Screen LK-10-DEM-PD-P42-0810-01 | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-08 | Terry Deaton | 2019-05-08 | Justin Houdeshell
DEM-01 | DEM-01 | PI00985 | Verified | Install grating STG LO Foundation - sump grate | A | C | Robert Risher | McD | 2019-05-06 | Robert Risher | Const | 2019-05-08 | Robert Risher | 2019-05-08 | Justin Houdeshell
DEM-01 | DEM-01 | PI00988 | Verified | Install grating Waste Water Containment | A | C | Robert Risher | McD | 2019-05-06 | Robert Risher | Const | 2019-05-08 | Robert Risher | 2019-05-08 | Justin Houdeshell
DEM-01 | DEM-01 | PI00989 | Verified | Clean out debris in drain hubs: east side of 1B CTG and at the south side of the sample building. | B | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-15 | Terry Deaton | 2019-05-15 | Justin Houdeshell
DEM-01 | DEM-01 | PI00990 | Verified | Cut down all threads in valve box north of 1B feedwater. | B | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-15 | Terry Deaton | 2019-05-15 | Justin Houdeshell
DEM-01 | DEM-01 | PI00991 | Verified | Remove rocks enough for valve access in 1A-DEM-0706 - between units A & B. | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-17 | Terry Deaton | 2019-07-22 | Danny Pase
DEM-01 | DEM-01 | PI00992 | Verified | Clean-out is inaccessible - sest side of GT 1B. | B | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-16 | Terry Deaton | 2019-07-23 | Danny Pase
DEM-01 | DEM-01 | PI00993 | Verified | Valve 1B-DEM-V-0708 is not installed at the 1B Seal Oil skid. | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-15 | Terry Deaton | 2019-05-15 | Justin Houdeshell
DEM-01 | DEM-01 | PI00994 | Verified | Chip concrete so the clean-out can be opened - south of the 1B filter house stairs. | A | C | Johnny Campbell | McD | 2019-05-06 | Johnny Campbell | Const | 2019-05-24 | Johnny Campbell | 2019-07-23 | Danny Pase
DEM-01 | DEM-01 | PI00995 | Verified | Chip concrete so the clean-out can be opened - west side of the 1B lube oil enclosure. | A | C | Johnny Campbell | McD | 2019-05-06 | Johnny Campbell | Const | 2019-05-24 | Johnny Campbell | 2019-07-23 | Danny Pase
DEM-01 | DEM-01 | PI00996 | Verified | Valve in box on the east side of the 1B switchyard is buried in dirt. | A | C | Johnny Campbell | McD | 2019-05-06 | Johnny Campbell | Const | 2019-05-24 | Johnny Campbell | 2019-07-22 | Danny Pase
DEM-01 | DEM-01 | PI00997 | Verified | Lower the clean-out at the stairs on the east side of 1A GT. | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-17 | Terry Deaton | 2019-06-21 | Justin Houdeshell
DEM-01 | DEM-01 | PI00998 | Verified | Chip concrete so the clean-out can be opened - west side of the 1A lube oil enclosure. | A | C | Johnny Campbell | McD | 2019-05-06 | Johnny Campbell | Const | 2019-07-23 | Johnny Campbell | 2020-01-21 | Michael Law
DEM-01 | DEM-01 | PI00999 | Verified | Valve 1A-DEM-V-0708 is not installed at the 1A Seal Oil skid. | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-15 | Terry Deaton | 2019-05-15 | Justin Houdeshell
DEM-01 | DEM-01 | PI01000 | Verified | Chip concrete so the clean-out can be opened - south of the 1A filter house stairs. | A | C | Johnny Campbell | McD | 2019-05-06 | Johnny Campbell | Const | 2019-05-24 | Johnny Campbell | 2019-07-23 | Danny Pase
DEM-01 | DEM-01 | PI01001 | Verified | Repair valve box 10-DEM-V-0535 - east side of the 1C switchyard transformer. | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-15 | Terry Deaton | 2019-05-15 | Justin Houdeshell
DEM-01 | DEM-01 | PI01002 | Verified | Clean-out is buried - west side of 1A GT. | A | P | Terry Deaton | McD | 2019-05-06 | Terry Deaton | Const | 2019-05-17 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI01005 | Verified | Clean-out missing (6") - northwest 1B HRSG. | A | P | Terry Deaton | McD | 2019-05-07 | Terry Deaton | Const | 2019-05-15 | Terry Deaton | 2019-05-15 | Justin Houdeshell
DEM-01 | DEM-01 | PI01006 | Verified | Clean-out missing north of STG Sampling Bldg. | A | P | Terry Deaton | McD | 2019-05-07 | Terry Deaton | Const | 2019-05-16 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI01018 | Verified | Flange is cracked at 1C-DEM-PD-P42-0356-01 - northeast corner of STG bldg. | A | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-15 | Terry Deaton | 2019-05-15 | Justin Houdeshell
DEM-01 | DEM-01 | PI01019 | Verified | Clean out debris at the drain hub at the "B" CCW heat exchanger. | A | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-16 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI01020 | Verified | Locate clean-outs at the north and west sides of the "A" CCW heat exchanger. | A | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-17 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI01021 | Verified | Water Treatment sump drain valves to be installed: 10-DEM-V-0701, 0702, 0703, 0704, 0705 and 0611. | A | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-17 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI01022 | Verified | 10-DEM-PD-P42-0735-01 - missing plastic sleeve - north side of the water treatment bldg. | A | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-16 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI01023 | Verified | Install clean-out at the south side of service water pumps. | A | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-16 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI01024 | Verified | Install clean-out at the south side of fire pump house. | A | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-16 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI01025 | Verified | 10-DEM-V-0802 - add rocks to valve box. | B | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-20 | Terry Deaton | 2019-05-20 | Justin Houdeshell
DEM-01 | DEM-01 | PI01166 | Verified | Complete Piping Test Package 90234 - Cooling Tower Chem. Storage Drains. | B | P | Terry Deaton | McD | 2019-05-24 | Terry Deaton | Const | 2019-06-14 | Terry Deaton | 2019-06-28 | Justin Houdeshell
DEM-01 | DEM-01 | PI02372 | Verified | Complete grating at the 1C Condensate Aqueous Ammonia Containment Sump. 1C-DEM-SUMP-0013. | C | S | Tim Gallegos | McD | 2019-07-19 | Tim Gallegos | Const | 2019-07-26 | Tim Gallegos | 2019-08-07 | Albert Burge
DEM-01 | DEM-01 | PI02373 | Verified | Clean out 1C Condensate Aqueous Ammonia Containment Sump. 1C-DEM-SUMP-0013. | C | C | Johnny Campbell | McD | 2019-07-19 | Johnny Campbell | Const | 2020-03-13 | Johnny Campbell | 2020-07-14 | Nelson Eichelberger
DEM-01 | DEM-01 | PI12662 | Verified | Containment drain valves to be where operations can lock them in the closed position. | C | P | James Beech | McD | 2019-10-31 | James Beech | Comm | 2020-05-05 | James Beech | 2021-04-21 | John Watts
DEM-01 | DEM-01 | PI12817 | Verified | There are three drains that are painted red & are not part of the fire protection system. These need to be painted a different color per NPFA code. 10-DEM-PIV-0507, 10-DEM-PIV-0517, 10-DEM-PIV-0803. Paint yellow. | C | C | Jorge Alexander | McD | 2019-11-06 | Jorge Alexander | Comm | 2019-11-21 | Jerry Smith | 2019-12-11 | Shannon Scott
DEM-01 | DEM-01 | PI13440 | Verified | Dig out around 1C-DEM-V-0529; 1C STG Main Transformer Containment Sump Drain Valve so top half of valve is exposed | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-08-06 | Brooks Baker | 2021-02-24 | John Watts
DEM-01 | DEM-01 | PI13441 | Verified | Replace broken valve box cover at 10-DEM-V-0601; Service Water Pumps Containment Sump Drain Isolation | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-01 | Brooks Baker | 2020-04-07 | Randy Carpenter
DEM-01 | DEM-01 | PI13442 | Verified | 10-DEM-V-0602; Wastewater Treatment Tanks Containment Sump Drain Valve will not fully close | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-07-24 | Nelson Eichelberger
DEM-01 | DEM-01 | PI13443 | Verified | Clean out Wastewater Treatment Tanks Containment Sump, sump does not drain when valve is open | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-15 | Nelson Eichelberger
DEM-01 | DEM-01 | PI13444 | Verified | Cannot manipulate 10-DEM-V-0505; Circ Water Sodium Hypochlorite Containment Sump Drain Valve | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-07-24 | Nelson Eichelberger
DEM-01 | DEM-01 | PI13445 | Verified | Need T-Handle for 10-DEM-V-0505; Circ Water Sodium Hypochlorite Containment Sump Drain Valve | C | C | Tim Green | McD | 2019-11-24 | Tim Green | Comm | 2020-08-06 | Tim Green | 2020-08-14 | Nelson Eichelberger
DEM-01 | DEM-01 | PI13446 | Verified | Rewrap around 90 at 1C-DEM-0608; 1C Condensate Aqueous Ammonia Containment Sump Drain | C | C | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-04-29 | James Beech | 2021-05-07 | John Watts
DEM-01 | DEM-01 | PI13447 | Verified | Clean out all Containments and Sumps within DEM-01 subsystem, cleanout to be verified by Entergy representative | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-09 | Michael Law | 2021-01-05 | Keith Pollock
DEM-01 | DEM-01 | PI13448 | Verified | Valve box not installed at 10-DEM-V-0612; Filter Press & Thickener Polymer Containment Sump Drain Valve | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-03 | Brooks Baker | 2020-04-07 | Randy Carpenter
DEM-01 | DEM-01 | PI13449 | Verified | 10-DEM-V-0612; Filter Press & Thickener Polymer Containment Sump Drain Valve needs tag | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-09 | Bobby Williams | 2020-07-28 | Nelson Eichelberger
DEM-01 | DEM-01 | PI13450 | Verified | 10-DEM-V-0612; Filter Press & Thickener Polymer Containment Sump needs grating cover | C | C | Alan Huntsman | McD | 2019-11-24 | Alan Huntsman | Comm | 2020-01-16 | Tim Gallegos | 2020-07-28 | Nelson Eichelberger
DEM-01 | DEM-01 | PI13451 | Verified | 10-DEM-V-0612; Filter Press & Thickener Polymer Containment Sump Drain Line needs to be wrapped | C | C | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-04-29 | James Beech | 2021-05-24 | Keith Pollock
DEM-01 | DEM-01 | PI13452 | Verified | Remove concrete splatter from 10-DEM-V-0613; Filter Press Feed Pump Containment Sump Drain Valve | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-07-24 | Nelson Eichelberger
DEM-01 | DEM-01 | PI13453 | Verified | Valve box not installed at 10-DEM-V-0613; Filter Press Feed Pump Containment Sump Drain Valve | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-15 | Nelson Eichelberger
DEM-01 | DEM-01 | PI13454 | Verified | 10-DEM-V-0613; Filter Press Feed Pump Containment Sump Drain Valve needs tag | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-09 | Bobby Williams | 2020-02-02 | Shannon Scott
DEM-01 | DEM-01 | PI13455 | Verified | 10-DEM-V-0613; Filter Press Feed Pump Containment Sump Drain Line needs to be wrapped | C | C | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-04-29 | James Beech | 2021-04-21 | John Watts
DEM-01 | DEM-01 | PI13456 | Verified | 10-DEM-V-0613; Filter Press Feed Pump Containment Sump needs grating cover | C | C | Bobby Williams | McD | 2019-11-24 | Bobby Williams | Comm | 2020-02-13 | Bobby Williams | 2020-04-06 | Bernard Stasse
DEM-01 | DEM-01 | PI13457 | Verified | 10-DEM-V-0613; Filter Press Feed Pump Containment Sump Drain Valve stem needs nut | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-07-24 | Nelson Eichelberger
DEM-01 | DEM-01 | PI13458 | Verified | Verify space between back of step and containment wall meets OSHA Standards at each entrance to Demin/Wastewater Treatment containments, W side of Demin Building | C | P | Bobby Williams | McD | 2019-11-24 | Bobby Williams | Comm |  |  | 2020-01-13 | Michael Law
DEM-01 | DEM-01 | PI13459 | Verified | Round off sharp edges where grating has been cut around all Demin/Wastewater Treatment drain valves | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-15 | Nelson Eichelberger
DEM-01 | DEM-01 | PI13460 | Verified | Remove tape from 10-DEM-PIV-0507; Ammonia Tank Containment Sump Post Indicator Valve | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-13 | Shannon Scott
DEM-01 | DEM-01 | PI13461 | Verified | Remove tape from 10-DEM-PIV-0517; Ammonia Unloading Area Sump Post Indicator Valve | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-13 | Shannon Scott
DEM-01 | DEM-01 | PI13462 | Verified | Replace defaced tag at 1A-DEM-V-0502; 1A Phosphate Containment Sump Drain Valve | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-09 | Bobby Williams | 2020-02-02 | Shannon Scott
DEM-01 | DEM-01 | PI13463 | Verified | Remove cable stub up and loose grounding rod between valve box and containment wall at 1A-DEM-V-0502; 1A Phosphate Containment Sump Drain Valve | C | E | Chris Colvin | McD | 2019-11-24 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2020-07-22 | Dave Goldak
DEM-01 | DEM-01 | PI13464 | Verified | Replace broken valve box and cover at 10-DEM-V-0521; Cooling Tower Chemical Unloading Area Sump | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-28 | Brooks Baker | 2020-07-22 | Dave Goldak
DEM-01 | DEM-01 | PI13465 | Verified | Dig out around 10-DEM-V-0521; Cooling Tower Chemical Unloading Area Sump Drain Valve so top half of valve is exposed | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-28 | Brooks Baker | 2020-08-06 | Nelson Eichelberger
DEM-01 | DEM-01 | PI13466 | Verified | Install valve box at 10-DEM-V-0610; Raw Water Flocculant Tank Containment Sump Drain Valve | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-28 | Michael Law | 2021-04-21 | John Watts
DEM-01 | DEM-01 | PI13467 | Verified | Need grating cover at 1A-DEM-SUMP-0025; 1A GT Generator Seal Oil Unit Sump | C | C | Tim Gallegos | McD | 2019-11-24 | Tim Gallegos | Comm | 2020-05-07 | Tim Gallegos | 2020-07-22 | Dave Goldak
DEM-01 | DEM-01 | PI13468 | Verified | Missing tag at 1A-DEM-V-0706; 1A Ammonia Flow Control Skid Containment | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-09 | Bobby Williams | 2020-01-13 | Shannon Scott
DEM-01 | DEM-01 | PI13469 | Verified | Back fill grading area between containment wall and valve box at 10-DEM-V-0802; MWS Polymer Containment Sump | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-28 | Brooks Baker | 2020-07-22 | Dave Goldak
DEM-01 | DEM-01 | PI13470 | Verified | Remove dirt out of 10-DEM-SUMP-0030; MWS Polymer Containment Sump | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-28 | Brooks Baker | 2021-04-21 | John Watts
DEM-01 | DEM-01 | PI13471 | Verified | Raise valve box to match grade at 10-DEM-V-0802; MWS Polymer Containment Sump | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-28 | Brooks Baker | 2020-07-22 | Dave Goldak
DEM-01 | DEM-01 | PI13472 | Verified | Ensure top of all valve boxes are 1" higher than grade but not lower than grade | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-09 | Michael Law | 2020-04-09 | Michael Law
DEM-01 | DEM-01 | PI13473 | Verified | Replace all cracked or broken floor drain covers | C | C | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-05-08 | James Beech | 2021-04-21 | John Watts
DEM-01 | DEM-01 | PI13474 | Verified | Remove tape and tape residue from all drain hubs | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-15 | Bobby Williams | 2020-02-02 | Shannon Scott
DEM-01 | DEM-01 | PI13475 | Verified | Clean out underneath and around all Floor Drains | C | C | Johnny Campbell | McD | 2019-11-24 | Johnny Campbell | Comm | 2020-04-08 | Johnny Campbell | 2021-04-21 | John Watts
DEM-01 | DEM-01 | PI13476 | Verified | Clean out around all Drain Hubs | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-28 | Brooks Baker | 2021-04-21 | John Watts
DEM-01 | DEM-01 | PI13477 | Verified | Provide T-Handle for removing threaded caps inside Clean Outs | C | C | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-05-21 | James Beech | 2021-05-24 | Keith Pollock
DEM-01 | DEM-01 | PI13478 | Verified | Back fill at all areas where Hubs or Clean Outs are currently above grade | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-28 | Brooks Baker | 2020-10-06 | Dave Goldak
DEM-01 | DEM-01 | PI13479 | Verified | Four 10" stub up drain piping needs Hub installed at E side of HRSG A | C | C | Tim Green | McD | 2019-11-24 | Tim Green | Comm | 2020-09-15 | Jason Ezell | 2020-10-06 | Dave Goldak
DEM-01 | DEM-01 | PI13480 | Verified | Four 10" stub up drain piping needs Hub installed at E side of HRSG B | C | P | Tim Green | McD | 2019-11-24 | Tim Green | Comm | 2020-09-15 | Jason Ezell | 2020-10-06 | Dave Goldak
DEM-01 | DEM-01 | PI13481 | Verified | Replace 3" Clean Out cracked man-way cover at ground floor STG building,near Closed Cooling Water Pumps, E side of pumps | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-13 | Shannon Scott
DEM-01 | DEM-01 | PI13482 | Verified | Back fill grade around 6" Clean Out located NW of CTG/HRSG A Stack | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-28 | Brooks Baker | 2020-07-27 | Dave Goldak
DEM-01 | DEM-01 | PI13483 | Verified | Back fill grade around 6" Clean Out located E side of Unit B Feedwater Pump Enclosure | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-03 | Brooks Baker | 2020-04-07 | Randy Carpenter
DEM-01 | DEM-01 | PI13484 | Verified | 6" Clean Out man-way cover is missing screw, E of Unit B Feedwater Pump Enclosure | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-13 | Shannon Scott
DEM-01 | DEM-01 | PI13485 | Verified | 6" Clean Out needs to be straightened and tightened at E side of Unit B Feedwater Pump Enclosure | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-13 | Shannon Scott
DEM-01 | DEM-01 | PI13486 | Verified | Back fill grade around 6" Clean Out W side of HRSG B, E of Fuel Gas Heater | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-28 | Brooks Baker | 2020-07-22 | Dave Goldak
DEM-01 | DEM-01 | PI13487 | Verified | 6" Close Out W side of HRSG B, E of Fuel Gas Heater is missing man-way cover screw | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-13 | Shannon Scott
DEM-01 | DEM-01 | PI13488 | Verified | Back fill around 6" Clean Out W side of GT B near GT CO2 Fire Supression Tank | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-28 | Brooks Baker | 2020-07-22 | Dave Goldak
DEM-01 | DEM-01 | PI13489 | Verified | Back fill around 6" Clean Out S end of GT B near SW Lube Oil Enclosure Door | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-03 | Brooks Baker | 2020-04-07 | Randy Carpenter
DEM-01 | DEM-01 | PI13490 | Verified | 3" Clean Out at SE side of GT B needs back fill | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-03 | Brooks Baker | 2020-04-07 | Randy Carpenter
DEM-01 | DEM-01 | PI13491 | Verified | 3" Clean Out at SE side of GT B has missing man-way cover screw | C | C | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-04-14 | James Beech | 2021-04-21 | John Watts
DEM-01 | DEM-01 | PI13492 | Verified | Back fill around 3" Clean Out at NE side of GT/HRSG B Stack, behind CEMS B Enclosure | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-03 | Brooks Baker | 2020-04-07 | Randy Carpenter
DEM-01 | DEM-01 | PI13493 | Verified | Back fill around 6" Clean Out at S end of GT A near SW Lube Oil Enclosure Door | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-03 | Brooks Baker | 2020-04-07 | Randy Carpenter
DEM-01 | DEM-01 | PI13494 | Verified | 3" Clean Out has broken Hub at E side of GT A Lube Oil Enclosure | C | C | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-04-14 | James Beech | 2021-05-07 | John Watts
DEM-01 | DEM-01 | PI13495 | Verified | 3" Clean Out needs to be straightend at E side of GT A Lube Oil Enclosure | C | C | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-04-13 | James Beech | 2020-08-20 | Nelson Eichelberger
DEM-01 | DEM-01 | PI13496 | Verified | 6" Clean Out at E side of GT A Blade Wash Skid has no interior threaded cap | C | C | Tim Gallegos | McD | 2019-11-24 | Tim Gallegos | Comm | 2020-05-11 | Tim Gallegos | 2021-04-21 | John Watts
DEM-01 | DEM-01 | PI13497 | Verified | No manway screws for 6" Clean Out at W side of GT A near Fuel Gas Heater | C | C | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-05-05 | James Beech | 2021-04-21 | John Watts
DEM-01 | DEM-01 | PI13498 | Verified | Hub is loose at 6" Clean Out at E side of Feedwater Pump Enclosure A | C | C | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-04-14 | James Beech | 2021-04-21 | John Watts
DEM-01 | DEM-01 | PI13499 | Verified | Hub is loose at 6" Clean Out at NW side of Unit A Stack | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-06 | Bernard Stasse
DEM-01 | DEM-01 | PI13500 | Verified | Water backing out of drain line, past interior screw cap at 6" Clean Out at W side of GT A near CO2 Fire Suppresion Tank, needs to be cleaned out | C | P | William Mitchell | McD | 2019-11-24 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2021-04-21 | John Watts
DEM-01 | DEM-01 | PI13501 | Verified | 3" Clean Out NE of Unit A Stack is holding water | C | P | William Mitchell | McD | 2019-11-24 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2020-10-06 | Dave Goldak
DEM-01 | DEM-01 | PI13502 | Verified | Back fill around 3" Clean Out NE of Unit A Stack | C | C | Brooks Baker | McD | 2019-11-24 | Brooks Baker | Comm | 2020-04-03 | Brooks Baker | 2020-04-07 | Randy Carpenter
DEM-01 | DEM-01 | PI13503 | Verified | Missing one of the 7 Clean Outs inside Demin Water Building | C | P | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-04-06 | Bernard Stasse
DEM-01 | DEM-01 | PI13504 | Verified | Floor Drain inside Firewater Electric Pump House not shown on P&ID | C | P | Kelvin Cook | McD | 2019-11-24 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-07 | Randy Carpenter
DEM-01 | DEM-01 | PI13505 | Verified | Floor Drain inside Firewater Diesel Pump House not shown on P&ID | C | P | Kelvin Cook | McD | 2019-11-24 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-07 | Randy Carpenter
DEM-01 | DEM-01 | PI13506 | Verified | Reinstall broken Clean Out S of Fire Water Pump House | C | C | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-05-05 | James Beech | 2020-07-22 | Dave Goldak
DEM-01 | DEM-01 | PI13507 | Verified | Need T-Handle extensions to lock the containment Valves | C | C | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
DEM-01 | DEM-01 | PI13508 | Verified | Need to handle extensions to remove clean out caps | C | C | James Beech | McD | 2019-11-24 | James Beech | Comm | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
DEM-01 | DEM-01 | PI17220 | Verified | Unplug floor drain under the CCW heat exchanger - NW corner of STG building. | C | P | Tim Green | McD | 2020-02-25 | Tim Green | Const | 2020-08-14 | Tim Green | 2020-10-06 | Dave Goldak
DEM-01 | DEM-01 | PI17319 | Verified | Missing drain cover North of Air Compressor. | C | P | Tim Green | McD | 2020-02-28 | Tim Green | Comm | 2020-10-06 | Eric Policarpio | 2020-10-06 | Dave Goldak
DEM-01 | DEM-01 | PI17327 | Verified | Fix floor drain NE of Lube Oil Containment. | C | P | James Beech | McD | 2020-02-28 | James Beech | Comm | 2020-03-27 | James Beech | 2020-08-06 | Dave Goldak
DEM-01 | DEM-01 | PI17329 | Verified | Open drain at column C/7 -SE of Condenser. | C | P | Tim Green | McD | 2020-02-28 | Tim Green | Comm | 2020-10-06 | Eric Policarpio | 2020-10-06 | Dave Goldak
DEM-01 | DEM-01 | PI17340 | Verified | Drain in the Lube Oil containment is blocked- standing water. | C | P | James Beech | McD | 2020-02-28 | James Beech | Comm | 2020-03-27 | James Beech | 2020-08-06 | Dave Goldak
DEM-01 | DEM-01 | PI18022 | Verified | 10-DEM-SUMP-0028 - Wash down the clarifier coagulant injection pump drain pan and the coagulant tank containment. Use a vacuum truck to remove the water and residual coagulant. Note: Do not drain the wash water to stormwater pond. | C | M | William Mitchell | McD | 2020-03-17 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2020-08-17 | Dave Goldak
DEM-01 | DEM-01 | PI18030 | Verified | Create/cut a small area in the grating to sample the contents in the containment. Operators are unable to sample the contents in the containment, which prevents it from being discharged. | C | S | Tim Gallegos | McD | 2020-03-17 | Tim Gallegos | Comm | 2020-05-07 | Tim Gallegos | 2021-05-24 | Keith Pollock
DGS-01 | DGS-01 | PI00087 | Verified | Complete installation of the following cables, 10DGSC0001, 10DGSC0005, 10DGSC0006, 10DGSK0001 | B | E | Logan Holland | CAT | 2019-01-18 | Logan Holland | Const | 2019-03-20 | Mike Tabbert | 2019-03-20 | Mike Tabbert
DGS-01 | DGS-01 | PI00090 | Verified | Complete all completion forms. | A | E | Shannon Savoy | McD | 2019-01-18 | Shannon Savoy | Const | 2019-02-08 | Ed Gober | 2019-02-12 | Mike Tabbert
DGS-01 | DGS-01 | PI00095 | Verified | Replace grating on stair platforms - serrated instead of plain | C | C | Robert Risher | McD | 2019-01-22 | Robert Risher | Const | 2019-04-01 | Robert Risher | 2019-04-03 | Tom Noble
DGS-01 | DGS-01 | PI00141 | Verified | Seal cable penetration in 10-DGS-DWS-0001 at 10-NJS-MCC-0002 in the main PDC. | C | E | Chris Colvin | McD | 2019-01-31 | Chris Colvin | Const | 2020-05-04 | Matt Gilmore | 2020-05-19 | Mike Tabbert
DGS-01 | DGS-01 | PI00142 | Verified | Provide calculated arc flash label on 10-NJS-MCC-0002 and 10-NJS-SWG-0002 in the main PDC. | B | E | Michael Law | McD | 2019-01-31 | Michael Law | Const | 2019-06-13 | Mike Tabbert | 2019-06-13 | Mike Tabbert
DGS-01 | DGS-01 | PI00143 | Verified | Red line dwg. LK-10-DGS-EE-WIR-0001 rev. 0 to reflect termination points in 10-DGS-DSW-0001. | A | E | Mike Tabbert | McD | 2019-01-31 | Mike Tabbert | Const | 2019-02-05 | Mike Tabbert | 2019-02-07 | Shannon Scott
DGS-01 | DGS-01 | PI00144 | Verified | Touch up supports for 10-DGS-BD-0001 at north side of main PDC. | C | E | Shannon Savoy | McD | 2019-01-31 | Shannon Savoy | Const | 2019-02-08 | Dan Dula | 2019-03-04 | Shannon Scott
DGS-01 | DGS-01 | PI00145 | Verified | Grout supports for 10-DGS-BD-0001 at north side of main PDC. | C | C | Johnny Campbell | McD | 2019-01-31 | Johnny Campbell | Const | 2019-02-12 | Johnny Campbell | 2019-03-04 | Shannon Scott
DGS-01 | DGS-01 | PI00146 | Verified | Grout supports for elec. pull box at the north side of the emergency diesel generator. | C | C | Johnny Campbell | McD | 2019-01-31 | Johnny Campbell | Const | 2019-03-11 | Johnny Campbell | 2019-03-15 | Shannon Scott
DGS-01 | DGS-01 | PI00147 | Verified | Power cables for 10-DGS-DSW-0001 and 10-DSG-PNL-0001 at the north end inside the emergency diesel generator enclosure need flex grounds. | C | E | Phil Work | McD | 2019-01-31 | Phil Work | Const | 2019-02-14 | Dan Dula | 2019-03-04 | Shannon Scott
DGS-01 | DGS-01 | PI00148 | Verified | Plug the hole for the temporary power cable at the north end of the emergency diesel generator (when temp. power is disconnected). | C | E | Dustin Futrell | McD | 2019-01-31 | Dustin Futrell | Const | 2019-10-04 | Richard Cruz | 2019-10-15 | Shannon Scott
DGS-01 | DGS-01 | PI00149 | Verified | Clean / remove duct tape on the emergency diesel generator control panel. | C | E | Phil Work | McD | 2019-01-31 | Phil Work | Const | 2019-02-08 | Dan Dula | 2019-02-11 | Mike Tabbert
DGS-01 | DGS-01 | PI00150 | Verified | Stair stringers (material) not per contract or specification at the emergency diesel generator. | D | E | Michael Law | McD | 2019-01-31 | Michael Law | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
DGS-01 | DGS-01 | PI00151 | Verified | Handrail assembly not per contract or specification at the emergency diesel generator. | D | E | Michael Law | McD | 2019-01-31 | Michael Law | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
DGS-01 | DGS-01 | PI00152 | Verified | Identify / label fuel fill and drain plugs at the emergency diesel generator. | C | M | Shane Crowe | McD | 2019-01-31 | Shane Crowe | Const | 2019-02-18 | Shane Crowe | 2019-03-06 | Dave Goldak
DGS-01 | DGS-01 | PI00153 | Verified | West load bank access door - lacks access platform to elevation at the emergency diesel generator. | D | E | Kevin Leppert | McD | 2019-01-31 | Kevin Leppert | Const | 2020-02-07 | Keith Pollock | 2020-03-03 | Keith Pollock
DGS-01 | DGS-01 | PI00154 | Verified | Patch gaps / remove slack from bird screen at intake plenums at the emergency diesel generator | D | M | Michael Law | McD | 2019-01-31 | Michael Law | Const | 2020-05-11 | Michael Law | 2020-07-24 | Nelson Eichelberger
DGS-01 | DGS-01 | PI00155 | Verified | Tighten / seal cable tray penetration cover plate for weather tight (upper left corner) at the emergency diesel generator enclosure. | C | E | Shannon Savoy | McD | 2019-01-31 | Shannon Savoy | Const | 2019-01-31 | Mike Tabbert | 2019-03-06 | Dave Goldak
DGS-01 | DGS-01 | PI00178 | Verified | High-temp caulk not applied to rooftop exhaust of the diesel generator. Refer to installation manual. | C | M | Shane Crowe | McD | 2019-02-04 | Shane Crowe | Const | 2019-02-18 | Shane Crowe | 2019-03-06 | Dave Goldak
DGS-01 | DGS-01 | PI00202 | Verified | Remove all shipping stops. | B | M | Logan Holland | McD | 2019-02-25 | Logan Holland | Const | 2019-04-03 | Gregg Sellers | 2019-04-11 | Dave Goldak
DGS-01 | DGS-01 | PI00203 | Verified | Check that vibration mountings are secure & set correctly. | B | M | Logan Holland | McD | 2019-02-25 | Logan Holland | Const | 2019-04-03 | Gregg Sellers | 2019-04-11 | Dave Goldak
DGS-01 | DGS-01 | PI00276 | Verified | Fuel fill to be a valve connection accessible from outer perimeter of the enclosure base. | C | M | Michael Law | CAT | 2019-03-06 | Michael Law | Comm | 2019-06-21 | Nelson Eichelberger | 2019-06-21 | Nelson Eichelberger
DGS-01 | DGS-01 | PI00872 | Verified | The word "Circuit" on the Diesel Generator Circuit Breaker tag is mispelled. | C | E | Mike Tabbert | McD | 2019-05-01 | Mike Tabbert | Comm | 2020-01-22 | Mike Tabbert | 2020-01-28 | Fred Michael
DGS-01 | DGS-01 | PI04781 | Verified | Emergency Diesel Generator enclosure is leaking, needs repair. | C | S | Shane Crowe | McD | 2019-09-05 | Shane Crowe | Comm | 2019-11-04 | Joshua Sturgeon | 2019-12-11 | Shannon Scott
DGS-01 | DGS-01 | PI09715 | Verified | Tighten door handle screws at northwest and southwest side of enclosure | C | M | Shane Crowe | McD | 2019-10-16 | Shane Crowe | Comm | 2020-01-15 | Shane Crowe | 2020-01-22 | Shannon Scott
DGS-01 | DGS-01 | PI09716 | Verified | Clean up inside of Diesel Generator enclosure | C | C | Johnny Campbell | McD | 2019-10-16 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-04-07 | Randy Carpenter
DGS-01 | DGS-01 | PI09717 | Verified | Reduce length of enclosure hold down anchor bolts | C | M | Shane Crowe | McD | 2019-10-16 | Shane Crowe | Comm | 2019-10-18 | Joshua Sturgeon | 2019-10-28 | Shannon Scott
DGS-01 | DGS-01 | PI09718 | Verified | Enclosure is leaking at floor level | C | M | Shane Crowe | McD | 2019-10-16 | Shane Crowe | Comm | 2019-12-17 | Shane Crowe | 2019-12-21 | Shannon Scott
DGS-01 | DGS-01 | PI15897 | Verified | 10-DGS-DE-0001 - Emergency Diesel Generator's external oil reservoir has a slow leak where the EDG hose connects to bottom of external oil reservoir. | C | M | Shane Crowe | McD | 2020-01-13 | Shane Crowe | Comm | 2020-01-15 | Shane Crowe | 2020-01-22 | Shannon Scott
DGS-01 | DGS-01 | PI18145 | Verified | The Emergency Diesel Generator's cooling water solenoid valve failed. | C | P | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2021-01-05 | Keith Pollock
DWS-01 | DWS-01 | PI04786 | Verified | Need Main PDC Battery Room eyewash station working. | B | M | William Mitchell | McD | 2019-09-05 | William Mitchell | Comm | 2019-12-09 | Alan Joiner | 2019-12-19 | Randy Carpenter
DWS-01 | DWS-01 | PI05100 | Verified | Tag all valves. | C | P | James Beech | McD | 2019-09-12 | James Beech | Const |  |  | 2019-12-09 | Alan Joiner
DWS-01 | DWS-01 | PI05101 | Verified | No coating on threaded connections. | B | P | Kelvin Cook | McD | 2019-09-12 | Kelvin Cook | Const | 2020-03-10 | Kelvin Cook | 2020-03-10 | Nelson Eichelberger
DWS-01 | DWS-01 | PI05102 | Verified | At Main PDC - 10-DWS-H-0001 - conduit needs low point drains. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
DWS-01 | DWS-01 | PI05103 | Verified | At Main PDC - 10-DWS-H-0001 - mount warning light. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05104 | Verified | At Main PDC - 10-DWS-H-0001 - conduit & seal tite to FSH-0001. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05105 | Verified | At Main PDC - 10-DWS-H-0001 - ground seal tite. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05106 | Verified | At Main PDC - 10-DWS-H-0001 - ground panel. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05107 | Verified | At Main PDC - 10-DWS-H-0001 - support anchor bolts too short. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05108 | Verified | At Main PDC - 10-DWS-H-0001 - need condulet covers. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
DWS-01 | DWS-01 | PI05109 | Verified | At Main PDC - 10-DWS-SWR-0001 - need pipe support. | B | P | Kelvin Cook | McD | 2019-09-12 | Kelvin Cook | Const | 2019-12-09 | James Beech | 2020-01-01 | Albert Burge
DWS-01 | DWS-01 | PI05110 | Verified | At Main PDC - 10-DWS-SWR-0001 - SRV-0107 - vent to safe location. | B | P | Kelvin Cook | McD | 2019-09-12 | Kelvin Cook | Const | 2019-10-28 | Kelvin Cook | 2020-01-27 | Michael Law
DWS-01 | DWS-01 | PI05111 | Verified | At Main PDC - 10-DWS-SWR-0001 - tighten u-bolt on 10-DWS-PD-462-0015. | B | P | James Beech | McD | 2019-09-12 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
DWS-01 | DWS-01 | PI05112 | Verified | At Main PDC - 10-DWS-SWR-0001 - grout supports. | C | C | Johnny Campbell | McD | 2019-09-12 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2019-12-09 | Alan Joiner
DWS-01 | DWS-01 | PI05113 | Verified | Main PDC - Red line P&ID 10-DWS-PID-0002 to show valves in battery room and at U/G connection. | C | P | James Beech | McD | 2019-09-12 | James Beech | Const | 2020-04-14 | James Beech | 2020-04-20 | Michael Law
DWS-01 | DWS-01 | PI05114 | Verified | At Main PDC - Seal floor penetrations in Battery Room. | B | C | Tim Gallegos | McD | 2019-09-12 | Tim Gallegos | Const | 2019-10-07 | Tim Gallegos | 2019-10-28 | Kelvin Cook
DWS-01 | DWS-01 | PI05115 | Verified | At 1C Condensate Chem Feed Skid - 1C-DWS-SWR-0009 - SRV-0910 - vent to safe location. | B | P | Kelvin Cook | McD | 2019-09-12 | Kelvin Cook | Const | 2020-01-07 | Kelvin Cook | 2020-02-27 | Michael Law
DWS-01 | DWS-01 | PI05116 | Verified | At 1C Condensate Chem Feed Skid - 1C-DWS-SWR-0009 - replace or tighten u-bolt. | B | P | James Beech | McD | 2019-09-12 | James Beech | Const |  |  | 2019-11-23 | Kelvin Cook
DWS-01 | DWS-01 | PI05117 | Verified | At 1C Condensate Chem Feed Skid - 1C-DWS-SWR-0009 - red line vendor P&ID. | C | P | Kelvin Cook | McD | 2019-09-12 | Kelvin Cook | Const |  |  | 2019-10-28 | Kelvin Cook
DWS-01 | DWS-01 | PI05118 | Verified | At 1C Condensate Chem Feed Skid - 1C-DWS-SWR-0009 - grout supports. | C | C | Johnny Campbell | McD | 2019-09-12 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2019-12-09 | Alan Joiner
DWS-01 | DWS-01 | PI05119 | Verified | At 1C Condensate Chem Feed Skid - 1C-DWS-H-0009 - label panel. | C | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
DWS-01 | DWS-01 | PI05120 | Verified | At 1C Condensate Chem Feed Skid - 1C-DWS-H-0009 - ground panel. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05121 | Verified | At 1C Condensate Chem Feed Skid - 1C-DWS-SWR-0009 - ground seal tite for light to flow switch. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05122 | Verified | At 1C Condensate Chem Feed Skid - 1C-DWS-H-0009 - re-route conduit for light/flow switch. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05123 | Verified | At 1C sample panel - ISO 1C-DWS-0040 not installed. | A | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-09-25 | Kelvin Cook
DWS-01 | DWS-01 | PI05124 | Verified | At WTB - 10-DWS-H-0003 - ground panel. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-13 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05125 | Verified | At WTB - 10-DWS-H-0003 - label panel. | C | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
DWS-01 | DWS-01 | PI05126 | Verified | At WTB - 10-DWS-H-0003 - install seal tite. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-13 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05127 | Verified | At WTB - 10-DWS-H-0003 - install conduit seal tite & grounding. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-13 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05128 | Verified | At WTB - 10-DWS-SWR-0003 - mount flow switch. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-13 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05129 | Verified | At WTB - 10-DWS-SWR-0002 - install conduit seal tite & grounding. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-13 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05130 | Verified | At WTB - 10-DWS-SWR-0002 - mount flow switch. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-13 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05131 | Verified | At WTB - 10-DWS-H-0003 - install raceway / grounding. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-13 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05132 | Verified | At WTB - piping & conduit touching downstream of FSH-0015. Need room for insulation. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-13 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05133 | Verified | At Make up Water Treatment area - 10-DWS-H-0004 - ground panel. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05134 | Verified | At Make up Water Treatment area - 10-DWS-H-0004 - label panel. | C | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-15 | Fred Michael
DWS-01 | DWS-01 | PI05135 | Verified | At Make up Water Treatment area - 10-DWS-H-0004 - install raceway / grounding. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05136 | Verified | At Make up Water Treatment area - 10-DWS-H-0004 - install & ground seal tite. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05137 | Verified | At Make up Water Treatment area - 10-DWS-SWR-0004 - mount light & switch. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05138 | Verified | At Make up Water Treatment area - 10-DWS-H-0004 - Install conduit & seal tite to switch. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05139 | Verified | At Make up Water Treatment area - 10-DWS-SWR-0004 - SRV-0007 - vent to safe location. | B | P | Kelvin Cook | McD | 2019-09-12 | Kelvin Cook | Const | 2020-01-07 | Kelvin Cook | 2020-02-27 | Michael Law
DWS-01 | DWS-01 | PI05140 | Verified | At Make up Water Treatment area - 10-DWS-SWR-0004 - install support 10-DWS-PD-HRG-01 38. | A | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const | 2019-09-30 | Kelvin Cook | 2019-09-30 | Kelvin Cook
DWS-01 | DWS-01 | PI05141 | Verified | At Make up Water Treatment area - 10-DWS-SWR-0004 - install support 10-DWS-PD-HRG-01 43. | A | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const | 2019-09-30 | Kelvin Cook | 2019-09-30 | Kelvin Cook
DWS-01 | DWS-01 | PI05142 | Verified | At Make up Water Treatment area - 10-DWS-SWR-0004 - install support 10-DWS-PD-HRG-01 45. | A | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const | 2019-09-30 | Kelvin Cook | 2019-09-30 | Kelvin Cook
DWS-01 | DWS-01 | PI05143 | Verified | At Make up Water Treatment area - 10-DWS-SWR-0004 - install support 10-DWS-PD-HRG-01 46. | A | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const | 2019-09-30 | Kelvin Cook | 2019-09-30 | Kelvin Cook
DWS-01 | DWS-01 | PI05144 | Verified | At Make up Water Treatment area - 10-DWS-SWR-0004 - install support 10-DWS-PD-HRG-0004. | B | P | James Beech | McD | 2019-09-12 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
DWS-01 | DWS-01 | PI05145 | Verified | At Make up Water Treatment area - 10-DWS-SWR-0004 - install support 10-DWS-PD-HRG-0005. | B | P | James Beech | McD | 2019-09-12 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
DWS-01 | DWS-01 | PI05146 | Verified | At Make up Water Treatment area - 10-DWS-SWR-0004 - install support 10-DWS-PD-HRG-0006. | A | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const | 2019-09-30 | Kelvin Cook | 2019-09-30 | Kelvin Cook
DWS-01 | DWS-01 | PI05147 | Verified | At Make up Water Treatment area - 10-DWS-SWR-0004 - relocate accumulator (per eng. Detail). | A | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const | 2019-09-30 | Kelvin Cook | 2019-09-30 | Kelvin Cook
DWS-01 | DWS-01 | PI05148 | Verified | At Make up Water Treatment area - 10-DWS-SWR-0004 - complete pipe at U/G connection. | A | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const | 2019-09-30 | Kelvin Cook | 2019-09-30 | Kelvin Cook
DWS-01 | DWS-01 | PI05150 | Verified | At Filter Press area - complete all installation. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-13 | Michael Law
DWS-01 | DWS-01 | PI05151 | Verified | At Cooling Tower Chemical Feed area - Add support for flow switch 10-DWS-FSH-0005. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05152 | Verified | At Cooling Tower Chemical Feed area - route SRV-0507 to safe location. | B | P | James Beech | McD | 2019-09-12 | James Beech | Const | 2020-01-07 | Kelvin Cook | 2020-02-27 | Michael Law
DWS-01 | DWS-01 | PI05153 | Verified | At Cooling Tower Chemical Feed area - replace oversized u-bolt. | B | P | James Beech | McD | 2019-09-12 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
DWS-01 | DWS-01 | PI05154 | Verified | At 1A Phosphate Feed Skid - 1A-DWS-H-0006 - ground panel. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05155 | Verified | At 1A Phosphate Feed Skid - 1A-DWS-H-0006 - complete raceway & seal tite. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05156 | Verified | At 1A Phosphate Feed Skid - 1A-DWS-SWR-0006 - mount light & switch. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05157 | Verified | At 1A Phosphate Feed Skid - 1A-DWS-H-0006 - install ground & seal tite. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05158 | Verified | At 1A Phosphate Feed Skid - 1A-DWS-H-0006 - conduit is incomplete. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05159 | Verified | At 1A Phosphate Feed Skid - 1A-DWS-H-0006 - grout all supports. | C | C | Johnny Campbell | McD | 2019-09-12 | Johnny Campbell | Const | 2019-10-10 | Johnny Campbell | 2019-11-20 | Fred Michael
DWS-01 | DWS-01 | PI05160 | Verified | At 1A Phosphate Feed Skid - 1A-DWS-SRV-0607 - vent to safe location. | B | P | Kelvin Cook | McD | 2019-09-12 | Kelvin Cook | Const | 2020-01-07 | Kelvin Cook | 2020-02-27 | Michael Law
DWS-01 | DWS-01 | PI05161 | Verified | At 1A Sample building - 1A-DWS-0039 not installed. | A | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const | 2019-09-30 | Kelvin Cook | 2019-09-30 | Kelvin Cook
DWS-01 | DWS-01 | PI05162 | Verified | At 1A GT Control Package - 1A-DWS-H-0016 - ground panel. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05163 | Verified | At 1A GT Control Package - 1A-DWS-H-0016 - label panel. | C | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
DWS-01 | DWS-01 | PI05164 | Verified | At 1A GT Control Package - 1A-DWS-H-0016 - missing condulet covers. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-10-15 | Fred Michael
DWS-01 | DWS-01 | PI05165 | Verified | At 1A GT Control Package - 1A-DWS-PI-0016 missing plug. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05166 | Verified | At 1A GT Control Package - 1A-DWS-SRV-0016 vent to safe location. | B | P | Kelvin Cook | McD | 2019-09-12 | Kelvin Cook | Const | 2020-01-07 | Kelvin Cook | 2020-02-27 | Michael Law
DWS-01 | DWS-01 | PI05167 | Verified | At 1A GT Control Package - Install proper u-bolts (2). | B | P | James Beech | McD | 2019-09-12 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
DWS-01 | DWS-01 | PI05168 | Verified | At 1A GT PDC - 1A-DWS-SWR-0016 - missing light. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05169 | Verified | At 1B GT Control Package - 1B-DWS-H-0017 - ground panel. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05170 | Verified | At 1B GT Control Package - 1B-DWS-H-0017 - label panel. | C | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
DWS-01 | DWS-01 | PI05171 | Verified | At 1B GT Control Package - 1B-DWS-H-0017 - missing condulet covers. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
DWS-01 | DWS-01 | PI05172 | Verified | At 1B GT Control Package - 1B-DWS-PI-0017 missing plug. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05173 | Verified | At 1B GT Control Package - 1B-DWS-SRV-0017 vent to safe location. | B | P | Kelvin Cook | McD | 2019-09-12 | Kelvin Cook | Const | 2019-10-28 | Kelvin Cook | 2020-01-27 | Michael Law
DWS-01 | DWS-01 | PI05174 | Verified | At 1B GT Control Package - Install proper u-bolts (2). | B | P | James Beech | McD | 2019-09-12 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
DWS-01 | DWS-01 | PI05175 | Verified | At Ammonia Storage - 10-DWS-H-0012 - ground panel. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05176 | Verified | At Ammonia Storage - 10-DWS-H-0012 - label panel. | C | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
DWS-01 | DWS-01 | PI05177 | Verified | At Ammonia Storage - 10-DWS-H-0012 - mount light & switch. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05178 | Verified | At Ammonia Storage - 10-DWS-H-0012 - install raceway & ground. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05179 | Verified | At Ammonia Storage - 10-DWS-H-0012 - ground seal tite for FSH to light. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05180 | Verified | At Ammonia Storage - 10-DWS-SWR-0012 - two u-bolts need replacing. | B | P | James Beech | McD | 2019-09-12 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
DWS-01 | DWS-01 | PI05181 | Verified | At 1B Phospate Feed Skid - 1A-DWS-H-0010 - ground panel. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05182 | Verified | At 1B Phospate Feed Skid - 1A-DWS-H-0010 - label panel. | C | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
DWS-01 | DWS-01 | PI05183 | Verified | At 1B Phospate Feed Skid - 1A-DWS-H-0010 - missing condulet covers. | B | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
DWS-01 | DWS-01 | PI05184 | Verified | At 1B Phospate Feed Skid - 1A-DWS-H-0010 - mount light & switch. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05185 | Verified | At 1B Phospate Feed Skid - 1A-DWS-H-0010 - complete seal tite & ground. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-11-14 | Richard Cruz | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05186 | Verified | At 1B Phospate Feed Skid - 1A-DWS-H-0010 - grout all supports. | C | C | Johnny Campbell | McD | 2019-09-12 | Johnny Campbell | Const | 2019-10-10 | Johnny Campbell | 2019-11-20 | Fred Michael
DWS-01 | DWS-01 | PI05187 | Verified | At 1B Phospate Feed Skid - 1A-DWS-SWR-0010 - route SRV-0407 to safe location. | B | P | James Beech | McD | 2019-09-12 | James Beech | Const | 2020-01-07 | Kelvin Cook | 2020-02-27 | Michael Law
DWS-01 | DWS-01 | PI05188 | Verified | At 1B Sample Bldg. - 1B-DWS-0038 not installed. Need to first valve. | A | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const | 2019-09-30 | Kelvin Cook | 2019-09-30 | Kelvin Cook
DWS-01 | DWS-01 | PI05204 | Verified | 10DWSC0002, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
DWS-01 | DWS-01 | PI05205 | Verified | 10DWSC0003, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05206 | Verified | 10DWSC0004, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05207 | Verified | 10DWSC0007, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
DWS-01 | DWS-01 | PI05208 | Verified | 10DWSC0008, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
DWS-01 | DWS-01 | PI05209 | Verified | 10DWSK0002, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
DWS-01 | DWS-01 | PI05210 | Verified | 10DWSK0003, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
DWS-01 | DWS-01 | PI05211 | Verified | 10DWSK0004, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05212 | Verified | 10DWSK0005, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05213 | Verified | 10DWSK0007, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05214 | Verified | 10DWSK0008, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05215 | Verified | 10DWSK0009, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05216 | Verified | 10DWSK0010, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05217 | Verified | 10DWSK0012, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05218 | Verified | 10DWSK0013, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
DWS-01 | DWS-01 | PI05219 | Verified | 10DWSK0014, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05220 | Verified | 10DWSK0017, Pull Cable | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-09 | Mike Tabbert
DWS-01 | DWS-01 | PI05221 | Verified | 10DWSK0018, Pull Cable | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-09 | Mike Tabbert
DWS-01 | DWS-01 | PI05222 | Verified | 10DWSK0019, Pull Cable | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-09 | Mike Tabbert
DWS-01 | DWS-01 | PI05223 | Verified | 10DWSK0020, Pull Cable | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-09 | Mike Tabbert
DWS-01 | DWS-01 | PI05224 | Verified | 10DWSK0021, Pull Cable | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-09 | Mike Tabbert
DWS-01 | DWS-01 | PI05225 | Verified | 1ADWSK0002, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05226 | Verified | 1ADWSK0004, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05227 | Verified | 1BDWSK0002, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05228 | Verified | 1BDWSK0003, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05229 | Verified | 1BDWSK0004, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05230 | Verified | 1BDWSK0006, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05231 | Verified | 1CDWSK0002, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05232 | Verified | 1CDWSK0003, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05233 | Verified | 10DWSC0001, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05234 | Verified | 10DWSC0002, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05235 | Verified | 10DWSC0003, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05236 | Verified | 10DWSC0004, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05237 | Verified | 10DWSC0005, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05238 | Verified | 10DWSC0006, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05239 | Verified | 10DWSC0007, To and From Termination | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
DWS-01 | DWS-01 | PI05240 | Verified | 10DWSC0008, To and From Termination | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
DWS-01 | DWS-01 | PI05241 | Verified | 10DWSK0001, To and From Termination | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2019-12-04 | Mike Tabbert
DWS-01 | DWS-01 | PI05242 | Verified | 10DWSK0002, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05243 | Verified | 10DWSK0003, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05244 | Verified | 10DWSK0004, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05245 | Verified | 10DWSK0005, To and From Termination | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2019-12-04 | Mike Tabbert
DWS-01 | DWS-01 | PI05246 | Verified | 10DWSK0006, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05247 | Verified | 10DWSK0007, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05248 | Verified | 10DWSK0008, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05249 | Verified | 10DWSK0009, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05250 | Verified | 10DWSK0010, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05251 | Verified | 10DWSK0011, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
DWS-01 | DWS-01 | PI05252 | Verified | 10DWSK0012, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
DWS-01 | DWS-01 | PI05253 | Verified | 10DWSK0013, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05254 | Verified | 10DWSK0014, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05255 | Verified | 10DWSK0015, To and From Termination | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
DWS-01 | DWS-01 | PI05256 | Verified | 10DWSK0017, To and From Termination | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-30 | Mike Tabbert
DWS-01 | DWS-01 | PI05257 | Verified | 10DWSK0018, To and From Termination | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
DWS-01 | DWS-01 | PI05258 | Verified | 10DWSK0019, To and From Termination | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
DWS-01 | DWS-01 | PI05259 | Verified | 10DWSK0020, To and From Termination | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
DWS-01 | DWS-01 | PI05260 | Verified | 10DWSK0021, To and From Termination | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
DWS-01 | DWS-01 | PI05261 | Verified | 1ADWSC0001, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05262 | Verified | 1ADWSC0002, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05263 | Verified | 1ADWSK0001, To and From Termination | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2019-12-04 | Mike Tabbert
DWS-01 | DWS-01 | PI05264 | Verified | 1ADWSK0002, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05265 | Verified | 1ADWSK0003, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05266 | Verified | 1ADWSK0004, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05267 | Verified | 1ADWSK0005, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05268 | Verified | 1ADWSK0006, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05269 | Verified | 1BDWSC0001, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05270 | Verified | 1BDWSC0002, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05271 | Verified | 1BDWSK0001, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05272 | Verified | 1BDWSK0002, To and From Termination | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const |  |  | 2019-12-04 | Mike Tabbert
DWS-01 | DWS-01 | PI05273 | Verified | 1BDWSK0003, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05274 | Verified | 1BDWSK0004, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05275 | Verified | 1BDWSK0005, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
DWS-01 | DWS-01 | PI05276 | Verified | 1BDWSK0006, To and From Termination | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
DWS-01 | DWS-01 | PI05277 | Verified | 1CDWSC0001, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
DWS-01 | DWS-01 | PI05278 | Verified | 1CDWSK0001, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05279 | Verified | 1CDWSK0002, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
DWS-01 | DWS-01 | PI05280 | Verified | 1CDWSK0003, To and From Termination | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const |  |  | 2019-11-23 | Chris Caywood
DWS-01 | DWS-01 | PI05843 | Verified | Cracked pipe at the supply to the Control / Admin. Building. | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-11-19 | James Beech | 2019-12-09 | Alan Joiner
DWS-01 | DWS-01 | PI07244 | Verified | PI (10-DWS-PI-0004?) is full of water, needs plug. Near MWS polymer skid. | A | I | Gonzalo Pena | McD | 2019-09-26 | Gonzalo Pena | Const | 2019-11-16 | James Tanner | 2019-12-09 | Alan Joiner
DWS-01 | DWS-01 | PI09144 | Verified | ISO 1A-DWS-PD-P41-033-01 Copper flange to be replace at UG connection. | A | P | James Beech | McD | 2019-10-07 | James Beech | Const |  |  | 2019-10-19 | Kelvin Cook
DWS-01 | DWS-01 | PI09145 | Verified | ISO 1C-DWS-PD-P41-040-01 Copper flange to be replace at UG connection. | A | P | James Beech | McD | 2019-10-07 | James Beech | Const |  |  | 2019-10-19 | Kelvin Cook
DWS-01 | DWS-01 | PI12625 | Verified | Mount alarm switches at safety showers. | A | I | Gonzalo Pena | McD | 2019-10-29 | Gonzalo Pena | Const | 2019-11-11 | Gonzalo Pena | 2019-12-09 | Alan Joiner
DWS-01 | DWS-01 | PI12626 | Verified | Install relief valve discharge pipe on safety showers. | A | P | James Beech | McD | 2019-10-29 | James Beech | Const | 2019-11-11 | James Beech | 2019-12-09 | Alex Isaac
DWS-01 | DWS-01 | PI13123 | Verified | 10-DWS-PD-P41-0026-01 DWS-SWR-0003 is missing water arrestor. | A | P | James Beech | McD | 2019-11-16 | James Beech | Const | 2019-11-21 | Michael Law | 2019-11-23 | Kelvin Cook
DWS-01 | DWS-01 | PI13124 | Verified | 10-DWS-PD-P41-0072-02 DWS-SWR-0007 is missing water arrestor. | A | P | James Beech | McD | 2019-11-16 | James Beech | Const |  |  | 2019-11-23 | Kelvin Cook
DWS-01 | DWS-01 | PI13125 | Verified | 10-DWS-PD-P41-0073-02 DWS-WES-0008 is missing a water arrestor. | A | P | James Beech | McD | 2019-11-16 | James Beech | Const |  |  | 2019-11-23 | Kelvin Cook
DWS-01 | DWS-01 | PI13142 | Verified | 10DWSK0007 - cable wired wrong - Aqueous Ammonia showers 12 & 13. | A | E | Dustin Futrell | McD | 2019-11-19 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
DWS-01 | DWS-01 | PI13143 | Verified | Change tag on 1B-DWS-H-0100 (from 10-) at the 1B HRSG phosphate skid shower. | C | E | Chris Colvin | McD | 2019-11-19 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-09 | Alan Joiner
DWS-01 | DWS-01 | PI13144 | Verified | Term. Wiring for amber light at the 1B HRSG phosphate skid shower. | A | E | Dustin Futrell | McD | 2019-11-19 | Dustin Futrell | Const | 2019-11-21 | Richard Cruz | 2019-11-22 | Mike Tabbert
DWS-01 | DWS-01 | PI13145 | Verified | Change tag on 1A-DWS-H-0100 (from 10-) at the 1A HRSG phosphate skid shower. | C | E | Chris Colvin | McD | 2019-11-19 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-09 | Alan Joiner
DWS-01 | DWS-01 | PI13146 | Verified | Term. Wiring for amber light at the 1A HRSG phosphate skid shower. | A | E | Dustin Futrell | McD | 2019-11-19 | Dustin Futrell | Const | 2019-11-21 | Dustin Futrell | 2019-11-22 | Mike Tabbert
DWS-01 | DWS-01 | PI13147 | Verified | Need spring nuts at switch at the 1A HRSG phosphate skid shower. | B | E | Dustin Futrell | McD | 2019-11-19 | Dustin Futrell | Const | 2019-11-21 | Dustin Futrell | 2019-11-22 | Mike Tabbert
DWS-01 | DWS-01 | PI13148 | Verified | Condulet cover missing at the 1A HRSG phosphae skid shower. | B | E | Dustin Futrell | McD | 2019-11-19 | Dustin Futrell | Const | 2019-11-21 | Dustin Futrell | 2019-11-22 | Mike Tabbert
DWS-01 | DWS-01 | PI13149 | Verified | Grout supports at the 1A phsophate skid shower. | C | C | Johnny Campbell | McD | 2019-11-19 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2019-12-09 | Alan Joiner
DWS-01 | DWS-01 | PI13150 | Verified | Grout supports at the 1A makeup water shower. | C | C | Johnny Campbell | McD | 2019-11-19 | Johnny Campbell | Const | 2019-12-09 | Jack Fields | 2019-12-13 | Mike Tabbert
DWS-01 | DWS-01 | PI13151 | Verified | Term. Amber light at the cooling tower chem. storage shower. | A | E | Dustin Futrell | McD | 2019-11-19 | Dustin Futrell | Const | 2019-11-21 | Dustin Futrell | 2019-11-22 | Mike Tabbert
DWS-01 | DWS-01 | PI13152 | Verified | Pipe needs support at the makeup water area shower. | A | P | James Beech | McD | 2019-11-19 | James Beech | Const | 2019-11-25 | James Beech | 2019-12-01 | Albert Burge
DWS-01 | DWS-01 | PI13153 | Verified | Wires too short for amber light at the makeup water area shower. | A | E | Dustin Futrell | McD | 2019-11-19 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
DWS-01 | DWS-01 | PI13154 | Verified | Cold galv threads at makeup water 10-DWS-SWR-0004. | C | E | Chris Colvin | McD | 2019-11-19 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-09 | Alan Joiner
DWS-01 | DWS-01 | PI13155 | Verified | Condulet cover missing at 10-DWS-SWR-0015 - batch neut. Area. | B | E | Chris Colvin | McD | 2019-11-19 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-13 | Mike Tabbert
DWS-01 | DWS-01 | PI13156 | Verified | 10-DWS-FSH-0002 not wired - batch neut. (inside WTB). | A | E | Chris Colvin | McD | 2019-11-19 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-14 | Mike Tabbert
DWS-01 | DWS-01 | PI13157 | Verified | Wires too short for amber light at 10-DWS-SWR-0003 in the WTB. | A | E | Chris Colvin | McD | 2019-11-19 | Chris Colvin | Const | 2019-11-23 | Dustin Futrell | 2019-12-14 | Mike Tabbert
DWS-01 | DWS-01 | PI13158 | Verified | Ground flex at 10-DWS-SWR-0002 in the WTB. | A | E | Chris Colvin | McD | 2019-11-19 | Chris Colvin | Const | 2019-11-23 | Dustin Futrell | 2019-12-14 | Mike Tabbert
DWS-01 | DWS-01 | PI13159 | Verified | Complete wiring to 10-DWS-SWR-0002/0003 in the WTB. | A | E | Chris Colvin | McD | 2019-11-19 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-09 | Alan Joiner
DWS-01 | DWS-01 | PI13160 | Verified | Complete all switch & light wiring at 1C-DWS-SWR-0009 at the condensate chem. Feed skid shower. | A | E | Dustin Futrell | McD | 2019-11-19 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
DWS-01 | DWS-01 | PI13161 | Verified | Complete all switch & light wiring at 10-DWS-SWR-00091 at the main PDC. | A | E | Dustin Futrell | McD | 2019-11-19 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
DWS-01 | DWS-01 | PI13162 | Verified | Change tag on 1A-DWS-H-0016 (from 10-) at the 1A GT Control package. | C | E | Chris Colvin | McD | 2019-11-19 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-09 | Alan Joiner
DWS-01 | DWS-01 | PI13163 | Verified | Change tag on 1B-DWS-H-0017 (from 10-) at the 1B GT Control package. | C | E | Chris Colvin | McD | 2019-11-19 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-09 | Alan Joiner
DWS-01 | DWS-01 | PI13164 | Verified | Wire up light in the 1B GT control package. | A | E | Dustin Futrell | McD | 2019-11-19 | Dustin Futrell | Const | 2019-11-21 | Dustin Futrell | 2019-11-22 | Mike Tabbert
DWS-01 | DWS-01 | PI13189 | Verified | Install 10-DWS-FSH-0007. | A | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-09 | James Beech | 2019-12-12 | James Tanner
DWS-01 | DWS-01 | PI13190 | Verified | Install 10-DWS-FSH-0008. | A | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-09 | James Beech | 2019-12-12 | James Tanner
DWS-01 | DWS-01 | PI15898 | Verified | Eye wash in "C" lab - This shower does not meet the ANSI standard for piping to an eyewash station. Per J. Stephens, a 3/8" tubing will not supply enough water to meet the required volume. Potable water outside the westside of the building is copper piped with 1 ½” pipe, reduced to ½" pipe, and then reduced to 3/8" tubing that goes through a heater on the wall to the eyewash station. | C | P | Michael Law | McD | 2020-01-13 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
DWS-01 | DWS-01 | PI15372 | Verified | 10-DWS-PD-P41-0073-01: Install 10-DWS-V-0073. | A | P | James Beech | McD | 2020-01-07 | James Beech | Const |  |  | 2020-01-23 | Kelvin Cook
DWS-01 | DWS-01 | PI16534 | Verified | Remove (temp.) potable water hose at south end of Aqueous Ammonia unloading area. | C | P | James Beech | McD | 2020-02-04 | James Beech | Const | 2020-05-05 | James Beech | 2020-08-06 | Dave Goldak
DWS-01 | DWS-01 | PI17239 | Verified | Complete insulation at 1B-DWS-SWR-0017; 1B GT Control Package Emergency Shower/Eyewash station | C | Q | Sheri Fritz | PCI | 2020-02-28 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-26 | Randy Carpenter
DWS-01 | DWS-01 | PI17240 | Verified | Place 1B-DWS-SWR-0017; 1B GT Control Package Emergency Shower/Eyewash station in-service, currently valved out | B | P | William Mitchell | McD | 2020-02-28 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-26 | John Watts
DWS-01 | DWS-01 | PI17242 | Verified | Complete insulation at 10-DWS-SWR-0012; Aqueous Ammonia Tank and Unloading Pad Emergency Shower/Eyewash station | C | Q | Josh Koerner | PCI | 2020-02-28 | Josh Koerner | Comm | 2020-06-19 | Jason Ezell | 2020-06-19 | Jason Ezell
DWS-01 | DWS-01 | PI17244 | Verified | Complete insulation at 10-DWS-SWR-0013; Aqueous Ammonia Tank and Unloading Pad Emergency Shower/Eyewash station | C | Q | Josh Koerner | PCI | 2020-02-28 | Josh Koerner | Comm | 2020-06-19 | Jason Ezell | 2020-06-19 | Jason Ezell
DWS-01 | DWS-01 | PI17246 | Verified | Complete insulation at 1B-DWS-SWR-0010; 1B Phosphate Feed Skid Emergency Shower/Eyewash station | C | Q | Sheri Fritz | PCI | 2020-02-28 | Sheri Fritz | Comm | 2020-05-26 | Sheri Fritz | 2020-05-26 | Randy Carpenter
DWS-01 | DWS-01 | PI17247 | Verified | Place 1B-DWS-SWR-0010; 1B Phosphate Feed Skid Emergency Shower/Eyewash station in-service | B | P | William Mitchell | McD | 2020-02-28 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-26 | John Watts
DWS-01 | DWS-01 | PI17249 | Verified | Complete complete insulation at 1A-DWS-SWR-0006; 1A Phosphate Feed Skid Emergency Shower/Eyewash station | C | Q | Sheri Fritz | PCI | 2020-02-28 | Sheri Fritz | Comm | 2020-05-26 | Sheri Fritz | 2020-05-26 | Randy Carpenter
DWS-01 | DWS-01 | PI17250 | Verified | Place 1A-DWS-SWR-0006; 1A Phosphate Feed Skid Emergency Shower/Eyewash station in-service, currently valved out | B | P | William Mitchell | McD | 2020-02-28 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-26 | Bernard Stasse
DWS-01 | DWS-01 | PI17252 | Verified | Complete insulation at 1C-DWS-SWR-0009; 1C Condensate Chem Feed Skid Emergency Shower/Eyewash station | C | Q | Josh Koerner | PCI | 2020-02-28 | Josh Koerner | Comm | 2020-06-19 | Jason Ezell | 2020-06-19 | Jason Ezell
DWS-01 | DWS-01 | PI17253 | Verified | Equipment tag missing at 1C-DWS-SWR-0009; 1C Condensate Chem Feed Skid Emergency Shower/Eyewash station | C | P | James Beech | McD | 2020-02-28 | James Beech | Comm | 2020-04-09 | James Beech | 2020-05-26 | Randy Carpenter
DWS-01 | DWS-01 | PI17255 | Verified | Complete insulation at 10-DWS-SWR-0008; Filter Press Area Emergency Shower/Eyewash station | C | Q | Sheri Fritz | PCI | 2020-02-28 | Sheri Fritz | Comm | 2020-05-26 | Sheri Fritz | 2020-05-26 | Randy Carpenter
DWS-01 | DWS-01 | PI17257 | Verified | Complete insulation at 10-DWS-SWR-0007; Filter Press Area Emergency Shower/Eyewash station | C | Q | Sheri Fritz | PCI | 2020-02-28 | Sheri Fritz | Comm | 2020-05-26 | Sheri Fritz | 2020-05-26 | Randy Carpenter
DWS-01 | DWS-01 | PI17259 | Verified | Complete insulation at 10-DWS-SWR-0005; Cooling Tower Chemical Storage Area Emergency Shower/Eyewash station | C | Q | Sheri Fritz | PCI | 2020-02-28 | Sheri Fritz | Comm | 2020-05-26 | Satyam Gajjar | 2020-05-26 | Randy Carpenter
DWS-01 | DWS-01 | PI17260 | Verified | Loose condolet cover on power cable to OFF / ON Switch at 10-DWS-SWR-0005; Cooling Tower Chemical Storage Area Emergency Shower/Eyewash station | C | E | Chris Colvin | McD | 2020-02-28 | Chris Colvin | Comm | 2020-04-16 | Matt Gilmore | 2020-05-26 | Randy Carpenter
DWS-01 | DWS-01 | PI17261 | Verified | Remove temporary drain hose from 10-DWS-SWR-0005; Cooling Tower Chemical Storage Area Emergency Shower/Eyewash station | C | P | William Mitchell | McD | 2020-02-28 | William Mitchell | Comm | 2020-04-14 | William Mitchell | 2020-05-26 | Randy Carpenter
DWS-01 | DWS-01 | PI17262 | Verified | Place 10-DWS-SWR-0005; Cooling Tower Chemical Storage Area Emergency Shower/Eyewash station in-service | B | P | William Mitchell | McD | 2020-02-28 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-26 | Bernard Stasse
DWS-01 | DWS-01 | PI17264 | Verified | Complete insulation at 10-DWS-SWR-0004; Makeup Water Treatment Area Emergency Shower/Eyewash station | C | Q | Josh Koerner | PCI | 2020-02-28 | Josh Koerner | Comm | 2020-06-19 | Jason Ezell | 2020-06-19 | Jason Ezell
DWS-01 | DWS-01 | PI17265 | Verified | Place 10-DWS-SWR-0004; Makeup Water Treatment Area Emergency Shower/Eyewash station in-service | B | P | William Mitchell | McD | 2020-02-28 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-26 | Bernard Stasse
DWS-01 | DWS-01 | PI17267 | Verified | Complete insulation at 10-DWS-SWR-0003; Water Treatment Building Chemical Storage Area Emergency Shower/Eyewash station | C | Q | Josh Koerner | PCI | 2020-02-28 | Josh Koerner | Comm | 2020-06-19 | Jason Ezell | 2020-06-19 | Jason Ezell
DWS-01 | DWS-01 | PI17268 | Verified | Place 10-DWS-SWR-0003; Water Treatment Building Chemical Storage Area Emergency Shower/Eyewash station in-service | B | P | William Mitchell | McD | 2020-02-28 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-26 | Bernard Stasse
DWS-01 | DWS-01 | PI17270 | Verified | Complete insulation at 10-DWS-SWR-0002; Water Treatment Building Equipment Area Emergency Shower/Eyewash station | C | Q | Josh Koerner | PCI | 2020-02-28 | Josh Koerner | Comm | 2020-06-19 | Jason Ezell | 2020-06-19 | Jason Ezell
DWS-01 | DWS-01 | PI17271 | Verified | Place 10-DWS-SWR-0002; Water Treatment Building Equipment Area Emergency Shower/Eyewash station in-service | B | P | William Mitchell | McD | 2020-02-28 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-26 | Bernard Stasse
DWS-01 | DWS-01 | PI17273 | Verified | Complete insulation at 10-DWS-SWR-0015; Batch Neutralization Area Emergency Shower/Eyewash station | C | Q | Sheri Fritz | PCI | 2020-02-28 | Sheri Fritz | Comm | 2020-05-26 | Sheri Fritz | 2020-05-26 | Randy Carpenter
DWS-01 | DWS-01 | PI17274 | Verified | Place 10-DWS-SWR-0015; Batch Neutralization Area Emergency Shower/Eyewash station in-service | B | P | William Mitchell | McD | 2020-02-28 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-03-31 | Randy Carpenter
DWS-01 | DWS-01 | PI17276 | Verified | Complete insulation at 1A-DWS-SWR-0016; 1A GT Control Package Emergency Shower/Eyewash station | C | Q | Sheri Fritz | PCI | 2020-02-28 | Sheri Fritz | Comm | 2020-05-26 | Sheri Fritz | 2020-05-26 | Randy Carpenter
DWS-01 | DWS-01 | PI18126 | Verified | All safety showers leak at the bottom. | C | P | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-14 | William Mitchell | 2020-04-30 | John Watts
ESE-01 | ESE-01 | PI01543 | Verified | Seal conduits in 10-NJS-DSW-0002 at control bldg. | A | E | Luis Cantu | McD | 2019-06-22 | Luis Cantu | Const | 2019-06-24 | Luis Cantu | 2019-06-26 | Logan Holland
ESE-01 | ESE-01 | PI01544 | Verified | Clean out 10-NJS-DSW-0002 at control bldg. | A | E | Luis Cantu | McD | 2019-06-22 | Luis Cantu | Const | 2019-06-24 | Luis Cantu | 2019-06-26 | Logan Holland
ESE-01 | ESE-01 | PI01545 | Verified | Attach micarta board in 10-NJS-DSW-0002 at control bldg. | A | E | Luis Cantu | McD | 2019-06-22 | Luis Cantu | Const | 2019-06-24 | Luis Cantu | 2019-06-26 | Logan Holland
ESE-01 | ESE-01 | PI01546 | Verified | Need blank in 10-NJS-PNL-0002 in the control bldg. | B | E | Dustin Futrell | McD | 2019-06-22 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-09-26 | Logan Holland
ESE-01 | ESE-01 | PI01687 | Verified | Pull out temp power out of 10-ESE-FM-0001 | B | E | Logan Holland | McD | 2019-06-28 | Logan Holland | Comm |  |  | 2019-10-28 | Logan Holland
ESE-01 | ESE-01 | PI01688 | Verified | Seal conduit penetrations underneath 10-ESE-XFM-0001 | C | E | Jonathan Donham | McD | 2019-06-28 | Jonathan Donham | Const | 2020-03-10 | Jonathan Donham | 2020-04-21 | Michael Law
ESE-01 | ESE-01 | PI01689 | Verified | Torque and torque mark cables 10NSJL0010A-1G on MCC end | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-15 | Fred Michael
ESE-01 | ESE-01 | PI01690 | Verified | Torque and torque mark cables 10NSJL0011A-1G on MCC end | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-15 | Fred Michael
ESE-01 | ESE-01 | PI01691 | Verified | Terminate Cooling Tower cables 10NJSL0009A-9G and install terminal block | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-19 | Logan Holland
ESE-01 | ESE-01 | PI01692 | Verified | Torque main feeder cables going into 1A-NJS-PNL-0001 | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-19 | Logan Holland
ESE-01 | ESE-01 | PI01693 | Verified | Term cables, firestop penetrations going into 1B-NJS-PNL-0001 | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-19 | Logan Holland
ESE-01 | ESE-01 | PI01694 | Verified | Ground the grounding bushing in Unit B | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-15 | Fred Michael
ESE-01 | ESE-01 | PI01695 | Verified | Ground the grounding bushing in Unit A | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-15 | Fred Michael
ESE-01 | ESE-01 | PI01696 | Verified | Ground the conduit underneath the Cooling Tower PDC | B | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-15 | Fred Michael
ESE-01 | ESE-01 | PI01697 | Verified | Install Edge guards on the cable tray underneath 10-NJS-PNL-0003 | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-19 | Shannon Scott
ESE-01 | ESE-01 | PI01698 | Verified | Cut excess tirewrap holding cables underneath Cooler Tower PDC | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-15 | Fred Michael
ESE-01 | ESE-01 | PI01699 | Verified | 10-NJS-PNL-0003 is on temp power | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-15 | Fred Michael
ESE-01 | ESE-01 | PI01700 | Verified | Finish conduit to 10-NJS-PNL-0007 | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01701 | Verified | Terminate and tail in cable 10NJSK0015 | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-15 | Fred Michael
ESE-01 | ESE-01 | PI01702 | Verified | Label and ground 10-NJS-PNL-0007 | B | E | Dustin Futrell | McD | 2019-06-28 | Dustin Futrell | Const | 2019-07-25 | Ken Mundy | 2019-08-16 | Logan Holland
ESE-01 | ESE-01 | PI01703 | Verified | 10ESEK0001, Pull cable to Lighting Contactor 10-ESE-CNT-0001 | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01704 | Verified | 10ESEK0002, Pull Cable to Photo Cell 10-ESE-PE-0001 | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01705 | Verified | 10NJSK0015Pull Cable , Feeder to 10-NJS-PNL-0007 Located at Chem Feed. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01706 | Verified | 10NJSL0009A, Pull Cable to 10-NJS-JB-0003 located at Cooling Tower PDC. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01707 | Verified | 10NJSL0009B, Pull Cable to 10-NJS-JB-0003 located at Cooling Tower PDC. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01708 | Verified | 10NJSL0009C, Pull Cable to 10-NJS-JB-0003 located at Cooling Tower PDC. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01709 | Verified | 10NJSL0009G, Pull Cable to 10-NJS-JB-0003 located at Cooling Tower PDC. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01710 | Verified | 10NJSL0010A, Pull Cable to 1A-NJS-PNL-0001 located at HRSG 1A PDC | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01711 | Verified | 10NJSL0010B, Pull Cable to 1A-NJS-PNL-0001 located at HRSG 1A PDC | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01712 | Verified | 10NJSL0010C, Pull Cable to 1A-NJS-PNL-0001 located at HRSG 1A PDC | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01713 | Verified | 10NJSL0010G, Pull Cable to 1A-NJS-PNL-0001 located at HRSG 1A PDC | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01714 | Verified | 10NJSL0011A, Pull Cable to 1B-NJS-PNL-0001 located at HRSG 1B PDC | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01715 | Verified | 10NJSL0011B, Pull Cable to 1B-NJS-PNL-0001 located at HRSG 1B PDC | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01716 | Verified | 10NJSL0011C, Pull Cable to 1B-NJS-PNL-0001 located at HRSG 1B PDC | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01717 | Verified | 10NJSL0011G, Pull Cable to 1B-NJS-PNL-0001 located at HRSG 1B PDC | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01718 | Verified | 10NJSL0013A, Pull Cable 10-NJS-JB-0003 to 10-NJS-PNL-0003 located Cooling Tower PDC. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01719 | Verified | 10NJSL0013B, Pull Cable 10-NJS-JB-0003 to 10-NJS-PNL-0003 located Cooling Tower PDC. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01720 | Verified | 10NJSL0013C, Pull Cable 10-NJS-JB-0003 to 10-NJS-PNL-0003 located Cooling Tower PDC. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01721 | Verified | 10NJSL0013G, Pull Cable 10-NJS-JB-0003 to 10-NJS-PNL-0003 located Cooling Tower PDC. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01722 | Verified | 10ESEK0001, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01723 | Verified | 10ESEK0002, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01724 | Verified | 10NJSK0015, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
ESE-01 | ESE-01 | PI01725 | Verified | 10NJSL0009A, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01726 | Verified | 10NJSL0009B, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01727 | Verified | 10NJSL0009C, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01728 | Verified | 10NJSL0009G, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01729 | Verified | 10NJSL0010A, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01730 | Verified | 10NJSL0010B, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01731 | Verified | 10NJSL0010C, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01732 | Verified | 10NJSL0010G, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01733 | Verified | 10NJSL0011A, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01734 | Verified | 10NJSL0011B, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01735 | Verified | 10NJSL0011C, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01736 | Verified | 10NJSL0011G, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01737 | Verified | 10NJSL0013A, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01738 | Verified | 10NJSL0013B, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01739 | Verified | 10NJSL0013C, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01740 | Verified | 10NJSL0013G, Terminate Cable Both Ends. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01741 | Verified | Install Lighting Contactor 10-ESE-CNT-0001 | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01742 | Verified | Install Lighting Photo Cell 10-ESE-PE-0001 | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01743 | Verified | Install Panel 10-NJS-PNL-0007, located at Chem Feed | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01744 | Verified | Complete any required conduit installation for above cable. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01745 | Verified | Complete any required cable tray grounding for this system. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Luis Cantu | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01746 | Verified | Complete any required sealtight external grounds for this system. | B | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
ESE-01 | ESE-01 | PI01747 | Verified | Confirm all cables have correct cable and wire markers. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01748 | Verified | Confirm all required cable connections have been torqued and torque record has been completed. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-02 | Tommy Vuong | 2019-07-02 | Mike Tabbert
ESE-01 | ESE-01 | PI01749 | Verified | Confirm all Panels, J-Boxes and General Area has been cleaned and excess material has been stored away. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
ESE-01 | ESE-01 | PI01750 | Verified | Confirm all Completion Paperwork is turned in. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-10 | Luis Cantu | 2019-07-10 | Mike Tabbert
ESE-01 | ESE-01 | PI12663 | Verified | Update Panel Schedule at 1A-ESE-PNL-0001; 208/120V, HRSG 1A PDC | C | E | Jonathan Donham | McD | 2019-11-01 | Jonathan Donham | Comm |  |  | 2020-01-29 | Fred Michael
ESE-01 | ESE-01 | PI12664 | Verified | Update Panel Schedule at 1A-NJS-PNL-0001; 480V, HRSG 1A PDC | C | E | Jonathan Donham | McD | 2019-11-01 | Jonathan Donham | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Randy Carpenter
ESE-01 | ESE-01 | PI12665 | Verified | Missing panel bolts at 1A-NJS-PNL-0001; 480V, HRSG 1A PDC | C | E | Chris Colvin | McD | 2019-11-01 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
ESE-01 | ESE-01 | PI12666 | Verified | Remove unused threaded fitting and plug hold at bottom right side of 1A-NJS-PNL-0001; 480V, HRSG 1A PDC | C | E | Chris Colvin | McD | 2019-11-01 | Chris Colvin | Comm | 2020-04-06 | Chris Colvin | 2021-01-05 | Keith Pollock
ESE-01 | ESE-01 | PI12667 | Verified | Update Panel Schedule at 1B-ESE-PNL-0001; 208/120V, HRSG 1B PDC | C | E | Jonathan Donham | McD | 2019-11-01 | Jonathan Donham | Comm |  |  | 2020-01-29 | Fred Michael
ESE-01 | ESE-01 | PI12668 | Verified | Seal floor penetration at 1B-NJS-PNL-0001; 480V HRSG 1B PDC | C | E | Chris Colvin | McD | 2019-11-01 | Chris Colvin | Comm | 2020-06-17 | Chris Colvin | 2021-01-25 | Dave Goldak
ESE-01 | ESE-01 | PI12669 | Verified | Update Panel Schedule at 1B-NJS-PNL-0001; 480V HRSG 1B PDC | C | E | Jonathan Donham | McD | 2019-11-01 | Jonathan Donham | Comm |  |  | 2020-01-29 | Fred Michael
ESE-01 | ESE-01 | PI12670 | Verified | Update Panel Schedule at 10-ESE-PNL-0001; 208/120V, Main PDC | C | E | Jonathan Donham | McD | 2019-11-01 | Jonathan Donham | Comm |  |  | 2020-01-29 | Fred Michael
ESE-01 | ESE-01 | PI12671 | Verified | Update Panel Schedule at 10-NJS-PNL-0001; 480V, Main PDC | C | E | Jonathan Donham | McD | 2019-11-01 | Jonathan Donham | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Randy Carpenter
ESE-01 | ESE-01 | PI12672 | Verified | Seal floor penetration at 10-NJS-PNL-0001; 480V, Main PDC | C | E | Chris Colvin | McD | 2019-11-01 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2020-08-17 | Dave Goldak
ESE-01 | ESE-01 | PI12673 | Verified | Missing panel bolts at 10-NJS-PNL-0001; 480V, Main PDC | C | E | Chris Colvin | McD | 2019-11-01 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
ESE-01 | ESE-01 | PI12674 | Verified | Tighten panel bolts at 10-ESE-PNL-0003; 208/120V, Cooling Tower PDC | C | E | Chris Colvin | McD | 2019-11-01 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
ESE-01 | ESE-01 | PI12675 | Verified | Update Panel Schedule at 10-ESE-PNL-0003; 208/120V, Cooling Tower PDC | C | E | Jonathan Donham | McD | 2019-11-01 | Jonathan Donham | Comm |  |  | 2020-01-29 | Fred Michael
ESE-01 | ESE-01 | PI12676 | Verified | Missing panel bolts at 10-NJS-PNL-0003; 480V, Main PDC | C | E | Chris Colvin | McD | 2019-11-01 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
ESE-01 | ESE-01 | PI12677 | Verified | Update Panel Schecule at 10-NJS-PNL-0003; 480V, Main PDC | C | E | Chris Colvin | McD | 2019-11-01 | Chris Colvin | Comm |  |  | 2020-01-29 | Fred Michael
ESE-01 | ESE-01 | PI12678 | Verified | Seal floor penetration at 10-NJS-PNL-0003; 480V, Main PDC | C | E | Chris Colvin | McD | 2019-11-01 | Chris Colvin | Comm | 2020-05-04 | Matt Gilmore | 2021-01-25 | Dave Goldak
ESE-01 | ESE-01 | PI12679 | Verified | Missing panel bolts at 10-ESE-PNL-0002; 208/120V, Control Building | C | E | Chris Colvin | McD | 2019-11-01 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
ESE-01 | ESE-01 | PI12680 | Verified | Update Panel Schedule at 10-ESE-PNL-0002; 208/120V, Control Building | C | E | Jonathan Donham | McD | 2019-11-01 | Jonathan Donham | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Fred Michael
ESE-01 | ESE-01 | PI12681 | Verified | Update Panel Schedule at 10-NJS-PNL-0002; 480V, Control Building | C | E | Jonathan Donham | McD | 2019-11-01 | Jonathan Donham | Comm |  |  | 2020-01-29 | Fred Michael
ESF-01 | ESF-01 | PI00245 | Verified | 10-ESF-SWB-0001, Need lug kit to facilitate two 500 MCM per phase | A | E | Shannon Savoy | McD | 2019-03-01 | Shannon Savoy | Const | 2019-03-04 | Mike Tabbert | 2019-03-04 | Mike Tabbert
ESF-01 | ESF-01 | PI00246 | Verified | Install and terminate 10-ESFK0004 at cooling tower PDC | A | E | Luis Cantu | McD | 2019-03-01 | Luis Cantu | Const | 2019-06-21 | Luis Cantu | 2019-06-27 | Logan Holland
ESF-01 | ESF-01 | PI00247 | Verified | Install J-Box 10-ESF-JB-0005B at Cooling Tower PDC | A | E | Luis Cantu | McD | 2019-03-01 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-06-14 | Mike Tabbert
ESF-01 | ESF-01 | PI00248 | Verified | Install Cables 10ESFL0001A1, A2, B1, B2, C1, C2, G1, G2, N1, N2 at Control Building | A | E | Shannon Savoy | McD | 2019-03-01 | Shannon Savoy | Const | 2019-03-28 | Mike Tabbert | 2019-03-28 | Mike Tabbert
ESF-01 | ESF-01 | PI00249 | Verified | Install Cables 10ESFL0002A1, B1, C1, G1, N1 at Cooling Tower PDC. | A | E | Luis Cantu | McD | 2019-03-01 | Luis Cantu | Const | 2019-06-27 | Logan Holland | 2019-06-27 | Logan Holland
ESF-01 | ESF-01 | PI00250 | Verified | Install and Terminate Cables 10ESFL0003A1, 3A2, 3B1, 3B2, 3C1, 3C2, 3G1, 3G2, 3N1, 3N2 | A | E | Shannon Savoy | McD | 2019-03-01 | Shannon Savoy | Const | 2019-03-04 | Mike Tabbert | 2019-03-04 | Mike Tabbert
ESF-01 | ESF-01 | PI00251 | Verified | Install and Termnate Cables 1AESFK0002, 1AESFL000A1, B1, C1, G1, N1 | A | E | Shannon Savoy | McD | 2019-03-01 | Shannon Savoy | Const | 2019-03-04 | Mike Tabbert | 2019-03-04 | Mike Tabbert
ESF-01 | ESF-01 | PI00252 | Verified | Install and Terminate Cables 1BESFK0002, 1BESFL0001A1, B1, C1, G1, N1 | A | E | Shannon Savoy | McD | 2019-03-01 | Shannon Savoy | Const | 2019-03-04 | Mike Tabbert | 2019-03-04 | Mike Tabbert
ESF-01 | ESF-01 | PI00268 | Verified | Seal all cable penetrations. | C | E | Jonathan Donham | McD | 2019-03-04 | Jonathan Donham | Const | 2020-03-31 | Jonathan Donham | 2020-04-21 | Michael Law
ESF-01 | ESF-01 | PI00269 | Verified | Ground cable trays at Main PDC, 1A HRSG PDC and 1B HRSG PDC. | A | E | Shannon Savoy | McD | 2019-03-04 | Shannon Savoy | Const | 2019-03-08 | Shannon Savoy | 2019-03-11 | Mike Tabbert
ESF-01 | ESF-01 | PI00270 | Verified | Ground all junction boxes for subsystem at Main PDC, 1A HRSG PDC and 1B HRSG PDC./ | A | E | Shannon Savoy | McD | 2019-03-04 | Shannon Savoy | Const | 2019-03-08 | Shannon Savoy | 2019-03-11 | Mike Tabbert
ESF-01 | ESF-01 | PI00271 | Verified | Ground conduit bushings under main PDC at 10-ESF-JB-0004 & 5A. | A | E | Shannon Savoy | McD | 2019-03-04 | Shannon Savoy | Const | 2019-03-08 | Shannon Savoy | 2019-03-11 | Mike Tabbert
ESF-01 | ESF-01 | PI00272 | Verified | Touch up supports (paint) for junction boxes under main PDC. | C | E | Luis Cantu | McD | 2019-03-04 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-06-21 | Mike Tabbert
ESF-01 | ESF-01 | PI00273 | Verified | Remove all duct tabe for cable trays at junction boxes under main PDC. | C | E | Luis Cantu | McD | 2019-03-04 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-06-21 | Mike Tabbert
ESF-01 | ESF-01 | PI00274 | Verified | Condulet cover missing under the 1B HRSG PDC. | B | E | Luis Cantu | McD | 2019-03-04 | Luis Cantu | Const | 2019-06-19 | Luis Cantu | 2019-06-21 | Mike Tabbert
ESF-01 | ESF-01 | PI00275 | Verified | Grout the supports for the junction boxes under main PDC. | C | C | Jessie Pipes | McD | 2019-03-04 | Jessie Pipes | Const | 2019-04-03 | Jessie Pipes | 2019-05-01 | Neil Simon
ESF-01 | ESF-01 | PI00281 | Verified | Insulate the neutral bus in 10-ESF-DSW-0004 at the control building. | A | E | Shannon Savoy | McD | 2019-03-28 | Shannon Savoy | Const | 2019-03-29 | Shannon Savoy | 2019-03-29 | Mike Tabbert
ESF-01 | ESF-01 | PI00282 | Verified | Submit outstanding Construction Completion Forms related to the Cooling Tower that are turnover exceptions. | B | E | Luis Cantu | McD | 2019-03-28 | Luis Cantu | Const | 2019-07-26 | Ed Gober | 2019-07-26 | Ed Gober
ESF-01 | ESF-01 | PI00283 | Verified | Submit all outstanding Construction Completion Forms (excluding exceptions). | A | E | Shannon Savoy | McD | 2019-03-28 | Shannon Savoy | Const | 2019-04-01 | Ed Gober | 2019-04-01 | Ed Gober
ESF-01 | ESF-01 | PI02791 | Verified | Submit Torque sheets for Cables 10EFSL0002A1, B1, C1, N1. | B | E | Fred Michael | McD | 2019-07-25 | Fred Michael | Const | 2019-07-30 | Fred Michael | 2019-08-09 | Ed Gober
ESF-01 | ESF-01 | PI09439 | Verified | 1B-ESF-PNL-0001 to complete bolt up of panel - need to order bolts | C | E | Mike Tabbert | McD | 2019-10-11 | Mike Tabbert | Comm |  |  | 2019-12-21 | Mike Tabbert
ESF-01 | ESF-01 | PI09440 | Verified | 10-ESF-PNL-0001 to complete bolt up of panel - need to order bolts | C | E | Mike Tabbert | McD | 2019-10-11 | Mike Tabbert | Comm |  |  | 2019-12-21 | Mike Tabbert
ESF-01 | ESF-01 | PI09441 | Verified | 1A-ESF-PNL-0001 to complete bolt up of panel - need to order bolts | C | E | Mike Tabbert | McD | 2019-10-11 | Mike Tabbert | Comm |  |  | 2019-12-21 | Mike Tabbert
ESF-01 | ESF-01 | PI09442 | Verified | 10-ESF-PNL-0004 panel cover to put back on - need to order bolts | C | E | Chris Boudreaux | McD | 2019-10-11 | Chris Boudreaux | Comm | 2019-12-23 | Mike Tabbert | 2020-01-13 | Fred Michael
ESF-01 | ESF-01 | PI09443 | Verified | 10-ESF-PNL-0001 install grounding on flex | C | E | Chris Colvin | McD | 2019-10-11 | Chris Colvin | Comm |  |  | 2019-12-21 | Mike Tabbert
ESF-01 | ESF-01 | PI09444 | Verified | All Panel boards - place the latest panel schedule inside panel | C | E | Mike Tabbert | McD | 2019-10-11 | Mike Tabbert | Comm |  |  | 2019-12-21 | Mike Tabbert
ESG-01 | ESG-01 | PI00006 | Verified | 10-ESG-JB-0004B Install | A | E | Luis Cantu | McD | 2019-01-15 | Luis Cantu | Const | 2019-06-19 | Luis Cantu | 2019-06-28 | Mike Tabbert
ESG-01 | ESG-01 | PI00007 | Verified | 10-ESG-JB-0004B, Install Cables, 10ESGL0009N, 9P, 10N, 10P | A | E | Luis Cantu | McD | 2019-01-15 | Luis Cantu | Const | 2019-06-19 | Luis Cantu | 2019-06-28 | Mike Tabbert
ESG-01 | ESG-01 | PI00008 | Verified | 10-NJS-MCC-0004B / 10-ESG-CHGR-0001B, Install Grounding Cables, Torque Power Cables | A | E | Phil Work | McD | 2019-01-15 | Phil Work | Const | 2019-01-29 | Phil Work | 2019-02-05 | Mike Tabbert
ESG-01 | ESG-01 | PI00135 | Verified | Missing arc flash labels on all charger compartments (A & B). | B | E | Michael Law | McD | 2019-01-28 | Michael Law | Const | 2019-06-13 | Mike Tabbert | 2019-06-13 | Mike Tabbert
ESG-01 | ESG-01 | PI00136 | Verified | Seal all penetrations. | B | E | Logan Holland | McD | 2019-01-28 | Logan Holland | Const | 2019-09-05 | Logan Holland | 2019-09-05 | Randy Carpenter
ESG-01 | ESG-01 | PI00137 | Verified | Install jumpers in 10-ESG-SWB-0001; TB2-6 & 9. | B | E | Phil Work | McD | 2019-01-28 | Phil Work | Const | 2019-02-08 | Dan Dula | 2019-02-11 | Mike Tabbert
ESG-01 | ESG-01 | PI00180 | Verified | Complete CCFs for 10-ESG-JB-004B and associated cables, and 10-ESG-PNL-0004 and associated cables. | B | E | Dustin Futrell | McD | 2019-02-11 | Dustin Futrell | Const | 2019-07-30 | Luis Cantu | 2019-08-09 | Ed Gober
ESG-01 | ESG-01 | PI04782 | Verified | Procure and install a RSA operator on the 125VDC main breaker to reduce arc flash exposure. Entergy to confirm who will install | C | E | Mike Tabbert | ENT | 2019-09-05 | Mike Tabbert | Comm | 2020-02-12 | Mike Tabbert | 2020-02-12 | Randy Carpenter
ESG-01 | ESG-01 | PI04783 | Verified | Current cable lists not matching.. GSN = 30, at Consturction handover to Commissioning = 36, in Co-Console = 42. To determine the correct number of cables for this subsystem - as of 06-Sep no of cable are matching at all list including GSN at 42 | C | E | Randy Carpenter | McD | 2019-09-05 | Randy Carpenter | Comm | 2019-09-06 | Eric Policarpio | 2019-09-25 | Eric Policarpio
ESG-01 | ESG-01 | PI18132 | Verified | Undervoltage alarm on 125VDC Essential Power bus in the Main PDC. | C | E | Jonathan Donham | McD | 2020-03-20 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2021-04-26 | Keith Pollock
ESH-01 | ESH-01 | PI13417 | Verified | 1B-ESH-PNL-0001 - missing panel cover slide plate (at Tomco skid).- NEED TO ORDER - F. Michael1-Dec | C | E | Mike Tabbert | McD | 2019-11-23 | Mike Tabbert | Const |  |  | 2019-12-17 | John Sullivan
ESH-01 | ESH-01 | PI13418 | Verified | 1B-ESH-PNL-0001 - panel missing screws (at Tomco skid). | B | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const |  |  | 2019-11-27 | Fred Michael
ESH-01 | ESH-01 | PI13419 | Verified | 1C-ESH-PNL-0002 - needs label (at air comp.) | C | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const |  |  | 2019-11-27 | Fred Michael
ESH-01 | ESH-01 | PI13420 | Verified | 1C-ESH-PNL-0002 - needs ground (at air comp.) | A | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const | 2019-11-27 | Brad Stanford | 2019-12-01 | Fred Michael
ESH-01 | ESH-01 | PI13421 | Verified | 1C-ESH-XFM-0002 - needs label (at air comp.) | C | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const |  |  | 2019-11-27 | Fred Michael
ESH-01 | ESH-01 | PI13422 | Verified | 1C-ESH-XFM-0002 - clean transformer. | C | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const |  |  | 2019-11-27 | Fred Michael
ESH-01 | ESH-01 | PI13423 | Verified | 1C-ESH-XFM-0001 - needs label (STG bldg. west side) | C | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const |  |  | 2019-11-27 | Fred Michael
ESH-01 | ESH-01 | PI13424 | Verified | 10-ESH-PNL-0004 - panel missing screws ( cooling tower PDC). | B | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const | 2019-11-27 | Brad Stanford | 2019-12-01 | Fred Michael
ESH-01 | ESH-01 | PI13425 | Verified | 10-ESH-PNL-0004 - needs ground ( cooling tower PDC). | A | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const | 2019-11-27 | Brad Stanford | 2019-11-27 | Fred Michael
ESH-01 | ESH-01 | PI13426 | Verified | 1A-ESH-PNL-0003, 0004, 0005 - need grounds (1A HRSG PDC). | A | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const | 2019-11-26 | Brad Stanford | 2019-12-01 | Fred Michael
ESH-01 | ESH-01 | PI13427 | Verified | 1A-ESH-PNL-0004 - panel missing screws (1A HRSG PDC). | B | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const | 2019-11-27 | Brad Stanford | 2019-12-01 | Fred Michael
ESH-01 | ESH-01 | PI13428 | Verified | 1A-ESH-PNL-0002 - move ground to panel (under duct burner platform). | A | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const | 2019-11-26 | Brad Stanford | 2019-12-01 | Fred Michael
ESH-01 | ESH-01 | PI13429 | Verified | 1A-ESH-PNL-0002 - grout (under duct burner platform). | C | C | Johnny Campbell | McD | 2019-11-23 | Johnny Campbell | Const |  |  | 2019-12-01 | Fred Michael
ESH-01 | ESH-01 | PI13430 | Verified | 1A-ESH-XFM-0002 - needs label (under duct burner platform). | C | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const |  |  | 2019-11-27 | Fred Michael
ESH-01 | ESH-01 | PI13431 | Verified | 1B-ESH-PNL-0002 - needs ground (under duct burner platform). | A | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const | 2019-11-26 | Brad Stanford | 2019-12-01 | Fred Michael
ESH-01 | ESH-01 | PI13432 | Verified | 1B-ESH-XFM-0002 - needs label (under duct burner platform). | C | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const |  |  | 2019-11-27 | Fred Michael
ESH-01 | ESH-01 | PI13433 | Verified | 1B-ESH-PNL-0003, 0004, 0005 - need grounds (1B HRSG PDC). | A | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const | 2019-11-26 | Brad Stanford | 2019-12-01 | Fred Michael
ESH-01 | ESH-01 | PI13434 | Verified | 1B-ESH-PNL-0004 - panel missing screws (1B HRSG PDC). | B | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const | 2019-11-27 | Brad Stanford | 2019-12-01 | Fred Michael
ESH-01 | ESH-01 | PI13435 | Verified | 10-ESH-PNL-0007 - panel door bottom clamp missing part (raw water). | B | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const |  |  | 2019-12-01 | Fred Michael
ESH-01 | ESH-01 | PI13436 | Verified | 10-ESH-XFM-0007 - needs label (raw water). | C | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const |  |  | 2019-11-27 | Fred Michael
ESH-01 | ESH-01 | PI13437 | Verified | 10-ESH-XFM-0007 - missing screws (raw water). | B | E | Dustin Futrell | McD | 2019-11-23 | Dustin Futrell | Const |  |  | 2019-11-27 | Fred Michael
ESH-01 | ESH-01 | PI15252 | Verified | Need laminated waterproof panel schedule at 1A-ESH-PNL-0001; 208/120V, Service CTG A, located at ground level SW side, near CO2 Tank | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15253 | Verified | Need touch up paint at 1A-ESH-PNL-0001; 208/120V, Service CTG A, located at ground level SW side, near CO2 Tank | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
ESH-01 | ESH-01 | PI15254 | Verified | Clean up interior of 1A-ESH-PNL-0001; 208/120V, Service CTG A, located at ground level SW side, near CO2 Tank | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
ESH-01 | ESH-01 | PI15255 | Verified | Need touch up paint at 1A-ESH-XFM-0001; 208/120V, Service CTG A, located at ground level SW side, near CO2 Tank | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
ESH-01 | ESH-01 | PI15256 | Verified | Missing cover bolts at 1A-ESH-XFM-0001; 208/120V, Service CTG A, located at ground level SW side, near CO2 Tank | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
ESH-01 | ESH-01 | PI15257 | Verified | Ground connection needs touch up paint at 1A-ESH-PNL-0001; 208/120V, Service CTG A, located at ground level SW side, near CO2 Tank | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
ESH-01 | ESH-01 | PI15258 | Verified | Need tie wrap on ground connection at 1A-ESH-PNL-0001; 208/120V, Service CTG A, located at ground level SW side, near CO2 Tank | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-08-14 | Dave Goldak
ESH-01 | ESH-01 | PI15259 | Verified | Condolet cover is bent at back side of 1A-ESH-PNL-0001; 208/120V, Service CTG A, located at ground level SW side, near CO2 Tank | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-13 | Fred Michael
ESH-01 | ESH-01 | PI15260 | Verified | Need laminated waterproof panel schedule at 1A-ESH-PNL-0002; 208/120V, Service HRSG 1A Top PNL, located at ground level, E side, near HRSG stairs | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15261 | Verified | Need touch up paint at 1A-ESH-PNL-0002; 208/120V, Service HRSG 1A Top PNL, located at ground level E side, near HRSG stairs | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
ESH-01 | ESH-01 | PI15262 | Verified | Clean up interior of 1A-ESH-PNL-0002; 208/120V, Service HRSG 1A Top, located at ground level E side, near HRSG stairs | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Randy Carpenter
ESH-01 | ESH-01 | PI15263 | Verified | Need touch up paint at 1A-ESH-XFM-0002; 208/120V, Service HRSG 1A Top PNL, located at ground level E side, near HRSG stairs | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
ESH-01 | ESH-01 | PI15264 | Verified | Need laminated waterproof panel schedule at 1A-ESH-PNL-0003; 208/120V, Service HRSG 1A Ground Level E, located inside HRSG A PDC | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15265 | Verified | Need touch up paint at 1A-ESH-PNL-0003; 208/120V, Service HRSG 1A Ground Level E, located inside HRSG A PDC | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
ESH-01 | ESH-01 | PI15266 | Verified | Clean up interior of 1A-ESH-PNL-0003; 208/120V, Service HRSG 1A Ground Level E, located inside HRSG A PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Randy Carpenter
ESH-01 | ESH-01 | PI15267 | Verified | 1A-ESH-XFM-0003 cover bolts missing at 1A-ESH-PNL-0003; 208/120V, Service HRSG 1A Ground Level E, located inside HRSG A PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Randy Carpenter
ESH-01 | ESH-01 | PI15268 | Verified | Tie wrap and straighten cable from cable tray to conduit at 1A-ESH-PNL-0003; 208/120V, Service HRSG 1A Ground Level E, located inside HRSG A PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-04-29 | Matt Gilmore | 2020-08-14 | Dave Goldak
ESH-01 | ESH-01 | PI15269 | Verified | Need laminated waterproof panel schedule at 1A-ESH-PNL-0004; 208/120V, Service HRSG 1A Ground Level West, located inside HRSG A PDC | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15270 | Verified | Need touch up paint at 1A-ESH-PNL-0004; 208/120V, Service HRSG 1A Ground Level West, located inside HRSG A PDC | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
ESH-01 | ESH-01 | PI15271 | Verified | Clean up interior of 1A-ESH-PNL-0004; 208/120V, Service HRSG 1A Ground Level West, located inside HRSG A PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15272 | Verified | Missing cover bolts at 1A-ESH-PNL-0004; 208/120V, Service HRSG 1A Ground Level West, located inside HRSG A PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Randy Carpenter
ESH-01 | ESH-01 | PI15273 | Verified | Clean off top of 1A-ESH-PNL-0004; 208/120V, Service HRSG 1A Ground Level West, located inside HRSG A PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Randy Carpenter
ESH-01 | ESH-01 | PI15274 | Verified | Need laminated waterproof panel schedule at 1A-ESH-PNL-0005; 208/120V,HRSG 1A PDC Non Essential PNL, located inside HRSG A PDC | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15275 | Verified | Need touch up paint at 1A-ESH-PNL-0005; 208/120V, HRSG 1A PDC Non Essential PNL, located inside HRSG A PDC | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
ESH-01 | ESH-01 | PI15276 | Verified | Clean up interior of 1A-ESH-PNL-0005; 208/120V, HRSG 1A PDC Non Essential PNL, located inside HRSG A PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15277 | Verified | Clean off top of 1A-ESH-PNL-0005; 208/120V, HRSG 1A PDC Non Essential PNL, located inside HRSG A PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Randy Carpenter
ESH-01 | ESH-01 | PI15278 | Verified | Need laminated waterproof panel schedule at 1B-ESH-PNL-0001; 208/120V, Service CTG 1B PNL, located at ground level, SE side of GT B, near CO2 Tank | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15279 | Verified | Need touch up paint at 1B-ESH-PNL-0001; 208/120V, Service CTG 1B PNL, located at ground level, SE side of GT B, near CO2 Tank | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-03-31 | Randy Carpenter
ESH-01 | ESH-01 | PI15280 | Verified | Clean up interior of 1B-ESH-PNL-0001; 208/120V, Service CTG 1B PNL, located at ground level, SE side of GT B, near CO2 Tank | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15281 | Verified | 1B-ESH-XFMR-0001 needs touch up paint at 1B-ESH-PNL-0001; 208/120V, Service CTG 1B PNL, located at ground level, SE side of GT B, near CO2 Tank | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
ESH-01 | ESH-01 | PI15282 | Verified | Need laminated waterproof panel schedule at 1B-ESH-PNL-0002; 208/120V, Service HRSG 1B Top PNL, located at ground level, E side of HRSG B, near HRSG stairs | C | C | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15283 | Verified | Need touch up paint (exterior and interior) at 1B-ESH-PNL-0002; 208/120V, Service HRSG 1B Top PNL, located at ground level, E side of HRSG B, near HRSG stairs | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-03-31 | Randy Carpenter
ESH-01 | ESH-01 | PI15284 | Verified | Clean up interior of 1B-ESH-PNL-0002; 208/120V, Service HRSG 1B Top PNL, located at ground level, E side of HRSG B, near HRSG stairs | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15285 | Verified | 1B-ESH-XFM-0002 needs touch up paint at 1B-ESH-PNL-0002; 208/120V, Service HRSG 1B Top PNL, located at ground level, E side of HRSG B, near HRSG stairs | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-03-31 | Randy Carpenter
ESH-01 | ESH-01 | PI15286 | Verified | 1B-ESH-XFM-0002 needs new phenolic lable at 1B-ESH-PNL-0002; 208/120V, Service HRSG 1B Top PNL, located at ground level, E side of HRSG B, near HRSG stairs | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Randy Carpenter
ESH-01 | ESH-01 | PI15287 | Verified | Need laminated waterproof panel schedule at 1B-ESH-PNL-0003; 208/120V, Service HRSG 1B Ground Level E PNL, located inside HRSG B PDC | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15288 | Verified | Need touch up paint at 1B-ESH-PNL-0003; 208/120V, Service HRSG 1B Ground Level E PNL, located inside HRSG B PDC | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-03-31 | Randy Carpenter
ESH-01 | ESH-01 | PI15289 | Verified | Clean up interior of 1B-ESH-PNL-0003; 208/120V, Service HRSG 1B Ground Level E PNL, located inside HRSG B PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15290 | Verified | Tie wrap and straighten cable from cable tray to conduit at 1B-ESH-PNL-0003; 208/120V, Service HRSG 1B Ground Level E PNL, located inside HRSG B PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-04-29 | Matt Gilmore | 2020-08-14 | Dave Goldak
ESH-01 | ESH-01 | PI15291 | Verified | Need laminated waterproof panel schedule at 1B-ESH-PNL-0004; 208/120V, Service HRSG 1B Ground Level W PNL, located inside HRSG B PDC | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15292 | Verified | Need touch up paint at 1B-ESH-PNL-0004; 208/120V, Service HRSG 1B Ground Level W PNL, located inside HRSG B PDC | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-03-31 | Randy Carpenter
ESH-01 | ESH-01 | PI15293 | Verified | Clean up interior of 1B-ESH-PNL-0004; 208/120V, Service HRSG 1B Ground Level W PNL, located inside HRSG B PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15294 | Verified | Need laminated waterproof panel schedule at 1B-ESH-PNL-0005; 208/120V, HRSG 1B PDC Non-Essential PNL, located inside HRSG B PDC | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15295 | Verified | Need touch up paint at 1B-ESH-PNL-0005; 208/120V, HRSG 1B PDC Non-Essential PNL, located inside HRSG B PDC | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-03-31 | Randy Carpenter
ESH-01 | ESH-01 | PI15296 | Verified | Clean up interior of 1B-ESH-PNL-0005; 208/120V, HRSG 1B PDC Non-Essential PNL, located inside HRSG B PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15297 | Verified | Need laminated waterproof panel schedule at 1C-ESH-PNL-0001; 208/120V, ST/BOP 1C Service Panel 1, located ground floor, W side of STG Bldg, near Closed Cooling Water Pumps | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15298 | Verified | Need touch up paint at 1C-ESH-PNL-0001; 208/120V, ST/BOP 1C Service Panel 1, located ground floor, W side of STG Bldg, near Closed Cooling Water Pumps | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-03-31 | Randy Carpenter
ESH-01 | ESH-01 | PI15299 | Verified | Clean up interior of 1C-ESH-PNL-0001; 208/120V, ST/BOP 1C Service Panel 1, located ground floor, W side of STG Bldg, near Closed Cooling Water Pumps | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15300 | Verified | Hold down cover for trip plate inside panel missing screw at 1C-ESH-PNL-0001; 208/120V, ST/BOP 1C Service Panel 1, located ground floor, W side of STG Bldg, near Closed Cooling Water Pumps | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-25 | Randy Carpenter
ESH-01 | ESH-01 | PI15301 | Verified | Need plastic caps on in-coming uni-strut conduit support at 1C-ESH-PNL-0001; 208/120V, ST/BOP 1C Service Panel 1, located ground floor, W side of STG Bldg, near Closed Cooling Water Pumps | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15302 | Verified | Need laminated waterproof panel schedule at 1C-ESH-PNL-0002; 208/120V, ST/BOP 1C Service Panel 2, located ground floor, STG Bldg SE corner | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm | 2020-01-20 | Mike Tabbert | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15303 | Verified | Need touch up paint at 1C-ESH-PNL-0002; 208/120V, ST/BOP 1C Service Panel 2, located ground floor, STG Bldg SE corner | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-03-31 | Randy Carpenter
ESH-01 | ESH-01 | PI15304 | Verified | Clean up interior of 1C-ESH-PNL-0002; 208/120V, ST/BOP 1C Service Panel 2, located ground floor, STG Bldg SE corner | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15305 | Verified | Need condolet covers at front and back side of 1C-ESH-PNL-0002; 208/120V, ST/BOP 1C Service Panel 2, located ground floor, STG Bldg SE corner | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-03-31 | Matt Gilmore | 2020-08-14 | Dave Goldak
ESH-01 | ESH-01 | PI15306 | Verified | Tighten trim plates inside 1C-ESH-PNL-0002; 208/120V, ST/BOP 1C Service Panel 2, located ground floor, STG Bldg SE corner | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2021-01-05 | Keith Pollock
ESH-01 | ESH-01 | PI15307 | Verified | Need laminated waterproof panel schedule at 10-ESH-PNL-0001; 208/120V, Main PDC (Non-Essential), located inside Main PDC | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15308 | Verified | Need touch up paint at 10-ESH-PNL-0001; 208/120V, Main PDC (Non-Essential), located inside Main PDC | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-03-31 | Randy Carpenter
ESH-01 | ESH-01 | PI15309 | Verified | Clean up interior of 10-ESH-PNL-0001; 208/120V, Main PDC (Non-Essential), located inside Main PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15310 | Verified | Missing panel cover bolts at 10-ESH-PNL-0001; 208/120V, Main PDC (Non-Essential), located inside Main PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
ESH-01 | ESH-01 | PI15311 | Verified | Need laminated waterproof panel schedule at 10-ESH-PNL-0002; 208/120V, Main PDC (Non-Essential), located inside Main PDC | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15312 | Verified | Clean up interior of 10-ESH-PNL-0002; 208/120V, Main PDC (Non-Essential), located inside Main PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
ESH-01 | ESH-01 | PI15313 | Verified | Need touch up paint at 10-ESH-PNL-0002; 208/120V, Main PDC (Non-Essential), located inside Main PDC | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-03-31 | Randy Carpenter
ESH-01 | ESH-01 | PI15314 | Verified | Need laminated waterproof panel schedule at 10-ESH-PNL-0004; 208/120V Service, Cooling Tower Area Panel, located inside Cooling Tower PDC | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15315 | Verified | Clean up interior of 10-ESH-PNL-0004; 208/120V Service, Cooling Tower Area Panel, located inside Cooling Tower PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
ESH-01 | ESH-01 | PI15316 | Verified | Need touch up paint at 10-ESH-PNL-0004; 208/120V Service, Cooling Tower Area Panel, located inside Cooling Tower PDC | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-03-31 | Randy Carpenter
ESH-01 | ESH-01 | PI15317 | Verified | Need laminated waterproof panel schedule at 10-ESH-PNL-0004; 208/120V, Demin Building Service Panel, located inside Demin Water Bldg | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15318 | Verified | Clean up interior of 10-ESH-PNL-0004; 208/120V, Demin Building Service Panel, located inside Demin Water Bldg | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
ESH-01 | ESH-01 | PI15319 | Verified | Need touch up paint at 10-ESH-PNL-0004; 208/120V, Demin Building Service Panel, located inside Demin Water Bldg | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-03-31 | Randy Carpenter
ESH-01 | ESH-01 | PI15320 | Verified | Replace interior cover at 10-ESH-PNL-0004; 208/120V, Demin Building Service Panel, located inside Demin Water Bldg | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Randy Carpenter
ESH-01 | ESH-01 | PI15321 | Verified | 10-ESH-PNL-0004; 208/120V, Demin Building Service Panel phenolic label is incorrect, need new tag, panel located inisde Demin Water Bldg | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
ESH-01 | ESH-01 | PI15322 | Verified | Need grounding on Myers Hub at 10-ESH-PNL-0004; 208/120V, Demin Building Service Panel, located inside Demin Water Bldg | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2021-03-03 | John Watts
ESH-01 | ESH-01 | PI15323 | Verified | Interior blank cover at bottom of panel is missing at 10-ESH-PNL-0007; 208-120V Water Intake Panel, located at Raw Water PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-04-22 | Matt Gilmore | 2021-03-03 | John Watts
ESH-01 | ESH-01 | PI15324 | Verified | Need laminated waterproof panel schedule at 10-ESH-PNL-0007; 208-120V Water Intake Panel, located at Raw Water PDC | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
ESH-01 | ESH-01 | PI15325 | Verified | Clean up interior of 10-ESH-PNL-0007; 208-120V Water Intake Panel, located at Raw Water PDC | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Randy Carpenter
ESH-01 | ESH-01 | PI15326 | Verified | Need touch up paint at 10-ESH-PNL-0007; 208-120V Water Intake Panel, located at Raw Water PDC | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-08-17 | Dave Goldak
ESH-01 | ESH-01 | PI15327 | Verified | 10-ESH-XFM-0007 needs touch up paint at 10-ESH-PNL-0007; 208-120V Water Intake Panel, located at Raw Water PDC | C | X | Jerry Smith | McD | 2020-01-06 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-08-17 | Dave Goldak
ESL-01 | ESL-01 | PI08458 | Verified | Complete lighting raw water area. | A | E | Michael Law | McD | 2019-10-02 | Michael Law | Const |  |  | 2020-01-13 | Michael Law
ESL-01 | ESL-01 | PI15588 | Cleared | Need additional lighting Fuel Gas Filter Separator skid | C | C | Mike Tabbert | McD | 2020-01-08 | Mike Tabbert | Comm | 2020-05-26 | Mike Tabbert
ESL-01 | ESL-01 | PI18110 | Verified | 1B HRSG Stack Lighting - 1B south west fixed stack lighting is out. | C | E | Mike Tabbert | McD | 2020-03-20 | Mike Tabbert | Comm | 2020-03-21 | Mike Tabbert | 2021-06-17 | John Watts
ESL-01 | ESL-01 | PI18111 | Open | 1A HRSG - Both south stack FAA warning lights are out. | C | E | Mike Tabbert | McD | 2020-03-20 | Mike Tabbert | Comm
ESL-01 | ESL-01 | PI18638 | Verified | CTG-1A Area, Complete installation of receptacles | C | E | Chris Colvin | McD | 2020-06-15 | Chris Colvin | Const | 2020-06-26 | Chris Colvin | 2020-08-21 | Mike Tabbert
ESL-01 | ESL-01 | PI18639 | Verified | CTG-1A Area, Light fixture circuits on SFC stairways need to be corrected. | C | E | Chris Colvin | McD | 2020-06-15 | Chris Colvin | Const | 2020-06-17 | Chris Colvin | 2020-08-07 | Mike Tabbert
ESL-01 | ESL-01 | PI18640 | Verified | CTG-1A Area, Light fixture circuits filter deck stair tower need to be corrected | C | E | Chris Colvin | McD | 2020-06-15 | Chris Colvin | Const | 2020-06-17 | Chris Colvin | 2020-08-07 | Mike Tabbert
ESL-01 | ESL-01 | PI18641 | Verified | CTG-1A Area, complete floodlight installation on GSU blast walls. | C | E | Chris Colvin | McD | 2020-06-15 | Chris Colvin | Const | 2020-07-20 | Chris Colvin | 2020-08-07 | Mike Tabbert
ESL-01 | ESL-01 | PI18642 | Verified | Red line panel schedule LK-1A-ESL-EE-PNL-0003 | B | E | Mike Tabbert | McD | 2020-06-15 | Mike Tabbert | Const | 2020-06-15 | Mike Tabbert | 2020-06-15 | Mike Tabbert
ESL-01 | ESL-01 | PI18643 | Verified | Red line drawing LK-1A-411-PL-EE-LTG-0002-S02 | B | E | Mike Tabbert | McD | 2020-06-15 | Mike Tabbert | Const | 2020-06-15 | Mike Tabbert | 2020-06-15 | Mike Tabbert
ESL-01 | ESL-01 | PI18644 | Verified | Red line drawing LK-1A-411-PL-EE-LTG-0001-S01 | B | E | Mike Tabbert | McD | 2020-06-15 | Mike Tabbert | Const | 2020-06-15 | Albert Burge | 2020-06-15 | Mike Tabbert
ESL-01 | ESL-01 | PI18645 | Verified | Red line drawing LK-1A-411-EV-EE-LTG-0001-S01 | B | E | Mike Tabbert | McD | 2020-06-15 | Mike Tabbert | Const | 2020-06-15 | Mike Tabbert | 2020-06-15 | Mike Tabbert
ESL-01 | ESL-01 | PI18671 | Verified | Gas Turbine B, Light Fixtures at Control Package B do not work. | C | E | Chris Colvin | McD | 2020-06-22 | Chris Colvin | Const | 2020-06-23 | Chris Colvin | 2020-07-10 | Mike Tabbert
ESL-01 | ESL-01 | PI18672 | Verified | Gas Turbine B, Panel 1B-ESL-PNL-0003, Receptacles in this area not working | C | E | Chris Colvin | McD | 2020-06-22 | Chris Colvin | Const | 2020-06-23 | Chris Colvin | 2020-08-21 | Mike Tabbert
ESL-01 | ESL-01 | PI18673 | Verified | Gas Turbine B, Intake Air deck recptacle box needs plug. | C | E | Chris Colvin | McD | 2020-06-22 | Chris Colvin | Const | 2020-06-23 | Chris Colvin | 2020-08-21 | Mike Tabbert
ESL-01 | ESL-01 | PI18674 | Verified | Gas Turbine B, east side light fixture at stairway to turbine enclosure missing T cover. | C | E | Chris Colvin | McD | 2020-06-22 | Chris Colvin | Const | 2020-06-23 | Chris Colvin | 2020-08-21 | Mike Tabbert
ESL-01 | ESL-01 | PI18675 | Verified | Gas turbine B, Drawing 1B-421-PL-EE-LTG-0002-S01, light fixtures on this drawing wrong circuit. | C | E | Chris Colvin | McD | 2020-06-22 | Chris Colvin | Const | 2020-06-23 | Chris Colvin | 2020-08-07 | Mike Tabbert
ESL-01 | ESL-01 | PI18676 | Verified | Gas Turbine B, Drawing 1B-421-PL-EE-LTG-0001-S02, Receptacle box on this drawing needs plug and T cover missing in this area. | C | E | Chris Colvin | McD | 2020-06-22 | Chris Colvin | Const | 2020-06-23 | Chris Colvin | 2020-08-21 | Mike Tabbert
ESL-01 | ESL-01 | PI18677 | Verified | Gas Turbine B, Drawing 1B-421-EV-EE-LTG-0001-S02, Light Fixtures on wrong circuit, receptacle not working, needs cover and plug. | C | E | Chris Colvin | McD | 2020-06-22 | Chris Colvin | Const | 2020-06-23 | Chris Colvin | 2020-08-07 | Mike Tabbert
ESL-01 | ESL-01 | PI18678 | Verified | Gas Turbine B, Drawing 1B-421-EV-EE-LTG-0001-S01, receptacle not working. | C | E | Chris Colvin | McD | 2020-06-22 | Chris Colvin | Const | 2020-06-23 | Chris Colvin | 2020-08-21 | Mike Tabbert
ESL-01 | ESL-01 | PI18679 | Verified | STG, Light Fixture at top of south stair tower needs permanent supports installed. | C | E | Chris Colvin | McD | 2020-06-22 | Chris Colvin | Const | 2020-07-20 | Chris Colvin | 2020-08-07 | Mike Tabbert
ESL-01 | ESL-01 | PI18680 | Cleared | STG, emergency lights need adjusted. | C | E | Chris Colvin | McD | 2020-06-22 | Chris Colvin | Const | 2020-06-26 | Chris Colvin | 2021-08-02 | John Watts
ESL-01 | ESL-01 | PI18899 | Verified | HRSG 1B, Drawing 1B-121-PL-EE-LTG-0001-S02, Fixtures on main pipe rack not complete. | C | E | Chris Colvin | McD | 2020-07-10 | Chris Colvin | Const | 2020-07-20 | Chris Colvin | 2020-08-21 | Mike Tabbert
ESL-01 | ESL-01 | PI18900 | Verified | HRSG 1B, Drawing 1B-121-PL-EE-LTG-0001-S02, Receptacle at 594 elevation not complete. | C | E | Chris Colvin | McD | 2020-07-10 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-08-24 | Mike Tabbert
ESL-01 | ESL-01 | PI18901 | Verified | HRSG 1B, Drawing 1B-121-PL-EE-LTG-0001-S02, Fixtures on stack wrong circuit. | C | E | Chris Colvin | McD | 2020-07-10 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-08-24 | Mike Tabbert
ESL-01 | ESL-01 | PI18902 | Verified | HRSG 1B, Drawing 1B-121-PL-EE-LTG-0002-S02, Fixture wrong circuit elevation 511 | C | E | Chris Colvin | McD | 2020-07-10 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-08-24 | Mike Tabbert
ESL-01 | ESL-01 | PI18903 | Verified | HRSG 1B, Drawing 1B-121-PL-EE-LTG-0002-S02, Fixture wrong circuit stack. | C | E | Chris Colvin | McD | 2020-07-10 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-08-24 | Mike Tabbert
ESL-01 | ESL-01 | PI18904 | Verified | HRSG 1B, Drawing 1B-121-PL-EE-LTG-0002-S01, Receptacles not installed elevation 509 | C | E | Chris Colvin | McD | 2020-07-10 | Chris Colvin | Const | 2020-07-20 | Chris Colvin | 2020-08-24 | Mike Tabbert
ESL-01 | ESL-01 | PI18905 | Verified | HRSG 1B, Drawing 1B-121-EV-EE-LTG-0002-S02, Fixture wrong circuit elevation 570 | C | E | Chris Colvin | McD | 2020-07-10 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-08-24 | Mike Tabbert
ESL-01 | ESL-01 | PI18906 | Verified | HRSG 1B, Condulet covers missing from top to bottom of HRSG. | C | E | Chris Colvin | McD | 2020-07-10 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-08-24 | Mike Tabbert
ESL-01 | ESL-01 | PI19257 | Verified | Redline drawing to submit | C | E | Mike Tabbert | McD | 2020-08-07 | Mike Tabbert | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
ESY-01 | ESY-01 | PI01547 | Verified | Seal conduits in 10-ESY-DSW-0003 at control bldg. | A | E | Luis Cantu | McD | 2019-06-22 | Luis Cantu | Const | 2019-06-24 | Luis Cantu | 2019-06-26 | Logan Holland
ESY-01 | ESY-01 | PI01548 | Verified | Clean out 10-ESY-DSW-0003 at control bldg. | A | E | Luis Cantu | McD | 2019-06-22 | Luis Cantu | Const | 2019-06-24 | Luis Cantu | 2019-06-26 | Logan Holland
ESY-01 | ESY-01 | PI01549 | Verified | Attach micarta board in 10-ESY-DSW-0003 at control bldg. | A | E | Luis Cantu | McD | 2019-06-22 | Luis Cantu | Const | 2019-06-24 | Luis Cantu | 2019-06-26 | Logan Holland
FGS-01 | FGS-01 | PI04774 | Verified | Seal conduits at disconnect switch at fuel gas metering area. | A | E | Dustin Futrell | McD | 2019-09-04 | Dustin Futrell | Const | 2019-09-10 | Richard Cruz | 2019-10-05 | Logan Holland
FGS-01 | FGS-01 | PI04775 | Verified | Ground seal tites at disconnect switch at fuel gas metering area. | A | E | Dustin Futrell | McD | 2019-09-04 | Dustin Futrell | Const | 2019-09-10 | Richard Cruz | 2019-10-05 | Logan Holland
FGS-01 | FGS-01 | PI04776 | Verified | Add ground jumper to inside of fiber box at fuel gas metering area. | A | E | Dustin Futrell | McD | 2019-09-04 | Dustin Futrell | Const | 2019-09-10 | Richard Cruz | 2019-10-05 | Logan Holland
FGS-01 | FGS-01 | PI04777 | Verified | Complete inst. tubing to 10-FGS-PDI-0106 & 0107 at fuel gas metering area. | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
FGS-01 | FGS-01 | PI04778 | Verified | Grout supports at fuel gas metering area. | C | C | Johnny Campbell | McD | 2019-09-04 | Johnny Campbell | Const | 2019-10-10 | Jack Fields | 2019-11-23 | Kelvin Cook
FGS-01 | FGS-01 | PI04779 | Verified | Complete inst. tubing to 10-FGS-PC-0109, 0110 & 0111 at fuel gas metering area. | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-06 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
FGS-01 | FGS-01 | PI04780 | Verified | Complete inst. tubing to 10-FGS-HV-0100 at fuel gas metering area. | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-06 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
FGS-01 | FGS-01 | PI04963 | Verified | Install 10-FGS-LI-0205. | B | I | Gonzalo Pena | McD | 2019-09-10 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-09-28 | Mike Tabbert
FGS-01 | FGS-01 | PI05189 | Verified | Rotate actuator on 10-FGS-V-0100A (make same as V-0100B). | A | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const |  |  | 2019-09-18 | Kelvin Cook
FGS-01 | FGS-01 | PI05190 | Verified | Install birdscreens on all 4 vents. | B | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const |  |  | 2019-09-18 | Kelvin Cook
FGS-01 | FGS-01 | PI05191 | Verified | Grout all supports. | C | C | Johnny Campbell | McD | 2019-09-12 | Johnny Campbell | Const | 2019-10-10 | Jack Fields | 2019-12-12 | Michael Law
FGS-01 | FGS-01 | PI05192 | Verified | Install 10-FGS-LSH-0206 on drains tank. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2019-12-12 | Michael Law
FGS-01 | FGS-01 | PI05193 | Verified | Wire up 10-FGS-LSH-0206 on drains tank. | A | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-11-02 | Brad Stanford | 2019-12-13 | Mike Tabbert
FGS-01 | FGS-01 | PI05194 | Verified | Add one (1) ground to the fuel gas drains tank. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
FGS-01 | FGS-01 | PI05195 | Verified | 10-FGS-LIT-0205 needs conduit, seal tite ground. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-03 | Dustin Futrell | 2019-10-04 | Mike Tabbert
FGS-01 | FGS-01 | PI05196 | Verified | Pour seal offs in all panels - after commissioning. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-12-23 | Michael Law | 2020-01-13 | Fred Michael
FGS-01 | FGS-01 | PI05197 | Verified | Ground 10MBY91GZ003. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Dustin Futrell | 2019-10-05 | Logan Holland
FGS-01 | FGS-01 | PI05198 | Verified | Ground pipe flanges. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-10-02 | Dustin Futrell | 2019-10-05 | Mike Tabbert
FGS-01 | FGS-01 | PI05199 | Verified | Tag all valves and instruments. | C | P | Bobby Williams | McD | 2019-09-12 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2020-01-17 | Kelvin Cook
FGS-01 | FGS-01 | PI05200 | Verified | Replace fuel gas drains tank. | A | M | Bobby Williams | McD | 2019-09-12 | Bobby Williams | Const | 2019-09-23 | Bobby Williams | 2019-10-04 | Kelvin Cook
FGS-01 | FGS-01 | PI05201 | Verified | Rotate valve 1A-FGS-V-0112A - interference. | A | P | Bobby Williams | McD | 2019-09-12 | Bobby Williams | Const | 2019-09-20 | Kelvin Cook | 2019-10-15 | Albert Burge
FGS-01 | FGS-01 | PI05202 | Verified | Rotate valve 1A-FGS-V-0113A - interference. | A | P | Bobby Williams | McD | 2019-09-12 | Bobby Williams | Const | 2019-09-20 | Kelvin Cook | 2019-10-15 | Albert Burge
FGS-01 | FGS-01 | PI05844 | Verified | 10CTSK0008, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Johnson
FGS-01 | FGS-01 | PI05845 | Verified | 10CTSK0009, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
FGS-01 | FGS-01 | PI05846 | Verified | 10CTSK0010, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-09-28 | Mike Tabbert
FGS-01 | FGS-01 | PI05847 | Verified | 10FGSC0006, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-10-03 | Michael Law
FGS-01 | FGS-01 | PI05848 | Verified | 10FGSC0007, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-10-03 | Michael Law
FGS-01 | FGS-01 | PI05849 | Verified | 10FGSC0008, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-10-03 | Michael Law
FGS-01 | FGS-01 | PI05850 | Verified | 10FGSC0010, From Termination | A | E | Chris Colvin | McD | 2019-09-13 | Chris Colvin | Const | 2019-11-02 | Brad Stanford | 2019-12-06 | Mike Tabbert
FGS-01 | FGS-01 | PI05851 | Verified | 10FGSK0001, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-10-03 | Michael Law
FGS-01 | FGS-01 | PI05852 | Verified | 10FGSK0003, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-10-03 | Michael Law
FGS-01 | FGS-01 | PI05853 | Verified | 10FGSX0003, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-10-02 | Mike Tabbert
FGS-01 | FGS-01 | PI05854 | Verified | 10FGSX0004, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-01 | FGS-01 | PI05855 | Verified | 10FGSX0155, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
FGS-01 | FGS-01 | PI05856 | Verified | 10CTSK0008, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-25 | Michael Law | 2019-09-25 | Michael Law
FGS-01 | FGS-01 | PI05857 | Verified | 10CTSK0009, To Termination | B | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
FGS-01 | FGS-01 | PI05858 | Verified | 10CTSK0010, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-01 | FGS-01 | PI05859 | Verified | 10FGSC0010, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-10-03 | Michael Law
FGS-01 | FGS-01 | PI05860 | Verified | 10FGSK0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-10-03 | Michael Law
FGS-01 | FGS-01 | PI05861 | Verified | 10FGSK0003, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-10-03 | Michael Law
FGS-01 | FGS-01 | PI05862 | Verified | 10FGSX0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-10-03 | Michael Law
FGS-01 | FGS-01 | PI05863 | Verified | 10FGSX0002, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-10-03 | Michael Law
FGS-01 | FGS-01 | PI05864 | Verified | 10FGSX0003, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const |  |  | 2019-10-02 | Mike Tabbert
FGS-01 | FGS-01 | PI05865 | Verified | 10FGSX0004, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-01 | FGS-01 | PI05866 | Verified | 10FGSX0155, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
FGS-01 | FGS-01 | PI05867 | Verified | Conduits at emergency gas valve need to have permanent supports installed. | B | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
FGS-01 | FGS-01 | PI05868 | Verified | T-Condulets at emergency gas valve instrument panel need to be relocated to be on the back side of the panel, and supports installed. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
FGS-01 | FGS-01 | PI05869 | Verified | Sealtight from T-Condulets to J-Box on instrument panel need to routed behind tubing, in a neat and workmenship like manner. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
FGS-01 | FGS-01 | PI05870 | Verified | Install grounding on all seal tight at instrument panel. | B | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
FGS-01 | FGS-01 | PI05871 | Verified | Install all condulet covers. | B | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
FGS-01 | FGS-01 | PI09142 | Verified | Missing limit switch cable for 10-FGS-ZSO-0100A/B - fuel gas emergency valve 10-FGS-HV-0100. | A | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell |  | 2019-10-09 | Dustin Futrell | 2019-10-10 | Albert Burge
FGS-01 | FGS-01 | PI09143 | Verified | Missing cable for 10-FGS-EHR-0100. Valve limit switch pack - 10-FGS-HV-0100. | A | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell |  | 2019-10-09 | Dustin Futrell | 2019-10-10 | Albert Burge
FGS-01 | FGS-01 | PI09344 | Verified | LK-10-FGS-PD-P41-0103-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-09 | Tom Noble | 2019-10-09 | Tom Noble
FGS-01 | FGS-01 | PI14733 | Verified | 1A-FGS-PD-P40-0265-01: 1A-FGS-HGr-0016 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-13 | Bobby Williams | 2019-12-15 | Kelvin Cook
FGS-01 | FGS-01 | PI15580 | Verified | Valve gear cover plate is open at 10-FGS-HV-0100; Main Fuel Gas Emergency Shutoff Valve | B | P | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Comm |  |  | 2020-02-16 | Shannon Scott
FGS-01 | FGS-01 | PI15581 | Verified | Tighten allen bolts on 10-FGS-HV-0100; Main Fuel Gas Emergency Shutoff Valve | B | P | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Comm | 2020-02-02 | Bobby Williams | 2020-02-05 | Shannon Scott
FGS-01 | FGS-01 | PI15583 | Verified | Remove temporary fitting and pressure indicator at 10-FGS-V-0101B; Nitrogen Purge Isolation Valve, upstream of Emergency Shutoff Valve and Install cap. | C | P | Tim Green | McD | 2020-01-08 | Tim Green | Comm | 2020-06-18 | Tim Green | 2021-04-21 | Johnny Campbell
FGS-01 | FGS-01 | PI15584 | Verified | Need bird screen at 10-FGS-V-0101C; Fuel Gas Header Vent Valve, upstream of Emergency Shutoff Valve | C | P | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Comm | 2020-02-12 | Joseph Lamb | 2020-03-03 | Keith Pollock
FGS-01 | FGS-01 | PI15585 | Verified | Remove all scaffolding at Gas Yard | C | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Comm | 2020-02-20 | Alan Huntsman | 2020-03-03 | Keith Pollock
FGS-01 | FGS-01 | PI15590 | Verified | Remove teflon tape from all tubing fittings and replace with teflon pipe thread sealant at the Fuel Gas Filter Separator Skid | C | I | Gonzalo Pena | McD | 2020-01-08 | Gonzalo Pena | Comm | 2020-02-03 | James Tanner | 2020-02-05 | Shannon Scott
FGS-01 | FGS-01 | PI15591 | Verified | INSTALL Anti Sweat (AS) insulation at Line No. 12-10-FGS-0100-601D1-AS-1.0 | C | Q | Richard McSpadden | PCI | 2020-01-08 | Richard McSpadden | Comm | 2020-08-07 | Richard McSpadden | 2020-10-06 | Dave Goldak
FGS-01 | FGS-01 | PI15592 | Verified | INSTALL Anti Sweat (AS) insulation at Line No. 12-10-FGS-0102-601D2-AS-1.0 | C | Q | Richard McSpadden | PCI | 2020-01-08 | Richard McSpadden | Comm | 2020-08-07 | Richard McSpadden | 2020-08-14 | Dave Goldak
FGS-01 | FGS-01 | PI15593 | Verified | Finish painting in Gas Yard | C | X | Jerry Smith | McD | 2020-01-08 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-06-16 | Dave Goldak
FGS-01 | FGS-01 | PI15594 | Verified | Grout vertical support stanchion baseplate in Gas Yard | C | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Comm | 2020-03-13 | Johnny Campbell | 2020-06-16 | Dave Goldak
FGS-01 | FGS-01 | PI15595 | Verified | Tighten vertical support stanchion baseplate anchor bolts in Gas Yard | C | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Comm | 2020-03-18 | Johnny Campbell | 2020-04-06 | Bernard Stasse
FGS-01 | FGS-01 | PI15596 | Verified | Replace/Straighten bent IA SS tubing at underground stub up, NE corner of Fuel Gas Filter Separator Skid | C | I | Gonzalo Pena | McD | 2020-01-08 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-20 | Shannon Scott
FGS-01 | FGS-01 | PI15597 | Verified | Pour incoming conduit seals at 10MBP01GH011; DC Power Junction Box | B | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm |  |  | 2020-01-13 | Fred Michael
FGS-01 | FGS-01 | PI15598 | Verified | Heat shrink wire tags at 10MBP01GH011; DC Power Junction Box | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2021-05-27 | John Watts
FGS-01 | FGS-01 | PI15599 | Verified | Remove spare parts and clean up inside 10MBP01GH011; DC Power Junction Box | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2021-05-27 | John Watts
FGS-01 | FGS-01 | PI15600 | Verified | Center door hinge is missing at 10MBP01GH011; DC Power Junction Box | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2020-06-16 | Dave Goldak
FGS-01 | FGS-01 | PI15601 | Verified | Heat shrink wire tags at 10MBP01GH012; AC Power Junction Box | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm |  |  | 2020-01-13 | Fred Michael
FGS-01 | FGS-01 | PI15602 | Verified | Verify wire tag number 10CTSK0010 is correct at 10MBP01GH012; AC Power Junction Box | C | E | Mike Tabbert | McD | 2020-01-08 | Mike Tabbert | Comm | 2020-02-12 | Mike Tabbert | 2020-02-15 | Shannon Scott
FGS-01 | FGS-01 | PI15603 | Verified | Spare tag 10CTSK0009 found inside panel, ensure all wiring is properly tagged at 10MBP01GH012; AC Power Junction Box | C | E | Mike Tabbert | McD | 2020-01-08 | Mike Tabbert | Comm | 2020-02-12 | Mike Tabbert | 2020-02-15 | Shannon Scott
FGS-01 | FGS-01 | PI15604 | Verified | Heat shrink wire tags at 1AMBY92GH063; FG Filter Separator Junction Box | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-15 | Shannon Scott
FGS-01 | FGS-01 | PI15605 | Verified | Conduit missing condolet covers at 10-FGS-LI-0205; Fuel Gas Filter Separator Drains Tank Level Indicator | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm |  |  | 2020-01-13 | Fred Michael
FGS-01 | FGS-01 | PI15606 | Verified | Flex conduit ground missing at 10-FGS-LI-0205; Fuel Gas Filter Separator Drains Tank Level Indicator | B | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-15 | Shannon Scott
FGS-01 | FGS-01 | PI15607 | Verified | One cable not terminated at 10-FGS-LI-0205; Fuel Gas Filter Separator Drains Tank Level Indicator | B | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-01-29 | Jared Stimpson | 2020-02-05 | Shannon Scott
FGS-01 | FGS-01 | PI15608 | Verified | Tighten U-Bolts at 1A Filter Separator 1" drain Line No. 1-1A-FGS-0205 | C | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-20 | Shannon Scott
FGS-01 | FGS-01 | PI15609 | Verified | Seal ground cable conduit on concrete pad at 1st above ground flange, Line No. 12-10-FGS-0102 | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2020-08-20 | Nelson Eichelberger
FGS-01 | FGS-01 | PI15610 | Verified | Remove unused uni-strut from 12" Fuel Gas Header Piping, downstream of 1st above ground flange, Line No. 12-10-FGS-0102 | C | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-22 | Shannon Scott
FGS-01 | FGS-01 | PI15611 | Verified | U-Bolt needs insulating kit, see downstream Fuel Gas Header insulated U-Bolts | B | P | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Comm | 2020-02-11 | Charlie English | 2020-02-15 | Shannon Scott
FGS-01 | FGS-01 | PI15612 | Verified | Need permanent tags indicating McDermott nomenclature for FGS-01 subsystem, the Fuel Gas Filter Separator components are currently tagged with Mitsubishi nomenclature | B | P | Bobby Williams | McD | 2020-01-08 | Bobby Williams | Comm | 2020-01-21 | Bobby Williams | 2020-02-02 | Shannon Scott
FGS-01 | FGS-01 | PI15614 | Verified | Interior insulation panel is loose, needs to be attached with glue at 10MBY91GZ009; GT Fuel Gas Calorie Meter Panel | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-15 | Shannon Scott
FGS-01 | FGS-01 | PI15615 | Verified | Install tubing drain for Vortex Cooler inside 10MBY91GZ009; GT Fuel Gas Calorie Meter Panel | C | I | Gonzalo Pena | McD | 2020-01-08 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
FGS-01 | FGS-01 | PI15616 | Verified | Seal and paint red all plugs inside 10MBY91GZ009; GT Fuel Gas Calorie Meter | B | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm |  |  | 2020-01-13 | Fred Michael
FGS-01 | FGS-01 | PI09358 | Verified | LK-10-FGS-PD-P41-0286-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const |  |  | 2019-10-29 | Tom Noble
FGS-01 | FGS-01 | PI06604 | Verified | Pour all seal-offs prior to gas. | B | E | Chris Colvin | McD | 2019-09-20 | Chris Colvin | Const |  |  | 2019-12-09 | Michael Law
FGS-01 | FGS-01 | PI07841 | Verified | 1A-FGS-PD-P40-0100-01 install ground wire at 1A-FGS-V-0110 & 1A-CTS-SP-0100/EKE01-101 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-02 | Dustin Futrell | 2019-10-02 | Kelvin Cook
FGS-01 | FGS-01 | PI07840 | Verified | 1A-FGS-PD-P40-0100-01 install ground plug at 1A-FGS-V-0110 & 1A-CTS-SP-0100/EKE01-101 | A | P | Damon Turner | McD | 2019-09-28 | Damon Turner | Const | 2019-10-02 | Bobby Williams | 2019-10-02 | Kelvin Cook
FGS-01 | FGS-01 | PI15617 | Verified | Valve installed at TP-1A instead of .5x.25 reducer. Assign equipment ID # to valve and update PID | C | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-05-12 | James Beech | 2020-06-16 | Dave Goldak
FGS-01 | FGS-01 | PI15618 | Verified | INSTALL Anti Sweat (AS) insulation at Line No. 12-10-FGS-0101-601D2-AS-1.0 | C | Q | Richard McSpadden | PCI | 2020-01-08 | Richard McSpadden | Comm | 2020-08-07 | Richard McSpadden | 2020-10-06 | Dave Goldak
FGS-01 | FGS-01 | PI15619 | Verified | Valve installed at TP-1B instead of .5x.25 reducer. Assign equipment ID # to valve and update PID | C | P | Charles Worthington | McD | 2020-01-08 | Charles Worthington | Comm | 2020-06-10 | Charles Worthington | 2020-06-16 | Dave Goldak
FGS-01 | FGS-01 | PI15620 | Verified | SRV 0109 and following vent not installed downstream of PI 108A/B. | C | I | Gonzalo Pena | McD | 2020-01-08 | Gonzalo Pena | Comm | 2020-02-10 | James Tanner | 2020-02-17 | Shannon Scott
FGS-01 | FGS-01 | PI15622 | Verified | Support 10-FGS-PD-HGR-0074 installed in different location per isometric | C | P | Kelvin Cook | McD | 2020-01-08 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-06-16 | Dave Goldak
FGS-01 | FGS-01 | PI15623 | Verified | Vendor supplied control skid not assembled in accordance with CBI PID. Surface site. | C | I | Charles Worthington | McD | 2020-01-08 | Charles Worthington | Comm | 2020-04-28 | Charles Worthington | 2020-06-16 | Dave Goldak
FGS-01 | FGS-01 | PI16535 | Verified | Grout pipe supports. | C | C | Alan Huntsman | McD | 2020-02-04 | Alan Huntsman | Const | 2020-02-20 | Alan Huntsman | 2020-03-03 | Michael Law
FGS-01 | FGS-01 | PI17767 | Verified | FGS-01 SRV-109 is incorrectly tagged. (It reads FGS-SRV-108.) | C | P | James Beech | McD | 2020-03-11 | James Beech | Const | 2020-03-12 | Tim Green | 2020-07-28 | Nelson Eichelberger
FGS-02 | FGS-02 | PI04448 | Verified | Complete the fuel gas inlet filter drain piping. | A | P | Joshua Sturgeon | McD | 2019-08-21 | Joshua Sturgeon | Const | 2019-10-08 | Shane Crowe | 2019-10-24 | Brian Ballard
FGS-02 | FGS-02 | PI04449 | Verified | Remove garlock gasket in the fuel gas supply line just downstream for the fuel gas inlet filter and restore with permanent gasket and hardware. | B | P | Terry Deaton | McD | 2019-08-21 | Terry Deaton | Const | 2019-08-26 | Terry Deaton | 2019-08-28 | Brian Ballard
FGS-02 | FGS-02 | PI04450 | Verified | Complete the piping connection for the fuel gas scrubber unit per LC-01685 page 16, connection EKE01-119. | A | P | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-24 | Brian Ballard
FGS-02 | FGS-02 | PI04451 | Verified | Complete the piping connection for the fuel gas scrubber unit per LC-01685 page 16, connection QFF11-644. | A | P | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-08-29 | Terry Deaton | 2019-10-24 | Brian Ballard
FGS-02 | FGS-02 | PI04453 | Verified | Complete the fuel gas heater drain pipe. | A | P | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const |  |  | 2019-10-25 | Ron McMurtry
FGS-02 | FGS-02 | PI04454 | Verified | Complete the fuel gas heater interconnect piping per LC-01585 page 24.. | A | P | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-10-25 | Bobby Williams | 2019-10-25 | Ron McMurtry
FGS-02 | FGS-02 | PI04455 | Verified | Complete the fuel gas heater platform installation per LC-01585 page 34-37. | A | M | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const |  |  | 2019-10-25 | Ron McMurtry
FGS-02 | FGS-02 | PI04456 | Verified | Complete the dew point heater connections LC-01681-QJA01-103 and EKE01-104. | A | P | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const |  |  | 2019-10-25 | Ron McMurtry
FGS-02 | FGS-02 | PI04457 | Verified | Remove rubber plates in the dew point heater flanges EKC01-101 and EKE01-103 and restore with permanent gasket and hardware.. | A | P | Bobby Williams | McD | 2019-08-21 | Bobby Williams | Const | 2019-09-09 | Damon Turner | 2019-10-24 | Brian Ballard
FGS-02 | FGS-02 | PI04964 | Verified | Install 1A-FGS-LI-0220. | B | I | Gonzalo Pena | McD | 2019-09-10 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-09-28 | Mike Tabbert
FGS-02 | FGS-02 | PI07389 | Verified | Tighten u-bolt on the inlet at the fuel gas separator. | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-12-19 | J.L. Bickham
FGS-02 | FGS-02 | PI07391 | Verified | Valve 1AQJA01AA112 missing handle - fuel gas separator. | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-15 | Shannon Scott
FGS-02 | FGS-02 | PI07392 | Verified | Grout all supports. | C | C | Johnny Campbell | McD | 2019-09-27 | Johnny Campbell | Const | 2019-10-10 | Jack Fields | 2019-12-12 | Joshua Sturgeon
FGS-02 | FGS-02 | PI07394 | Verified | Clean all fuel gas skids. | B | C | Alan Huntsman | McD | 2019-09-27 | Alan Huntsman | Const | 2019-11-12 | Carlos Wallen | 2019-12-31 | William Mitchell
FGS-02 | FGS-02 | PI07397 | Verified | Valves handles 1A-FGS-V-0264, 0263 & 0260 at the duct burner skid have interference with handrail. | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-15 | Shannon Scott
FGS-02 | FGS-02 | PI07400 | Verified | Set all spring cans to cold setting & pull gags. | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-12-31 | William Mitchell
FGS-02 | FGS-02 | PI07402 | Verified | Replace CS nipple with SS nipple at 1ABMBA01CT026 at the fuel gas inlet filter. | A | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-10-15 | Gonzalo Pena | 2019-10-24 | Shannon Scott
FGS-02 | FGS-02 | PI07404 | Verified | Valve 1AEKE01AA852 missing handle at the fuel gas scrubber. | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07405 | Verified | Adjust high point vent valve for operator usage at the fuel gas scrubber. | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07407 | Verified | Valve 1AEKC01AA103 - handle missing operating knob - at dew point heater skid. | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-02 | FGS-02 | PI07408 | Verified | Valve 1AEKC01AA103 at dew point heater skid has insufficient clearance with column. | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-23 | Kelvin Cook
FGS-02 | FGS-02 | PI07410 | Verified | Tag all valves. | C | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const |  |  | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07412 | Verified | Conduit on LS-MP01CL222 and 223 to straighten up. Need additional support on conduit to stay straight | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-11 | Brad Stanford | 2019-12-30 | Chris Boudreaux
FGS-02 | FGS-02 | PI07415 | Verified | Low point drain or a bug screen needed for TE-MBP01CT026 - FG filter inlet | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-04 | Richard Cruz | 2019-12-30 | Chris Boudreaux
FGS-02 | FGS-02 | PI07416 | Verified | PI-EKE01CP302 not installed on top of FG Scrubber unit | A | I | Joshua Sturgeon | McD | 2019-09-27 | Joshua Sturgeon | Const | 2019-10-24 | Gonzalo Pena | 2019-10-24 | Albert Burge
FGS-02 | FGS-02 | PI07417 | Verified | LS-EKE01CL201 not mounted - FG Scrubber unit | B | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-12-01 | Albert Burge
FGS-02 | FGS-02 | PI07421 | Verified | Ground 1st flange from UG to grid - FG Separator skid | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FGS-02 | FGS-02 | PI07422 | Verified | Ground 2nd flange from UG, to the next flange to grid - FG Separator skid | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-25 | Mike Tabbert
FGS-02 | FGS-02 | PI07423 | Verified | Ground separator tanks to grid (2 each) | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-04 | Richard Cruz | 2019-12-30 | Chris Boudreaux
FGS-02 | FGS-02 | PI07424 | Verified | FG Separator skid - ground duct bank | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-11 | Brad Stanford | 2019-12-30 | Chris Boudreaux
FGS-02 | FGS-02 | PI07425 | Verified | FG Separator skid - seal at duct banks | B | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-11 | Brad Stanford | 2019-12-30 | Chris Boudreaux
FGS-02 | FGS-02 | PI07426 | Verified | FG Separator skid - JB separator to ground | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-11 | Brad Stanford | 2019-12-30 | Chris Boudreaux
FGS-02 | FGS-02 | PI07427 | Verified | FG Separator skid - pour seal at stub ups. Comm to advise | B | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-12-23 | Michael Law | 2020-01-08 | Mike Tabbert
FGS-02 | FGS-02 | PI07428 | Verified | FG Separator skid - torque the level gauges on the separators, all level switches | A | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-10-10 | Gonzalo Pena | 2019-11-04 | Albert Burge
FGS-02 | FGS-02 | PI07429 | Verified | EKC Heater Panel - remove shipping materials on panel, remove paper on flex glass | A | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-12-30 | Chris Boudreaux
FGS-02 | FGS-02 | PI07430 | Verified | EKC Heater Panel - ground the cable tray all the way | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FGS-02 | FGS-02 | PI07431 | Verified | EKC Heater Panel - ground the bushings and cable tray supports | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-25 | Mike Tabbert
FGS-02 | FGS-02 | PI07432 | Verified | EKC Heater Panel - support need to install on the cable tray, 90 bend to panel | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FGS-02 | FGS-02 | PI07433 | Verified | EKC Heater Panel - replace ground wire on the flex (EKC01AC103) wire too small | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-09 | Dustin Futrell | 2019-12-30 | Chris Boudreaux
FGS-02 | FGS-02 | PI07447 | Verified | 1B-FGS-PID-0002 AA701 and AA702 valves need to ground flex | B | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-11 | Brad Stanford | 2019-12-08 | John Sullivan
FGS-02 | FGS-02 | PI07448 | Verified | FG Heater and FG Dew point heater skids - 4 x 2" conduits at the tray need seal off | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FGS-02 | FGS-02 | PI07450 | Verified | General: Install all missing condulet covers | B | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
FGS-02 | FGS-02 | PI07452 | Verified | FG inlet filter - MBP01CP501 ground on flex, and the next 2 instruments | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-16 | Dustin Futrell | 2020-01-13 | Fred Michael
FGS-02 | FGS-02 | PI07453 | Verified | FGS-V-0280B valve not working, FGS-V-280C valve has a pinch point area, FGS-V-280A need to reach far to operate | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-28 | Albert Burge
FGS-02 | FGS-02 | PI07456 | Verified | FIT-8100 not installed | B | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-12-07 | Gonzalo Pena | 2019-12-20 | Albert Burge
FGS-02 | FGS-02 | PI07459 | Verified | MBP01AA711 FG emergency vent valve - Rotate 90 degree | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-28 | Albert Burge
FGS-02 | FGS-02 | PI07461 | Verified | EKC01AC102 drain missing on condulet on 2 LS-MBP01CL222 and 223 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-18 | Brad Stanford | 2019-10-28 | Albert Burge
FGS-02 | FGS-02 | PI07481 | Verified | Relief valve at duct burner skid missing rain flapper. | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-28 | Albert Burge
FGS-02 | FGS-02 | PI07717 | Verified | 1AFGSX0003, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
FGS-02 | FGS-02 | PI07718 | Verified | 1ACTSL0007A1, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-02 | Mike Tabbert
FGS-02 | FGS-02 | PI07719 | Verified | 1ACTSL0007A2, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-02 | FGS-02 | PI07720 | Verified | 1ACTSL0007A3, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-02 | FGS-02 | PI07721 | Verified | 1ACTSL0007B1, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-02 | FGS-02 | PI07722 | Verified | 1ACTSL0007B2, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-02 | FGS-02 | PI07723 | Verified | 1ACTSL0007B3, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-02 | FGS-02 | PI07724 | Verified | 1ACTSL0007C1, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-02 | FGS-02 | PI07725 | Verified | 1ACTSL0007C2, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-02 | FGS-02 | PI07726 | Verified | 1ACTSL0007C3, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-02 | FGS-02 | PI07727 | Verified | 1ACTSL0007G1, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-02 | FGS-02 | PI07728 | Verified | 1ACTSL0007G2, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-02 | FGS-02 | PI07729 | Verified | 1ACTSL0007G3, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-02 | FGS-02 | PI07730 | Verified | 1AFGSC0010, From Termination | B | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-11-04 | Dustin Futrell | 2019-12-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07731 | Verified | 1AFGSX0001, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
FGS-02 | FGS-02 | PI07732 | Verified | 1AFGSX0003, From Termination | B | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
FGS-02 | FGS-02 | PI07733 | Verified | 1AFGSX0004, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FGS-02 | FGS-02 | PI07734 | Verified | 1ACTSL0007A1, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07735 | Verified | 1ACTSL0007A2, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07736 | Verified | 1ACTSL0007A3, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07737 | Verified | 1ACTSL0007B1, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07738 | Verified | 1ACTSL0007B2, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07739 | Verified | 1ACTSL0007B3, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07740 | Verified | 1ACTSL0007C1, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07741 | Verified | 1ACTSL0007C2, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07742 | Verified | 1ACTSL0007C3, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07743 | Verified | 1ACTSL0007G1, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07744 | Verified | 1ACTSL0007G2, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07745 | Verified | 1ACTSL0007G3, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07746 | Verified | 1AFGSC0010, To Termination | B | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-11-04 | Dustin Futrell | 2019-12-14 | Mike Tabbert
FGS-02 | FGS-02 | PI07747 | Verified | 1AFGSX0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FGS-02 | FGS-02 | PI07748 | Verified | 1AFGSX0002, To Termination | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
FGS-02 | FGS-02 | PI07749 | Verified | 1AFGSX0003, To Termination | B | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
FGS-02 | FGS-02 | PI07750 | Verified | 1AFGSX0004, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FGS-02 | FGS-02 | PI07842 | Verified | 1A-FGS-PD-P40-0208-01 install ground plug at 1A-CTS-EKE01AT101/EKE01-102 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07843 | Verified | 1A-FGS-PD-P40-0208-01 install ground wire at 1A-CTS-EKE01AT101/EKE01-102 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07844 | Verified | On ISO 1A-FGS-PD-P40-0210-01 pipe support 1A-FGS-PD-HGR-0001 is not installed | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07845 | Verified | On ISO 1A-FGS-PD-P40-0210-01 pipe support 1A-FGS-PD-HGR-0004 roll shoe proper | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07846 | Verified | On ISO 1A-FGS-PD-P40-0210-01 missing 45 el on pipe spool 0210-4 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-03 | Damon Turner | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07847 | Verified | On ISO 1A-FGS-PD-P40-0210-02 install ground lug at 1A-FGS-V-0210 & 1A-FGS-PCV-0210 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07848 | Verified | On ISO 1A-FGS-PD-P40-0210-02 install ground wire at 1A-FGS-V-0210 & 1A-FGS-PCV-0210 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07849 | Verified | On ISO 1A-FGS-PD-P40-0210-03 connection to 1A-CTS-EKC01AC103/EKC01-101 has wrong gasket installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-03 | Damon Turner | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07850 | Verified | On ISO 1A-FGS-PD-P40-0210-03 install ground lug at 1A-FGS-V-0211 & 1A-CTS-EKC01AC103/EKC01-101 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07851 | Verified | On ISO 1A-FGS-PD-P40-0210-03 install ground wire at 1A-FGS-V-0211 & 1A-CTS-EKC01AC103/EKC01-101 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07852 | Verified | On ISO 1A-FGS-PD-P40-0220-01 connection to 1A-CTS-EKC01AC103/EKC01-103 has wrong gasket installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07853 | Verified | On ISO 1A-FGS-PD-P40-0220-01 connecting to 1A-CTS-MBP01CF001/TP-1AMBP01-101 missing 5 bolts | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07854 | Verified | On ISO 1A-FGS-PD-P40-0220-01 install FE after cleaning commissioning 1A-CTS-MBP01CF001 | B | P | William Mitchell | McD | 2019-09-28 | William Mitchell | Const | 2019-12-14 | Kelvin Cook | 2019-12-14 | Kelvin Cook
FGS-02 | FGS-02 | PI07855 | Verified | On ISO 1A-FGS-PD-P40-0220-01 install ground lug at 1A-FGS-V-0222 & 1A-FGS-V-0226A & 1A-FGS-V-0227 & 1A-CTS-MBP01CF001 & 1A-CTS-EKC01AC103/EKC01-102 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07856 | Verified | On ISO 1A-FGS-PD-P40-0220-01 install ground wire at 1A-FGS-V-0222 & 1A-FGS-V-0226A & 1A-FGS-V-0227 & 1A-CTS-MBP01CF001 & 1A-CTS-EKC01AC103/EKC01-102 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07857 | Verified | On ISO 1A-FGS-PD-P40-0225-01 missing 8 bolts at connection to 1A-CTS-MBP01CF001 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07858 | Verified | On ISO 1A-FGS-PD-P40-0225-01 Install Fe after commissioning completion cleaning | B | P | William Mitchell | McD | 2019-09-28 | William Mitchell | Const | 2019-12-07 | Michael Law | 2019-12-15 | Kelvin Cook
FGS-02 | FGS-02 | PI07859 | Verified | On ISO 1A-FGS-PD-P40-0225-01 Install ground lug at 1A-CTS-MBP01CF001 & 1A-FGS-V-0225A & 1A-CTS-MBP01AA701/TP-1AMBP01-103A | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07860 | Verified | On ISO 1A-FGS-PD-P40-0225-01 Install ground wire at 1A-CTS-MBP01CF001 & 1A-FGS-V-0225A & 1A-CTS-MBP01AA701/TP-1AMBP01-103A | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07861 | Verified | On ISO 1A-FGS-PD-P40-0227-01 install ground lug at 1A-FGS-V-0227 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07862 | Verified | On ISO 1A-FGS-PD-P40-0227-01 install ground wire at 1A-FGS-V-0227 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07863 | Verified | On ISO 1A-FGS-PD-P40-0227-01 remove values and cap per detail | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-10 | Kelvin Cook
FGS-02 | FGS-02 | PI07864 | Verified | On ISO 1A-FGS-PD-P40-0230-01 install ground lug 1A-CTS-MBP01AA702/ TP-1AMBP01-104A & 1A-CTS-MBP01AA701 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-09 | Bobby Williams | 2019-10-09 | Kelvin Cook
FGS-02 | FGS-02 | PI07865 | Verified | On ISO 1A-FGS-PD-P40-0230-01 install ground wire 1A-CTS-MBP01AA702/ TP-1AMBP01-104A & 1A-CTS-MBP01AA701 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07866 | Verified | On ISO 1A-FGS-PD-P40-0235-01 Rotate T to the north on 1A-FGS-TW-0235 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07867 | Verified | On ISO 1A-FGS-PD-P40-0235-01 install ground lug at 1A-CTS-EKC01AC101/102/ MBP01-105 & 1A-CTS-MBP01AA702 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07868 | Verified | On ISO 1A-FGS-PD-P40-0235-01 install ground wire at 1A-CTS-EKC01AC101/102/ MBP01-105 & 1A-CTS-MBP01AA702 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07869 | Verified | On ISO 1A-FGS-PD-P40-0236-01 install ground lug 1A-CTS-MBP01AA702 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07870 | Verified | On ISO 1A-FGS-PD-P40-0236-01 install ground wire 1A-CTS-MBP01AA702 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07871 | Verified | On ISO 1A-FGS-PD-P40-0236-02 remove plastic & tighten flange | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07872 | Verified | On ISO 1A-FGS-PD-P40-0236-02 install ground lug at 1A-FGS-FO-0236 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07873 | Verified | On ISO 1A-FGS-PD-P40-0236-02 install ground wire at 1A-FGS-FO-0236 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07874 | Verified | On ISO 1A-FGS-PD-P40-0236-02 Install FO after cleaning completion | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-12-06 | Bobby Williams | 2019-12-06 | Kelvin Cook
FGS-02 | FGS-02 | PI07875 | Verified | On ISO 1A-FGS-PD-P40-0242-01 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07876 | Verified | On ISO 1A-FGS-PD-P40-0242-01 install ground wire at 1A-FGS-T-0250/V | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07877 | Verified | On ISO 1A-FGS-PD-P40-0242-02 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07878 | Verified | On ISO 1A-FGS-PD-P40-0242-02 install ground wire at 1A-FGS-FA-0250 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07879 | Verified | On ISO 1A-FGS-PD-P40-0245-01 install ground lug at 1A-CTS-MBP01AA701 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07880 | Verified | On ISO 1A-FGS-PD-P40-0245-01 install ground wire at 1A-CTS-MBP01AA701 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07881 | Verified | On ISO 1A-FGS-PD-P40-0246-01 Install FO after cleaning completion | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-12-06 | Bobby Williams | 2019-12-06 | Kelvin Cook
FGS-02 | FGS-02 | PI07882 | Verified | On ISO 1A-FGS-PD-P40-0246-01 pipe support 1A-FGS-PD-HGR-0105 ubolt not installed | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07883 | Verified | On ISO 1A-FGS-PD-P40-0246-01 install ground lug at 1A-FGS-FO-0245 & 1A-CTS-MBP01AA711 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07884 | Verified | On ISO 1A-FGS-PD-P40-0246-01 install ground wire at 1A-FGS-FO-0245 & 1A-CTS-MBP01AA711 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07885 | Verified | On ISO 1A-FGS-PD-P40-0246-02 install bird screens | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07886 | Verified | On ISO 1A-FGS-PD-P40-0246-02 pipe support 1A-FGS-HGR-0128 has loose ubolt | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07887 | Verified | On ISO 1A-FGS-PD-P40-0246-02 pipe support 1A-FGS-HGR-0108 missing ubolt | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07888 | Verified | On ISO 1A-FGS-PD-P40-0246-03 pipe support 1A-FGS-HGR-0106 missing ubolt | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07889 | Verified | On ISO 1A-FGS-PD-P40-0246-03 install ground lug at 1A-FGS-SRV-0250 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07890 | Verified | On ISO 1A-FGS-PD-P40-0246-03 install ground wire at 1A-FGS-SRV-0250 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07891 | Verified | On ISO 1A-FGS-PD-P40-0250-01 connection to 1A-CTS-EKC01AC101/102/MBP01-107 missing bolts | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07892 | Verified | On ISO 1A-FGS-PD-P40-0250-01 install ground lug at 1A-CTS-EKC01AC101/102/MBP01-107 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Brad Stanford | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07893 | Verified | On ISO 1A-FGS-PD-P40-0250-01 install ground wire at 1A-CTS-EKC01AC101/102/MBP01-107 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07894 | Verified | On ISO 1A-FGS-PD-P40-0250-01 pipe support 1A-FGS-PD-HGR-0098 needs to have nuts to lock at eye bolt and turnbuckle | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07895 | Verified | On ISO 1A-FGS-PD-P40-0250-02 pipe support 1A-FGS-PD-HGR-0101 set spring can on cold setting after degrease | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07896 | Verified | On ISO 1A-FGS-PD-P40-0250-02 connection to 1A-CTS-EKE01BB101/MBP01-117 has loose bolts | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07897 | Verified | On ISO 1A-FGS-PD-P40-0250-02 install ground lug 1A-CTS-EKE01BB101/MBP01-117 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07898 | Verified | On ISO 1A-FGS-PD-P40-0250-02 install ground wire 1A-CTS-EKE01BB101/MBP01-117 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07899 | Verified | On ISO 1A-FGS-PD-P40-0260-01 pipe support 1A-FGS-PD-HGR-0080 roll shoe proper and add shim as needed | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07900 | Verified | On ISO 1A-FGS-PD-P40-0260-01 at field weld 5 remove valve and add plug and seal weld | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07901 | Verified | On ISO 1A-FGS-PD-P40-0260-02 valve 1A-FGS-V-0260 mising handwheel | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07902 | Verified | On ISO 1A-FGS-PD-P40-0260-02 install ground lug at 1A-FGS-V-0260 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07903 | Verified | On ISO 1A-FGS-PD-P40-0260-02 install ground wire at 1A-FGS-V-0260 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07904 | Verified | On ISO 1A-FGS-PD-P40-0260-02 flanges connecting valve 1A-FGS-V-0260 mising 8 cap screws | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07905 | Verified | On ISO 1A-FGS-PD-P40-0260-02 pipe support 1A-FGS-PD-HGR-0015 remove dunnage & install support/shim | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07906 | Verified | On ISO 1A-FGS-PD-P40-0260-02 pipe support 1A-FGS-PD-HGR-0014 plumb up support | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07907 | Verified | On ISO 1A-FGS-PD-P40-0265-01 valve 1A-FGS-V-0263 missing handwheel | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07908 | Verified | On ISO 1A-FGS-PD-P40-0265-01 install ground lug at 1A-FGS-V-0263 & 1A-FGS-PCV-0260A | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07909 | Verified | On ISO 1A-FGS-PD-P40-0265-01 install ground wire at 1A-FGS-V-0263 & 1A-FGS-PCV-0260A | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07910 | Verified | On ISO 1A-FGS-PD-P40-0265-01 flanges connecting valve 1A-FGS-V-0263 mising 16 cap screws | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07911 | Verified | On ISO 1A-FGS-PD-P40-0265-01 flanges connecting valve 1A-FGS-V-0263 mising 16 cap screws | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-09 | Michael Law
FGS-02 | FGS-02 | PI07912 | Verified | On ISO 1A-FGS-PD-P40-0265-02 valve 1A-FGS-V-0264 mising handwheel | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07913 | Verified | On ISO 1A-FGS-PD-P40-0265-02 install ground lug at 1A-FGS-PCV-0260A & 1A-FGS-V-0264 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07914 | Verified | On ISO 1A-FGS-PD-P40-0265-02 install ground wire at 1A-FGS-PCV-0260A & 1A-FGS-V-0264 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-18 | Brad Stanford | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07915 | Verified | On ISO 1A-FGS-PD-P40-0270-01 install 1A-FGS-FE-8100 after cleaning by comm | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-12-05 | Bobby Williams | 2019-12-06 | Kelvin Cook
FGS-02 | FGS-02 | PI07916 | Verified | On ISO 1A-FGS-PD-P40-0270-01 install ground lug at 1A-FGS-V-0264 & 1A-FGS-SRV-0270 & 1A-FGS-FE-0100 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07917 | Verified | On ISO 1A-FGS-PD-P40-0270-01 install ground wire at 1A-FGS-V-0264 & 1A-FGS-SRV-0270 & 1A-FGS-FE-0100 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07918 | Verified | On ISO 1A-FGS-PD-P40-0271-01 flange connecting to 1A-FGS-SRV-0270 is missing all bolts | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07919 | Verified | On ISO 1A-FGS-PD-P40-0271-01 install ground lug at 1A-FGS-SRV-0270 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07920 | Verified | On ISO 1A-FGS-PD-P40-0271-01 install ground wire at 1A-FGS-SRV-0270 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07921 | Verified | On ISO 1A-FGS-PD-P40-0271-01 pipe support 1A-FGS-PD-HGR-0024 shim & install ubolt | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07922 | Verified | On ISO 1A-FGS-PD-P40-0271-01 pipe support 1A-FGS-PD-HGR-0023 install ubolt | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07923 | Verified | On ISO 1A-FGS-PD-P40-0271-01 install 1A-FGS-RC-0271 | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07924 | Verified | On ISO 1A-FGS-PD-P40-0275-01 remove detail H. install plug or cap | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07925 | Verified | On ISO 1A-FGS-PD-P40-0275-01 install ground lug at flange connection | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07926 | Verified | On ISO 1A-FGS-PD-P40-0275-01 install ground wire at flange connection | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07927 | Verified | On ISO 1A-FGS-PD-P40-0310-01 pipe support 1A-FGS-PD-HGR-0055 set spring can to cold setting | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07928 | Verified | On ISO 1A-FGS-PD-P40-0310-01 install ground lug 1A-CTS-EKE01BB101/MBP-01-118 & 1A-CTS-MBP01AT101/MBP01-110 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07929 | Verified | On ISO 1A-FGS-PD-P40-0310-01 install ground wire 1A-CTS-EKE01BB101/MBP-01-118 & 1A-CTS-MBP01AT101/MBP01-110 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07930 | Verified | On ISO 1A-FGS-PD-P40-0310-01 connection to 1A-CTS-EKE01BB101/MBP-01-118 has the wrong gasket installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07931 | Verified | On ISO 1A-FGS-PD-P40-0320-01 connection to 1A-CTS-MBP01AT101/MBP01-111 has the wrong gasket installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07932 | Verified | On ISO 1A-FGS-PD-P40-0320-01 install ground lug at 1A-CTS-MBP01AT101/MBP01-111 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07933 | Verified | On ISO 1A-FGS-PD-P40-0320-01 install ground wire at 1A-CTS-MBP01AT101/MBP01-111 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07934 | Verified | On ISO 1A-FGS-PD-P40-0320-01 replace CS nipple with SS nipple on Instrument 1A-FGS-TW-1AMBP01CT026 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07935 | Verified | On ISO 1A-FGS-PD-P40-0320-01 pipe support 1A-FGS-PD-HGR-0058 install ss wrap proper and install hose clamps | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07936 | Verified | On ISO 1A-FGS-PD-P40-0320-01 pipe support 1A-FGS-PD-HGR-0059 install hose clamps | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07937 | Verified | On ISO 1A-FGS-PD-P40-0320-02 pipe support 1A-FGS-PD-HGR-0060 install ss wrap proper with hose clamps | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07938 | Verified | On ISO 1A-FGS-PD-P40-0320-02 install ground lugs on spool 0320-1 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07939 | Verified | On ISO 1A-FGS-PD-P40-0320-02 install ground wire on spool 0320-1 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07940 | Verified | On ISO 1A-FGS-PD-P41-0210-01 spool 0210-2 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07941 | Verified | On ISO 1A-FGS-PD-P41-0210-01 pipe support 1A-FGS-PD-HGR-0160 missing bolts to pipe shoe support | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07942 | Verified | On ISO 1A-FGS-PD-P41-0210-02 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07943 | Verified | On ISO 1A-FGS-PD-P41-0220-01 pipe supports 1A-FGS-PD-HGR-0169 & 0173 & 0172 has loose bolts | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07944 | Verified | On ISO 1A-FGS-PD-P41-0220-01 remove wood and install proper steel 1.5 channel iron at pipe support 1A-FGS-PD-HGR-0165 | B | P | Kelvin Cook | McD | 2019-09-28 | Kelvin Cook | Const |  |  | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07945 | Verified | On ISO 1A-FGS-PD-P41-0220-01 pipe supports 1A-FGS-PD-HGR-0170 is not installed | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07946 | Verified | On ISO 1A-FGS-PD-P41-0220-01 pipe supports 1A-FGS-PD-HGR-0171 set shoe to center line on support | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07947 | Verified | On ISO 1A-FGS-PD-P41-0220-01 install bird screent at vent | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07948 | Verified | On ISO 1A-FGS-PD-P41-0220-01 pipe support 1A-FGS-PD-HGR-0167 needs to have a second set of nuts | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07949 | Verified | On ISO 1A-FGS-PD-P41-0220-03 install bird screent at vent | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07950 | Verified | On ISO 1A-FGS-PD-P41-0220-03 pipe supports 1A-FGS-PD-HGR-0192 & 0193 & 0194 has loose bolts | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07951 | Verified | On ISO 1A-FGS-PD-P41-0220-03 pipe supports 1A-FGS-PD-HGR-0191 set shoe proper center line of support | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07952 | Verified | On ISO 1A-FGS-PD-P41-0220-03 pipe supports 1A-FGS-PD-HGR-0190 is not installed | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07953 | Verified | On ISO 1A-FGS-PD-P41-0220-03 pipe supports 1A-FGS-PD-HGR-0187 second set of nuts required | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07954 | Verified | On ISO 1A-FGS-PD-P41-0220-03 pipe supports 1A-FGS-PD-HGR-0186 missing 2 bolt clamps | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07955 | Verified | On ISO 1A-FGS-PD-P41-0220-03 rotate valves handles to be operator friendly | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07956 | Verified | On ISO 1A-FGS-PD-P41-0220-03 threaded cap is not install on valve 1A-FGS-V-0220B | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07957 | Verified | On ISO 1A-FGS-PD-P41-0225-01 pipe supports 1A-FGS-PD-HGR-0234 & 0235 & 0236 have loose ubolts | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07958 | Verified | On ISO 1A-FGS-PD-P41-0225-01 pipe supports 1A-FGS-PD-HGR-0234 & 0235 & 0236 requires double nuts | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07959 | Verified | On ISO 1A-FGS-PD-P41-0225-01 pipe supports 1A-FGS-PD-HGR-0232 & 0233 have loose clamps | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07960 | Verified | On ISO 1A-FGS-PD-P41-0225-01 rotate valve handles to be operator friendly | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07961 | Verified | On ISO 1A-FGS-PD-P41-0225-02 pipe supports 1A-FGS-PD-HGR-0222 & 0221 & 0220 have loose ubolts | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07962 | Verified | On ISO 1A-FGS-PD-P41-0225-02 pipe supports 1A-FGS-PD-HGR-0222 & 0221 & 0220 second set of nuts required | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07963 | Verified | On ISO 1A-FGS-PD-P41-0225-02 pipe supports 1A-FGS-PD-HGR-0217 & 0218 have loose clamps | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07964 | Verified | On ISO 1A-FGS-PD-P41-0225-02 rotate valve 1A-FGS-V-00224A handle to be operator friendly | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07965 | Verified | On ISO 1A-FGS-PD-P41-0225-03 install bird screen | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07966 | Verified | On ISO 1A-FGS-PD-P41-0225-03 pipe supports 1A-FGS-PD-HGR-0241 & 0242 & 0243 have loose ubolts | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07967 | Verified | On ISO 1A-FGS-PD-P41-0225-03 pipe supports 1A-FGS-PD-HGR-0241 & 0242 & 0243 double nuts required | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07968 | Verified | On ISO 1A-FGS-PD-P41-0225-03 pipe supports 1A-FGS-PD-HGR-0237 & 0238 & 0239 set shoe on center line of support | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07969 | Verified | On ISO 1A-FGS-PD-P41-0225-04 install bird screen | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07970 | Verified | On ISO 1A-FGS-PD-P41-0225-04 pipe supports 1A-FGS-PD-HGR-0227 & 0228 & 0229 have loose ubolts | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07971 | Verified | On ISO 1A-FGS-PD-P41-0225-04 pipe supports 1A-FGS-PD-HGR-0227 & 0228 & 0229 need second set of nuts | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07972 | Verified | On ISO 1A-FGS-PD-P41-0225-04 pipe supports 1A-FGS-PD-HGR-0223 & 0224 & 0225 verify 2 bolt clamps are tight and all shoe are on center line on support | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07973 | Verified | On ISO 1A-FGS-PD-P41-0230-01 pipe supports 1A-FGS-PD-HGR-0206 & 0207 & 0208 have loose ubolts | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07974 | Verified | On ISO 1A-FGS-PD-P41-0230-01 pipe supports 1A-FGS-PD-HGR-0203 & 0204 loose 2 bolt clamps | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07975 | Verified | On ISO 1A-FGS-PD-P41-0230-01 pipe supports 1A-FGS-PD-HGR-0205 set shoe on center line of support | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07976 | Verified | On ISO 1A-FGS-PD-P41-0230-01 rotate valve 1A-FGS-V-00230A handle to be operator friendly | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07977 | Verified | On ISO 1A-FGS-PD-P41-0230-01 threaded cap is not install on valve 1A-FGS-V-0230B | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07978 | Verified | On ISO 1A-FGS-PD-P41-0230-02 install bird screen | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07979 | Verified | On ISO 1A-FGS-PD-P41-0230-02 pipe support 1A-FGS-PD-HGR-0213 & 0214 & 0215 need to tighen all ubolts as an anchor | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07980 | Verified | On ISO 1A-FGS-PD-P41-0230-02 pipe support 1A-FGS-PD-HGR-0209 & 0211 set shoe on center line of support | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07981 | Verified | On ISO 1A-FGS-PD-P41-0235-01 pipe support 1A-FGS-PD-HGR-0351 is not installed | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07982 | Verified | On ISO 1A-FGS-PD-P41-0235-01 pipe support 1A-FGS-PD-HGR-0352 install shim as needed | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07983 | Verified | On ISO 1A-FGS-PD-P41-0235-01 pipe support 1A-FGS-PD-HGR-0353 & 0354 & 0355 & 0356 set shoe on center line of support | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07984 | Verified | On ISO 1A-FGS-PD-P41-0235-01 pipe support 1A-FGS-PD-HGR-0353 & 0357 & 0358 have loose ubolts | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07985 | Verified | On ISO 1A-FGS-PD-P41-0235-01 threaded cap is not install on valve 1A-FGS-V-0235B | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07986 | Verified | On ISO 1A-FGS-PD-P41-0235-02 install bird screen | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07987 | Verified | On ISO 1A-FGS-PD-P41-0235-02 pipe supports 1A-FGS-PD-HGR-0363 & 0364 & 0365 have loose ubolts | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07988 | Verified | On ISO 1A-FGS-PD-P41-0235-02 pipe supports 1A-FGS-PD-HGR-0363 & 0364 & 0365 second set of nuts required | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07989 | Verified | On ISO 1A-FGS-PD-P41-0235-02 pipe supports 1A-FGS-PD-HGR-0359 set shoe center line of support | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07990 | Verified | ISO 1A-FGS-PD-P41-0250-01 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07991 | Verified | ISO 1A-FGS-PD-P41-0250-01 install ground lug at 1A-FGS-SRV-0250 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07992 | Verified | ISO 1A-FGS-PD-P41-0250-01 install ground wire at 1A-FGS-SRV-0250 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07993 | Verified | On ISO 1A-FGS-PD-P41-0260-01 install bird screen | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07994 | Verified | On ISO 1A-FGS-PD-P41-0260-01 rotate valve 1A-FGS-V-0261B & 0261C handle to be operator friendly | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07995 | Verified | ISO 1A-FGS-PD-P41-0260-02 is not installed | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI07996 | Verified | On ISO 1A-FGS-PD-P41-0265-01 pipe support 1A-FGS-PD-HGR-0135 missing ubolt | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07997 | Verified | On ISO 1A-FGS-PD-P41-0265-01 missing gaskets for flanges connecting to 1A-FGS-PCV-0260B | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07998 | Verified | On ISO 1A-FGS-PD-P41-0265-01 install ground plug at 1A-FGS-PCV-0260B | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI07999 | Verified | On ISO 1A-FGS-PD-P41-0265-01 install ground wire at 1A-FGS-PCV-0260B | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08000 | Verified | On ISO 1A-FGS-PD-P41-0270-02 instrument 1A-FGS-PP-0270 is not installed | B | I | Gonzalo Pena | McD | 2019-09-28 | Gonzalo Pena | Const |  |  | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08001 | Verified | On ISO 1A-FGS-PD-P41-0270-03 install bird screen | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08002 | Verified | On ISO 1A-FGS-PD-P41-0270-03 rotate valve handles to be operator friendly | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08003 | Verified | On ISO 1A-FGS-PD-P41-0270-03 threaded cap is not install on valve 1A-FGS-V-0280B | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08004 | Verified | On ISO 1A-FGS-PD-P41-0310-01 threaded cap is not install on valve 1A-FGS-V-0310B | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08005 | Verified | On ISO 1A-FGS-PD-P41-0310-01 pipe supports 1A-FGS-PD-HGR-0404 & 0405 & 0406 set shoe center line of support | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08006 | Verified | On ISO 1A-FGS-PD-P41-0310-02 install bird screen | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08007 | Verified | On ISO 1A-FGS-PD-P41-0310-02 pipe supports 1A-FGS-PD-HGR-0411 & 0412 has loose bolts and requires second set of bolts | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08008 | Verified | On ISO 1A-FGS-PD-P41-0310-02 pipe supports 1A-FGS-PD-HGR-0409 is not installed | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08009 | Verified | On ISO 1A-FGS-PD-P41-0310-02 pipe supports 1A-FGS-PD-HGR-0407 & 0408 & 0410 set shoe center line of support | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08010 | Verified | On ISO 1A-FGS-PD-P41-0320-04 spool 0320-2 & 0320-3 & 0320-4 are not installed | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08011 | Verified | On ISO 1A-FGS-PD-P41-0320-04 pipe supports 1A-FGS-PD-HGR-0487 is not installed | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08012 | Verified | On ISO 1A-FGS-PD-P41-0320-04 pipe supports 1A-FGS-PD-HGR-0487 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08013 | Verified | ISO 1A-FGS-PD-P40-0242-01 is not installed - duplicate of PI07875 | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-03 | Eric Policarpio
FGS-02 | FGS-02 | PI08014 | Verified | ISO 1A-FGS-PD-P40-0242-02 is not installed - duplicate of PI07877 | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-03 | Eric Policarpio
FGS-02 | FGS-02 | PI08015 | Verified | ISO 1A-FGS-PD-P40-0246-03 verify gap at bottom of pipe & support | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08016 | Verified | ISO 1A-FGS-PD-P40-0246-03 pipe support 1A-FGS-PD-HGR-0106 ubolt or not - duplicate of PI07888 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-03 | Eric Policarpio
FGS-02 | FGS-02 | PI08017 | Verified | ISO 1A-FGS-PD-P41-0201-01 install bird screen | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08018 | Verified | ISO 1A-FGS-PD-P41-0201-01 install ground lug at 1A-CTS-EKE01AT101/EKE01-104 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08019 | Verified | ISO 1A-FGS-PD-P41-0201-01 install ground wire at 1A-CTS-EKE01AT101/EKE01-104 | A | P | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08020 | Verified | ISO 1A-FGS-PD-P41-0202-01 install bird screen | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08021 | Verified | ISO 1A-FGS-PD-P41-0202-01 install ground lug at 1A-CTS-EKE01AT101/EKE01-105 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08022 | Verified | ISO 1A-FGS-PD-P41-0202-01 install ground wire at 1A-CTS-EKE01AT101/EKE01-105 | A | P | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-16 | Kelvin Cook
FGS-02 | FGS-02 | PI08023 | Verified | ISO 1A-FGS-PD-P41-0205-01 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08024 | Verified | ISO 1A-FGS-PD-P41-0205-01 install ground lug at 1A-CTS-EKE01AT101/EKE01-103 & 10-FGS-T-0205/A3 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-16 | Kelvin Cook
FGS-02 | FGS-02 | PI08025 | Verified | ISO 1A-FGS-PD-P41-0205-01 install ground wire at 1A-CTS-EKE01AT101/EKE01-103 & 10-FGS-T-0205/A3 | A | P | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08026 | Verified | ISO 1A-FGS-PD-P41-0210-03 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08027 | Verified | ISO 1A-FGS-PD-P41-0211-01 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08028 | Verified | ISO ISO 1A-FGS-PD-P41-0212-01 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08029 | Verified | ISO 1A-FGS-PD-P41-0212-01 install ground lug at 1A-CTS-EKC01AC103/EKC01-103 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-16 | Kelvin Cook
FGS-02 | FGS-02 | PI08030 | Verified | ISO 1A-FGS-PD-P41-0212-01 install ground wire at 1A-CTS-EKC01AC103/EKC01-103 | A | P | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-16 | Kelvin Cook
FGS-02 | FGS-02 | PI08031 | Verified | ISO 1A-FGS-PD-P41-0215-01 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08032 | Verified | ISO 1A-FGS-PD-P41-0215-01 install ground lug at 1A-FGS-T-0250/L2 & 1A-CTS-EKC01AC103/EKC01-104 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08033 | Verified | ISO 1A-FGS-PD-P41-0215-01 install ground wire at 1A-FGS-T-0250/L2 & 1A-CTS-EKC01AC103/EKC01-104 | A | P | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08034 | Verified | ISO 1A-FGS-PD-P41-0238-01 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08035 | Verified | ISO 1A-FGS-PD-P41-0238-01 install ground lug at 1A-CTS-EKC01AC101/102/ MBP01-106 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08036 | Verified | ISO 1A-FGS-PD-P41-0238-01 install ground wire at 1A-CTS-EKC01AC101/102/ MBP01-106 | A | P | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08037 | Verified | ISO 1A-FGS-PD-P41-0239-01 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08038 | Verified | ISO 1A-FGS-PD-P41-0239-01 installed ground lug at 1A-CTS-EKC01AC101/102/MBP01-106 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-16 | Kelvin Cook
FGS-02 | FGS-02 | PI08039 | Verified | ISO 1A-FGS-PD-P41-0239-01 installed ground wire at 1A-CTS-EKC01AC101/102/MBP01-106 | A | P | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-16 | Kelvin Cook
FGS-02 | FGS-02 | PI08040 | Verified | ISO 1A-FGS-PD-P41-0240-01 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08041 | Verified | ISO 1A-FGS-PD-P41-0240-01 install ground lug at 1A-FGS-T-0250/A1 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08042 | Verified | ISO 1A-FGS-PD-P41-0240-01 install ground wire at 1A-FGS-T-0250/A1 | A | P | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08043 | Verified | ISO 1A-FGS-PD-P41-0241-01 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08044 | Verified | ISO 1A-FGS-PD-P41-0241-01 install ground lug at 1A-FGS-T-0250/A2 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08045 | Verified | ISO 1A-FGS-PD-P41-0241-01 install ground wire at 1A-FGS-T-0250/A2 | A | P | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08046 | Verified | ISO 1A-FGS-PD-P41-0285-01 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08047 | Verified | ISO 1A-FGS-PD-P41-0285-01 install ground lug at 1A-FGS-T-0250/B1 & Pump out connection | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08048 | Verified | ISO 1A-FGS-PD-P41-0285-01 install ground wire at 1A-FGS-T-0250/B1 & Pump out connection | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08049 | Verified | ISO 1A-FGS-PD-P41-0300-01 spool 0300-2 is not installed | B | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08050 | Verified | ISO 1A-FGS-PD-P41-0300-01 pipe support 1A-FGS-PD-HGR-0381 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08051 | Verified | ISO 1A-FGS-PD-P41-0300-01 anti seize botls at the connection to 1A-CTS-EKE01BB101 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08052 | Verified | ISO 1A-FGS-PD-P41-0300-01 install ground lug at 1A-CTS-EKE01BB101/EKE01-128 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08053 | Verified | ISO 1A-FGS-PD-P41-0300-01 install ground wire at 1A-CTS-EKE01BB101/EKE01-128 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08054 | Verified | ISO 1A-FGS-PD-P41-0300-02 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08055 | Verified | ISO 1A-FGS-PD-P41-0301-01 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08056 | Verified | ISO 1A-FGS-PD-P41-0301-01 install ground lug at 1A-CTS-EKE01BB101/EKE01-119 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08057 | Verified | ISO 1A-FGS-PD-P41-0301-01 install ground wire at 1A-CTS-EKE01BB101/EKE01-119 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08058 | Verified | ISO 1A-FGS-PD-P41-0301-02 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08059 | Verified | ISO 1A-FGS-PD-P41-0301-02 install ground lug at 1A-FGS-T-0250/A3 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08060 | Verified | ISO 1A-FGS-PD-P41-0301-02 install ground wire at 1A-FGS-T-0250/A3 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-16 | Kelvin Cook
FGS-02 | FGS-02 | PI08061 | Verified | ISO 1A-FGS-PD-P41-0302-01 is not installed | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI08062 | Verified | ISO 1A-FGS-PD-P41-0302-01 install ground lug at 1A-CTS-EKE01BB101/QJA01-101 | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI08063 | Verified | ISO 1A-FGS-PD-P41-0302-01 install ground wire at 1A-CTS-EKE01BB101/QJA01-101 | A | E | Dustin Futrell | McD | 2019-09-28 | Dustin Futrell | Const |  |  | 2019-10-12 | Kelvin Cook
FGS-02 | FGS-02 | PI09318 | Verified | Test Package FGS-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const | 2019-10-22 | Kelvin Cook | 2019-10-22 | Kelvin Cook
FGS-02 | FGS-02 | PI09319 | Verified | Test Package FGS-T-02 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-15 | Kelvin Cook
FGS-02 | FGS-02 | PI09320 | Verified | Test Package FGS-T-03 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-18 | Kelvin Cook
FGS-02 | FGS-02 | PI09321 | Verified | Test Package FGS-T-04 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-15 | Kelvin Cook
FGS-02 | FGS-02 | PI09322 | Verified | Test Package FGS-T-05 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const | 2019-10-22 | Kelvin Cook | 2019-10-22 | Kelvin Cook
FGS-02 | FGS-02 | PI09323 | Verified | Test Package FGS-T-06 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-18 | Kelvin Cook
FGS-02 | FGS-02 | PI09324 | Verified | Test Package FGS-T-07 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-18 | Kelvin Cook
FGS-02 | FGS-02 | PI09325 | Verified | Test Package FGS-T-08 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-18 | Kelvin Cook
FGS-02 | FGS-02 | PI09326 | Verified | Test Package FGS-T-09 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-15 | Kelvin Cook
FGS-02 | FGS-02 | PI09327 | Verified | Test Package FGS-T-10 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-18 | Kelvin Cook
FGS-02 | FGS-02 | PI09328 | Verified | Test Package FGS-T-11 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI09329 | Verified | Test Package FGS-T-12 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI09330 | Verified | Test Package FGS-T-13 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-19 | Kelvin Cook
FGS-02 | FGS-02 | PI09331 | Verified | Test Package FGS-T-14 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-15 | Kelvin Cook
FGS-02 | FGS-02 | PI09332 | Verified | Test Package FGS-T-15 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-15 | Kelvin Cook
FGS-02 | FGS-02 | PI09333 | Verified | Test Package FGS-T-16 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-15 | Kelvin Cook
FGS-02 | FGS-02 | PI09348 | Verified | LK-1A-FGS-PD-P41-0210-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-15 | Tom Noble
FGS-02 | FGS-02 | PI09349 | Verified | LK-1A-FGS-PD-P41-0210-02 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-15 | Tom Noble
FGS-02 | FGS-02 | PI09350 | Verified | LK-1A-FGS-PD-P41-0210-03 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-15 | Tom Noble
FGS-02 | FGS-02 | PI09351 | Verified | LK-1A-FGS-PD-P41-0215-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const |  |  | 2019-10-10 | Tom Noble
FGS-02 | FGS-02 | PI09352 | Verified | LK-1A-FGS-PD-P41-0250-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const |  |  | 2019-10-10 | Tom Noble
FGS-02 | FGS-02 | PI09353 | Verified | LK-1A-FGS-PD-P41-0301-02 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const |  |  | 2019-10-10 | Tom Noble
FGS-02 | FGS-02 | PI09354 | Verified | LK-1A-FGS-PD-P41-0310-02 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-16 | Tom Noble
FGS-02 | FGS-02 | PI09345 | Verified | LK-1A-FGS-PD-P41-0286-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const |  |  | 2019-10-29 | Tom Noble
FGS-02 | FGS-02 | PI09346 | Verified | LK-1A-FGS-PD-P41-0300-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-15 | Tom Noble
FGS-02 | FGS-02 | PI09347 | Verified | LK-1A-FGS-PD-P41-0300-02 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-15 | Tom Noble
FGS-02 | FGS-02 | PI10246 | Verified | Install 1A-FGS-LSH-0221 | B | I | Gonzalo Pena | McD | 2019-10-23 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2019-11-23 | Michael Law
FGS-02 | FGS-02 | PI12711 | Verified | 1A-FGS-TI-0220 not installed. | B | I | Gonzalo Pena | McD | 2019-11-02 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-12-13 | Gonzalo Pena
FGS-02 | FGS-02 | PI15688 | Verified | Red line LK-1A-FGS-ME-PID-0001; Piping & Instrumentation Diagram Fuel Gas System to indicate 1A-FGS-FIT-8100; Duct Burner Supply Pressure Transmitter | C | P | Charles Worthington | McD | 2020-01-09 | Charles Worthington | Comm | 2020-04-28 | Charles Worthington | 2020-06-16 | Dave Goldak
FGS-02 | FGS-02 | PI15689 | Verified | Dew Point Heater Unit valves 1A-EKC01AA904, 1A-EKC01AA905, 1A-EKC01AA906, 1A-EKC01AA907 are inaccessible | D | P | Michael Law | McD | 2020-01-09 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-08-20 | Nelson Eichelberger
FGS-02 | FGS-02 | PI15690 | Verified | Verify that no supports are required on vertical Fuel Gas 12" piping from first above ground flange to horizontal turn at pipe rack, Line No. 12-1A-FGS-0210 | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm |  |  | 2020-01-10 | Michael Law
FGS-02 | FGS-02 | PI15691 | Verified | 1A-FGS-V-0209C; FG Header Vent Valve, 1" line needs additional support | D | P | Michael Law | McD | 2020-01-09 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-08-20 | Nelson Eichelberger
FGS-02 | FGS-02 | PI15692 | Verified | 1A-FGS-V-0209B; FG Header Nitrogen Purge Valve needs cap | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-05-12 | James Beech | 2020-06-16 | Dave Goldak
FGS-02 | FGS-02 | PI15693 | Verified | 1A-FGS-V-0209B/C: FG Header Vent Valve and 1" line needs to be painted yellow | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-04-07 | Randy Carpenter
FGS-02 | FGS-02 | PI15694 | Verified | 1A-FGS-V-0209C; FG Header Vent needs bird screen | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-02-11 | Charlie English | 2020-02-15 | Shannon Scott
FGS-02 | FGS-02 | PI15695 | Verified | Clean all rusty bolts throughout sub system and apply protective coating | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-03-20 | Jerry Smith | 2020-04-06 | Bernard Stasse
FGS-02 | FGS-02 | PI15696 | Verified | Finish painting throughout sub system | C | X | Johnny Campbell | McD | 2020-01-09 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
FGS-02 | FGS-02 | PI15697 | Verified | Vertical pipe support baseplate anchor nuts loose, downstream of 1A-FGS-PCV-0210; Fuel Gas Pressure Control Valve | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-01-15 | Bobby Williams | 2020-01-22 | Shannon Scott
FGS-02 | FGS-02 | PI15698 | Verified | 1A-FGS-V-0210B; Fuel Gas Header Nitrogen Purge Valve 1" line needs additional support | D | P | Michael Law | McD | 2020-01-09 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-07-10 | Dave Goldak
FGS-02 | FGS-02 | PI15699 | Verified | Remove test gauge from 1A-FGS-V-0210B; Fuel Gas Header Nitrogen Purge Valve | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-05-08 | Michael Law | 2020-05-08 | Michael Law
FGS-02 | FGS-02 | PI15700 | Verified | Install cap at 1A-FGS-V-0210B; Fuel Gas Header Nitrogen Purge Valve | D | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-22 | Shannon Scott
FGS-02 | FGS-02 | PI15701 | Verified | Resurface 1A Fuel Gas Dew Point Heater concrete pad foundation | C | C | Alan Huntsman | McD | 2020-01-09 | Alan Huntsman | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15702 | Verified | Clean up 1A Fuel Gas Dew Point Heater skid | C | C | Johnny Campbell | McD | 2020-01-09 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-04-07 | Randy Carpenter
FGS-02 | FGS-02 | PI15703 | Verified | Fuel Gas Dew Point Heater control panel needs phenolic label | C | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm |  |  | 2020-02-11 | Mike Tabbert
FGS-02 | FGS-02 | PI15704 | Verified | Fuel Gas Dew Point Heater control panel is missing screws on doors | C | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15705 | Verified | Clean off carbon contamination at Fuel Gas Dew Point Heater control panel | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-04-06 | Bernard Stasse
FGS-02 | FGS-02 | PI15706 | Verified | Fuel Gas Dew Point Heater control panel pressure gauge is pegged out - not in range | C | I | Albert Burge | McD | 2020-01-09 | Albert Burge | Comm |  |  | 2020-01-22 | Albert Burge
FGS-02 | FGS-02 | PI15707 | Verified | Entergy to inspect interior of Fuel Gas Dew Point Heater control panel during outage | C | P | Shannon Scott | McD | 2020-01-09 | Shannon Scott | Comm |  |  | 2020-02-02 | Shannon Scott
FGS-02 | FGS-02 | PI15708 | Verified | Remove temporary fitting from 1A-FGS-V-0227B; Nitrogen Purge Valve and install cap | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-05-08 | Michael Law | 2020-05-08 | Michael Law
FGS-02 | FGS-02 | PI15709 | Verified | 1A-FGS-V-0223C; Fuel Gas Header Vent Valve 1" line needs additional support | D | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-03-10 | John Watts
FGS-02 | FGS-02 | PI15710 | Verified | Complete insulation at 1A-FGS-V-0223C; Fuel Gas Header Vent Valve 1" line | C | Q | Sheri Fritz | PCI | 2020-01-09 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-06-16 | Dave Goldak
FGS-02 | FGS-02 | PI15711 | Verified | Repair broken flex conduit connection and replace seal at 1A-CTS-MBP01AA701; 1A GT Fuel Gas Emergency Shutoff Valve | D | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-15 | Shannon Scott
FGS-02 | FGS-02 | PI15712 | Verified | Reroute flex conduit under 1A-CTS-MBP01AA701; 1A GT Fuel Gas Emergency Shutoff Valve, currently routed over top of valve | D | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-15 | Shannon Scott
FGS-02 | FGS-02 | PI15713 | Verified | Repair and terminate disconnected cable at 1A-CTS-MBP01AA702; 1A GT Temperature Control Valve | B | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm |  |  | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15714 | Verified | Insulate 2" drain line from 1A Fuel Gas Dew Point Heater to 1A Fuel Gas Drains Tank | C | Q | Richard McSpadden | PCI | 2020-01-09 | Richard McSpadden | Comm | 2020-07-27 | Eric Policarpio | 2020-07-27 | Dave Goldak
FGS-02 | FGS-02 | PI15715 | Verified | Insulate 1" drain line from 1A Fuel Gas Scrubber to 1A Fuel Gas Drains Tank | C | Q | Sheri Fritz | PCI | 2020-01-09 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-06-16 | Dave Goldak
FGS-02 | FGS-02 | PI15716 | Verified | LK-1A-FGS-ME-PID-0002; Piping and Instrumentation Diagram Fuel Gas System indicates two Level Indicators (1A-FGS-LI-0220) at 1A Fuel Gas Drains Tank, only one LI is installed | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm | 2020-02-10 | Kelvin Cook | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15717 | Verified | Conduit to 1A-FGS-LIT-0220; 1A Fuel Gas Drains Tank Level Transmitter needs to be raised so maintenance on the LIT can be performed | C | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-01-14 | Mike Tabbert | 2020-01-22 | Shannon Scott
FGS-02 | FGS-02 | PI15718 | Verified | 1A-FGS-LIT-0220; 1A Fuel Gas Drains Tank Level Transmitter nozzle needs to be relocates so transmitter can read full volume of tank | D | P | Michael Law | McD | 2020-01-09 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-04-21 | John Watts
FGS-02 | FGS-02 | PI15719 | Verified | Flex conduit to 1A-FGS-LIT-0220; 1A Fuel Gas Drains Tank Level Transmitter is disconnected | B | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-01-28 | Jared Stimpson | 2020-02-02 | Shannon Scott
FGS-02 | FGS-02 | PI15720 | Verified | Remove unused vertical support at E side of 1A Fuel Gas Drains Tank | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-02-11 | Charlie English | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15721 | Verified | Clean 1A Fuel Gas Inlet Scrubber skid | C | C | Alan Huntsman | McD | 2020-01-09 | Alan Huntsman | Comm | 2020-03-11 | Alan Huntsman | 2020-04-06 | Bernard Stasse
FGS-02 | FGS-02 | PI15722 | Verified | Remove scaffolding from 1A Fuel Gas Inlet Scrubber skid | C | C | Brooks Baker | McD | 2020-01-09 | Brooks Baker | Comm | 2020-04-01 | Johnny Campbell | 2020-04-07 | Randy Carpenter
FGS-02 | FGS-02 | PI15723 | Verified | 1A-IAS-V-0346; IA Valve handle operation impeded by tubing, cannot be opened fully, lower tubing at 1A Fuel Gas Inlet Scrubber | C | I | Gonzalo Pena | McD | 2020-01-09 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
FGS-02 | FGS-02 | PI15724 | Verified | Condolet cover missing at 1A Fuel Gas Inlet Scrubber Junction Box | C | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15725 | Verified | Missing condolet covers at East side of 1A Fuel Gas Inlet Filter skid | C | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15726 | Verified | Loose ground cable at 1A GT Fuel Gas Inlet Filter outlet flange, E side of filter | B | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15727 | Verified | 1A-FGS-PIT-1AMBP01CP142 and 1A-FGS-PIT-1AMBP01CP142 tubing is hard agains uni-strut, reroute | C | I | Gonzalo Pena | McD | 2020-01-09 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
FGS-02 | FGS-02 | PI15728 | Verified | Flex ground not connected at 1A-FGS-PIT-1AMBP01CP142 | B | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm |  |  | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15729 | Verified | Final spool piece flange to flange jumper grounds are disconnected at GT enclosure | B | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-02-13 | Mike Tabbert | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15730 | Verified | Flange ground missing at 1A-FGS-PCV-0260; Duct Burner Fuel Gas Supply Header Pressure Control Valve, upstream and downstream flanges | B | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15731 | Verified | Ground cable disconnected at downstream side of 1A-FGS-PCV-0260B; Duct Burner Fuel Gas Supply Header Pressure Control Valve | B | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15732 | Verified | Need cap for 1A-FGS-PP-0270; Duct Burner Fuel Gas Supply Header Pressure Point | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-02-12 | Joseph Lamb | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15733 | Verified | Loose U-Bolt nuts downstream of 1A-FGS-PP-0270; Duct Burner Fuel Gas Supply Header Pressure Point | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-01-15 | Bobby Williams | 2020-01-22 | Shannon Scott
FGS-02 | FGS-02 | PI15734 | Verified | Need washers on all U-bolts at Duct Burner Fuel Gas Supply Header piping, Line No.'s 6-1A-FGS-0265, 8-1A-FGS-0270, 8-1A-FGS-0275 | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-20 | Shannon Scott
FGS-02 | FGS-02 | PI15735 | Verified | Need ground jumper at flange upstream of 1A-FGS-FIT-8100; Duct Burner Fuel Gas Supply Header Flow Transmitter | B | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15736 | Verified | 1A-FGS-FIT-8100; Duct Burner Fuel Gas Supply Header Flow Transmitter flex conduit needs ground | B | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm |  |  | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15737 | Verified | Need condolet covers at 1A-FGS-FIT-8100; Duct Burner Fuel Gas Supply Header Flow Transmitter | C | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15738 | Verified | Need ground jumper at flange downstream of 1A-FGS-TE-8100; Duct Burner Fuel Gas Supply Header Temperature Element | B | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-02 | FGS-02 | PI15739 | Verified | Install Anti-Sweat insulation 12-1A-FGS-0208-601D2-AS-1.0 | C | Q | Richard McSpadden | PCI | 2020-01-09 | Richard McSpadden | Comm | 2020-08-07 | Richard McSpadden | 2020-08-14 | Dave Goldak
FGS-02 | FGS-02 | PI15740 | Verified | Install HC insulation 8-1A-FGS-0220-601D2-HC-1.0 | C | Q | Richard McSpadden | PCI | 2020-01-09 | Richard McSpadden | Comm | 2020-07-28 | Eric Policarpio | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15741 | Verified | Install Anti-Sweat insulation 8-1A-FGS-0227-601D2-AS-1.0 | C | Q | Richard McSpadden | PCI | 2020-01-09 | Richard McSpadden | Comm | 2020-07-28 | Eric Policarpio | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15742 | Verified | Install HC insulation 8-1A-FGS-0225-601D2-AS-1.0 | C | Q | Richard McSpadden | PCI | 2020-01-09 | Richard McSpadden | Comm | 2020-07-28 | Eric Policarpio | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15743 | Verified | Install Anti-Sweat insulation 2-1A-FGS-0212-151D1-AS-1.0 | C | Q | Richard McSpadden | PCI | 2020-01-09 | Richard McSpadden | Comm |  |  | 2020-08-06 | Dave Goldak
FGS-02 | FGS-02 | PI15744 | Verified | Incomplete pipe support 1A-FGS-PD-HGR-0001 (Ubolt, nuts) | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-02-12 | Joseph Lamb | 2020-02-21 | John Watts
FGS-02 | FGS-02 | PI15745 | Verified | Verify support 1A-FGS-PD-HGR-0003 (guides not visible) | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm | 2020-01-10 | Michael Law | 2020-01-10 | Michael Law
FGS-02 | FGS-02 | PI15746 | Verified | Verify support 1A-FGS-PD-HGR-0005 (guides not visible) | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm | 2020-01-10 | Michael Law | 2020-01-10 | Michael Law
FGS-02 | FGS-02 | PI15747 | Verified | Raise vent outlet above 1A-FGS-V-0261C (not to safe elevation) | D | P | Michael Law | McD | 2020-01-09 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-05-27 | John Watts
FGS-02 | FGS-02 | PI15748 | Verified | Repair/replace screen: vent outlet above 1A-FGS-V-0261C | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-02-12 | Joseph Lamb | 2020-02-17 | Shannon Scott
FGS-02 | FGS-02 | PI15749 | Verified | Verify insulation type: Line 6-1A-FGS-0260-601D2-AS-1.0 (Anti-Sweat specified, HC? installed) | C | P | Sheri Fritz | PCI | 2020-01-09 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-07-30 | Dave Goldak
FGS-02 | FGS-02 | PI15750 | Verified | Paint galvanize hanger welds, Line 6-1A-FGS-0260-601D2-AS-1.0 | C | X | Johnny Campbell | McD | 2020-01-09 | Johnny Campbell | Comm | 2020-04-06 | Johnny Campbell | 2020-04-24 | Mark Williamson
FGS-02 | FGS-02 | PI15751 | Verified | 1A-FGS-STN-0260 missing equipment tag | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15752 | Verified | Line downstream from 1A-FGS-V-0262B not routed to drain. Cap installed. Not per PID. | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-06-16 | Dave Goldak
FGS-02 | FGS-02 | PI15760 | Verified | 1A-FGS-PCV-0260B missing equipment tag | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15761 | Verified | U-bolts loose, upstream and downstream of 1A FGS-PCV-0260B | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-01-15 | Bobby Williams | 2020-01-23 | Shannon Scott
FGS-02 | FGS-02 | PI15762 | Verified | 1A-FGS-V-0263; Paint ground tabs | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15763 | Verified | 1A-FGS-V-0263; install valve handle roll pin | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-01-15 | Bobby Williams | 2020-01-23 | Shannon Scott
FGS-02 | FGS-02 | PI15764 | Verified | 1A-FGS-V-0264; Paint ground tabs | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15765 | Verified | 1A-FGS-V-0264; install valve handle roll pin | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-01-15 | Bobby Williams | 2020-01-23 | Shannon Scott
FGS-02 | FGS-02 | PI15766 | Verified | Verify pilot valve connection distance from 1A-FGS-PCV-0260A. Requires six pipe diameters. | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2021-04-21 | John Watts
FGS-02 | FGS-02 | PI15767 | Verified | Missing cap, 1A FGS-PP-0270 | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15768 | Verified | Patch paint ground jumper tabs at 1A-FGS-SRV-0270 | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15769 | Verified | U-bolts loose, support for 10-1A-FGS-0271-151D1 vent line | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-23 | Shannon Scott
FGS-02 | FGS-02 | PI15770 | Verified | Attach flange ground jumpers, CBI to Vendor flow element spool (BOTH ENDS) | B | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm |  |  | 2020-01-13 | Fred Michael
FGS-02 | FGS-02 | PI15771 | Verified | Patch paint ground jumper tabs at CBI to Vendor flow element spool | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15772 | Verified | Conduit cover missing 1A-FGS-FE-8100 | C | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm |  |  | 2020-02-12 | Dave Goldak
FGS-02 | FGS-02 | PI15773 | Verified | Install U-bolt double-nut at TP-36 to vendor HRSG duct burner skid | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-01-15 | Bobby Williams | 2020-01-23 | Shannon Scott
FGS-02 | FGS-02 | PI15774 | Verified | Vent line support not in contact with support steel - Vent line at 1A-FGS-V-0280C. | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-23 | Shannon Scott
FGS-02 | FGS-02 | PI15775 | Verified | Loose bolts, HGR -0007 | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-01-27 | Bobby Williams | 2020-02-21 | John Watts
FGS-02 | FGS-02 | PI15776 | Verified | 1A-FGS-PCV-0210 missing equipment tag | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-10 | John Watts
FGS-02 | FGS-02 | PI15777 | Verified | 1A-FGS-PCV-0210 verify settings | C | I | William Mitchell | McD | 2020-01-09 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15778 | Verified | Patch paint yellow, 1A-FGS-V-0209 A, B, C | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15779 | Verified | Verify appropriate equipment tagging, 1A-FGS-V-0209 A, B, C. | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-05-08 | James Beech | 2021-04-26 | Keith Pollock
FGS-02 | FGS-02 | PI15780 | Verified | Verify appropriate equipment tagging, 1A-FGS-V-0220 A, B, C. | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-05-08 | James Beech | 2021-02-22 | Dave Goldak
FGS-02 | FGS-02 | PI15781 | Verified | Patch paint , 1A-FGS-V-0210 A, B, C | C | X | Jorge Alexander | McD | 2020-01-09 | Jorge Alexander | Comm | 2020-01-16 | Bobby Williams | 2020-02-06 | Dave Goldak
FGS-02 | FGS-02 | PI15782 | Verified | Carbon contamination on eq tags, 1A-FGS-V-0210 A, B, C | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-01-27 | Bobby Williams | 2020-02-06 | Dave Goldak
FGS-02 | FGS-02 | PI15783 | Verified | Verify support installation, vent line 2-1A-FGS-0212-151D1-AS-1.0 (ADD'L needed) | D | P | Michael Law | McD | 2020-01-09 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
FGS-02 | FGS-02 | PI15784 | Verified | Paint cap 1A-FGS-V-0221B | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15785 | Verified | Paint ground tabs: Fuel Gas Dew Point Heater | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15786 | Verified | Patch paint ground tabs: 1A-FGS-V-0222 | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15787 | Verified | Two LB conduit covers uncovered (1A-GT-FGS Emergency Shut off valve) | C | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm |  |  | 2020-02-12 | Dave Goldak
FGS-02 | FGS-02 | PI15788 | Verified | 1A-GT-FGS Emergency Shut off valve: Instrument air service support required. Valve not indicated . | C | P | James Tanner | McD | 2020-01-09 | James Tanner | Comm | 2020-02-12 | James Tanner | 2020-02-17 | Shannon Scott
FGS-02 | FGS-02 | PI15789 | Verified | Touch up paint paint ground tabs: Fuel Gas Temperature Control Valve | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15790 | Verified | 12x8 reducer is concentric on PID (Prior to FGS Heaters). Eccentric reducer installed. Red line PID. | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-07-28 | Keith Pollock
FGS-02 | FGS-02 | PI15791 | Verified | 1A GT Fuel Gas Heater - Cladding damaged on top of heater drum. Walked on. | C | Q | Josh Koerner | PCI | 2020-01-09 | Josh Koerner | Comm | 2020-06-19 | Jason Ezell | 2020-06-19 | Jason Ezell
FGS-02 | FGS-02 | PI15792 | Verified | 1B GT Fuel Gas Heater - Cladding damaged on top of heater drum. Walked on. | C | Q | Josh Koerner | PCI | 2020-01-09 | Josh Koerner | Comm | 2020-06-19 | Jason Ezell | 2020-06-19 | Jason Ezell
FGS-02 | FGS-02 | PI15793 | Verified | Gas leak detected during walkdown 1A FGS Heater outlet flange. Reported to Commissioning. | A | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-03-27 | Bobby Williams | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15794 | Verified | Verify support needed, 1A-FGS-V-0240B | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm |  |  | 2020-01-10 | Michael Law
FGS-02 | FGS-02 | PI15795 | Verified | Verify appropriate equipment tagging, 1A-FGS-TI-240. Not accessible. | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm |  |  | 2020-01-10 | Michael Law
FGS-02 | FGS-02 | PI15796 | Verified | Verify appropriate equipment tagging, 1A-FGS-SRV-0250. Not accessible. | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm |  |  | 2020-01-10 | Michael Law
FGS-02 | FGS-02 | PI15797 | Verified | Verify appropriate equipment tagging, 1A-FGS-V-240 A, B. And PI 0238. Not accessible. | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm |  |  | 2020-01-10 | Michael Law
FGS-02 | FGS-02 | PI15798 | Verified | Verify appropriate equipment tagging, 1A-FGS Emergency Vent Valve and bypass. Not accessible. | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm |  |  | 2020-01-10 | Michael Law
FGS-02 | FGS-02 | PI15802 | Verified | Valve 1A-FGS-V-0285 incorrectly tagged (Needs 1A prefix) | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-10 | John Watts
FGS-02 | FGS-02 | PI15803 | Verified | Remove rust and patch paint ground tabs -1A FGS Drains tank flanges (all). | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2021-07-08 | Eric Policarpio | 2021-07-08 | John Watts
FGS-02 | FGS-02 | PI15804 | Verified | Verify appropriate equipment tagging, 1A-FGS-V-238 A, B. Not accessible. | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15805 | Verified | 1A-FGS-V-0287 not piped to drain as shown on PID. Cap installed. Red line ? | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-06-16 | Dave Goldak
FGS-02 | FGS-02 | PI15806 | Verified | Remove rust and patch paint ground tabs -1A FGS Scrubber inlet and outlet flanges | C | X | Brooks Baker | McD | 2020-01-09 | Brooks Baker | Comm | 2020-06-23 | Brooks Baker | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15807 | Verified | Tee and cap installed on line 1-1A-FGS-0301 not shown on drawings. Red line PID. | C | P | Mike Tabbert | McD | 2020-01-09 | Mike Tabbert | Comm | 2020-06-18 | Mike Tabbert | 2020-06-22 | Dave Goldak
FGS-02 | FGS-02 | PI15808 | Verified | Missing cap 1A-FGS-V-0310B | C | P | Tim Green | McD | 2020-01-09 | Tim Green | Comm | 2020-06-18 | Tim Green | 2020-06-18 | Dave Goldak
FGS-02 | FGS-02 | PI15809 | Verified | Patch paint yellow, 1A-FGS-V-0310 A, B, C | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15810 | Verified | Remove rust and patch paint ground tabs -1A FGS Inlet filter flanges | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15811 | Verified | Patch paint 1A-FGS-V-0319 A, B, C | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15812 | Verified | Install equipment tags 1A-FGS-TE- 1AMBP01CT026 | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15813 | Verified | Two open conduit covers (ground and overhead) 1A-FGS-TE- 1AMBP01CT026 | C | E | Chris Colvin | McD | 2020-01-09 | Chris Colvin | Comm |  |  | 2020-02-12 | Dave Goldak
FGS-02 | FGS-02 | PI15814 | Verified | Install insulation blanket on terminal flange at GT unit connection | C | Q | Richard McSpadden | PCI | 2020-01-09 | Richard McSpadden | Comm | 2020-07-28 | Eric Policarpio | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15815 | Verified | Verify supports (vertical) 8-1A-FGS-0310-601D2-HC-1.0 upstream of FGS inlet filter | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm |  |  | 2020-01-10 | Michael Law
FGS-02 | FGS-02 | PI15816 | Verified | Verify presence of TE EKCO1CT003 and 004 in dewpoint heater cabinet (not open during walkdown) | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm |  |  | 2020-01-10 | Michael Law
FGS-02 | FGS-02 | PI15817 | Verified | Install equipment tags 1A GT Fuel Gas Emergency Shutoff valve and associated solenoids, etc. | C | P | Tim Green | McD | 2020-01-09 | Tim Green | Comm | 2020-06-01 | Tim Gallegos | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15818 | Verified | N2 Supply piping not per PID LP-00823. N2 lines on either side of FGS Temperature control valve capped. No check valves installed. Additional bleed/vent valve installed. Add equipment tag numbers and red line PID | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2021-04-21 | John Watts
FGS-02 | FGS-02 | PI15819 | Verified | Remove rust and patch paint ground tabs -1A FGS Temp Control Valve MBL01AA702 flanges | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15820 | Verified | 1A FGS Heater: Loose housing LS MBP01CL216 | C | I | Gonzalo Pena | McD | 2020-01-09 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
FGS-02 | FGS-02 | PI15821 | Verified | 1A FGS Heater: Reattach tag valve MBP01AA823 | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15822 | Verified | 1A FGS Heater: Missing tag valve MBP01AA827 | C | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-02 | FGS-02 | PI15823 | Verified | Paint welds on pipe between FGS Heaters A & B | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-06-16 | Dave Goldak
FGS-02 | FGS-02 | PI15824 | Verified | Spring Can Hanger out of plumb, line 8-1A-FGS-0250-601D2-HC-1.0 | C | P | James Beech | McD | 2020-01-09 | James Beech | Comm | 2020-05-26 | James Beech | 2020-06-18 | Dave Goldak
FGS-02 | FGS-02 | PI15825 | Verified | Complete HC insulation, line 8-1A-FGS-0250-601D2-HC-1.0 | C | Q | Richard McSpadden | PCI | 2020-01-09 | Richard McSpadden | Comm | 2020-07-28 | Eric Policarpio | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15826 | Verified | 1A FGS Inlet Scrubber: Bent tubing on vent/N2 connection EKEO1AA959 | C | I | Gonzalo Pena | McD | 2020-01-09 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-23 | Shannon Scott
FGS-02 | FGS-02 | PI15827 | Verified | 1A FGS Inlet Scrubber: Bent tubing at valve EKEO1AA961 | C | I | Gonzalo Pena | McD | 2020-01-09 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-23 | Shannon Scott
FGS-02 | FGS-02 | PI15828 | Verified | 1A FGS Inlet Scrubber: Patch paint ground tabs, N2 supply inlet flange | C | X | Jerry Smith | McD | 2020-01-09 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2021-04-21 | John Watts
FGS-02 | FGS-02 | PI15829 | Verified | 1A FGS Inlet Scrubber: Verify appropriate equipment tagging, valves 1AA854, 1AA859, and PI 1CP302. Not accessible. | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm | 2020-01-10 | Michael Law | 2021-04-21 | John Edwards
FGS-02 | FGS-02 | PI15830 | Verified | 1A FGS Inlet Scrubber: Verify appropriate equipment tagging, valves 1AA172 and relief valve 1AA171. Not accessible. | C | P | Kelvin Cook | McD | 2020-01-09 | Kelvin Cook | Comm | 2020-01-10 | Michael Law | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15831 | Verified | 1A FGS Inlet Scrubber: Bent tubing at valve EKEO1AA70 | C | I | Gonzalo Pena | McD | 2020-01-09 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
FGS-02 | FGS-02 | PI15852 | Verified | Install insul, line 6-1A-FGS-0265-601D2-FP-2.0-ET | C | Q | Richard McSpadden | PCI | 2020-01-10 | Richard McSpadden | Comm | 2020-07-28 | Dave Goldak | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15853 | Verified | Install insul, line 8-1A-FGS-0270-301D1-FP-2.0-ET | C | Q | Richard McSpadden | PCI | 2020-01-10 | Richard McSpadden | Comm | 2020-07-28 | Eric Policarpio | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15854 | Verified | Install insul, line 1-1A-FGS-0265-601D2-FP-2.0-ET | C | Q | Richard McSpadden | PCI | 2020-01-10 | Richard McSpadden | Comm | 2020-07-28 | Eric Policarpio | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15855 | Verified | Install insul, line 2-1A-FGS-0270-301D1-FP-2.0-ET | C | Q | Richard McSpadden | PCI | 2020-01-10 | Richard McSpadden | Comm | 2020-07-28 | Eric Policarpio | 2020-07-28 | Dave Goldak
FGS-02 | FGS-02 | PI15856 | Verified | Install insul, line 6-1A-FGS-0270-301D1-FP-2.0-ET | C | Q | Richard McSpadden | PCI | 2020-01-10 | Richard McSpadden | Comm | 2020-08-06 | Eric Policarpio | 2020-08-06 | Dave Goldak
FGS-02 | FGS-02 | PI15857 | Verified | Install insul, line 8-1A-FGS-0275-301D1-FP-2.0-ET | C | Q | Richard McSpadden | PCI | 2020-01-10 | Richard McSpadden | Comm | 2020-08-06 | Eric Policarpio | 2020-08-06 | Dave Goldak
FGS-02 | FGS-02 | PI15858 | Verified | Install insul, line 2-1A-FGS-0215-151D1-FP-2.0-ET | C | Q | Richard McSpadden | PCI | 2020-01-10 | Richard McSpadden | Comm | 2020-08-06 | Eric Policarpio | 2020-08-06 | Dave Goldak
FGS-02 | FGS-02 | PI15859 | Verified | Install insul, line 1-1A-FGS-0238-601D2-FP-2.0-ET | C | Q | Richard McSpadden | PCI | 2020-01-10 | Richard McSpadden | Comm | 2020-08-06 | Eric Policarpio | 2020-08-06 | Dave Goldak
FGS-02 | FGS-02 | PI15860 | Verified | Install insul, line 1-1A-FGS-0239-601D2-FP-2.0-ET | C | Q | Sheri Fritz | PCI | 2020-01-10 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI15861 | Verified | Install insul, line 1-1A-FGS-0301-601D2-FP-2.0-ET | C | Q | Sheri Fritz | PCI | 2020-01-10 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI16197 | Verified | The purge/vent valves are installed close to the safety relief valve (1A-FGS-SRV-0270). Valve handles hits the connection flange (1A-FGS-V-0280B & 1A-FGS-V-0280C) | B | P | James Beech | McD | 2020-01-20 | James Beech | Comm | 2020-03-04 | Tim Green | 2020-03-09 | Nelson Eichelberger
FGS-02 | FGS-02 | PI16438 | Verified | 1A FGS Inlet Scrubber: valve QEF11AA307 not lockable | C | P | James Beech | McD | 2020-01-29 | James Beech | Comm | 2020-04-22 | James Beech | 2020-08-07 | Dave Goldak
FGS-02 | FGS-02 | PI16439 | Verified | 1A FGS Inlet Scrubber: valve QJA01AA105 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-02 | FGS-02 | PI16440 | Verified | 1A FGS Inlet Scrubber: valve QJA01AA107 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-02 | FGS-02 | PI16441 | Verified | 1A FGS Inlet Scrubber: valve QJA01AA115 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-02 | FGS-02 | PI16442 | Verified | 1A FGS Inlet Scrubber: valve EKE01AA961 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-02 | FGS-02 | PI16443 | Verified | 1A FGS Inlet Scrubber: valve EKE01AA959 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-02 | FGS-02 | PI16444 | Verified | 1A FGS Inlet Scrubber: valve QJA01AA110 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-02 | FGS-02 | PI16445 | Verified | 1A FGS Inlet Scrubber: valve QJA01AA108 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-02 | FGS-02 | PI16446 | Verified | 1A FGS Inlet Scrubber: valve QJA01AA109 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-02 | FGS-02 | PI16447 | Verified | 1A FGS Inlet Scrubber: valve EKE01AA960 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-02 | FGS-02 | PI16448 | Verified | 1A FGS Inlet Scrubber: valve QEF11AA306 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-02 | FGS-02 | PI16516 | Verified | 1AEKC01GH001 Fuel Gas Dew Point Heater Control Panel - Inside panel needs to be cleaaned (rags, papers, dirt, packing material) | C | E | Chris Colvin | McD | 2020-02-04 | Chris Colvin | Comm |  |  | 2020-02-10 | Fred Michael
FGS-02 | FGS-02 | PI16517 | Verified | 1AEKC01GH001 Fuel Gas Dew Point Heater Control Panel - Cable & wire Tags need heat shrink | C | E | Chris Colvin | McD | 2020-02-04 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Fred Michael
FGS-02 | FGS-02 | PI17862 | Verified | See attached photo DSCN1930; hanger not centered east/west and two loose nuts, 1A-FGS-HGR-0077 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17863 | Verified | See attached photo DSCN1933; U-Bolt nuts missing, 1A-FGS-HGR-0423 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17864 | Verified | See attached photo DSCN1943; hanger not centered east/west, 1A-FGS-HGR-0009 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-18 | Dave Goldak
FGS-02 | FGS-02 | PI17865 | Verified | See attached photo DSCN1945; Differenct clamp than drawing and loose nuts, 1A-FGS-HGR-0093 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-07-30 | Dave Goldak
FGS-02 | FGS-02 | PI17866 | Verified | See attached photo DSCN1947; Emergency shutoff value not supported | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-10-06 | Dave Goldak
FGS-02 | FGS-02 | PI17867 | Verified | See attached photo DSCN1949; Cold galv. welds, 1A-FGS-HGR-0097 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17868 | Verified | See attached photo DSCN1951; Cold galv. weld, Hanger rod not plumb, 1A-FGS-HGR-0100 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-26 | James Beech | 2020-06-17 | Satyam Gajjar
FGS-02 | FGS-02 | PI17869 | Verified | See attached photo DSCN1954; loose nut/bolt too short, 1A-FGS-HGR-0101 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17870 | Verified | See attached photo DSCN1956; turnbuckle added , 1A-FGS-HGR-0098 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-27 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17871 | Verified | See attached photo DSCN1958; Cold galv. welds, 1A-FGS-HGR-0099 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17872 | Verified | See attached photo DSCN1960; Hanger not centered, 1A-FGS-HGR-0003 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-07-30 | Dave Goldak
FGS-02 | FGS-02 | PI17873 | Verified | See attached photo DSCN1962; Cold galv. welds and remove rope/snow fence, 1A-FGS-HGR-0056 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-12 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17874 | Verified | See attached photo DSCN1964; Cold galv. Weld and bend cotter pin, 1A-FSG-HGR-0057 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17875 | Verified | See attached photo DSCN1966; Cold galv. Weld, 1A-FGS-HGR-0058 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17876 | Verified | See attached photo DSCN1970; Hanger not centered north/south and two loose nuts at base plate, 1A-FGS-HGR-0060 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17877 | Verified | See attached photo DSCN1972; Guides not installed and 2 loose nuts at base plate, 1A-FGS-HGR-0510 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17878 | Verified | See attached photo DSCN1975; Cold galv. Welds, 1A-FGS-HGR-0080 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17879 | Verified | See attached photo DSCN1978; Shoe not centered east/west, 1A-FGS-HGR-0011 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17880 | Verified | See attached photo DSCN1981; Shoe not centered east/west, 1A-FGS-HGR-0012 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17881 | Verified | See attached photo DSCN1983; Spacer added and guides not installed, 1A-FGS-HGR-0015 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-12 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17882 | Verified | See attached photo DSCN1985; Install roll pin in place of #9 wire holding handle onto valve, 1A-FGS-V-0260 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-12 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17883 | Verified | See attached photo DSCN1987; Both nuts on bottom of u-bolt, 1A-FGS-HGR-0016 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17884 | Verified | See attached photo DSCN1989; Both nuts on bottom of u-bolt and burnt flange of support steel, 1A-FGS-HGR-0017 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17885 | Verified | See attached photo DSCN1992; extra u-bolt installed, 1A-FGS-HGR-0023 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17886 | Verified | See attached photo DSCN1994; two nuts installed on u-bolt and base field welded, 1A-FGS-HGR-0024 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17887 | Verified | See attached photo DSCN1997; both nuts on bottom of u-bolt, 1A-FGS-HGR-0026 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17888 | Verified | See attached photo DSCN2000; extra u-bolt installed, 1A-FGS-HGR-0135 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17889 | Verified | See attached photo DSCN2002; both nuts on bottom of u-bolt, 1A-FGS-HGR-0027 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17890 | Verified | See attached photo DSCN2004; Show drain connection and valve per isometric, 1A-FGS-ME-PID-0001 | C | P | Charles Worthington | McD | 2020-03-17 | Charles Worthington | Comm | 2020-06-24 | Dave Goldak | 2020-06-24 | Dave Goldak
FGS-02 | FGS-02 | PI17891 | Verified | See attached photo DSCN2006; one nut on top, one on bottom of u-bolt, 1A-FGS-HGR-0139 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17892 | Verified | See attached photo DSCN2008; Hanger rod bent, 1A-FGS-HGR-0137 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17893 | Verified | See attached photo DSCN2010; Cold galv. Welds and spacers added and guides not installed, 1A-FGS-HGR-0166 | C | X | Bobby Williams | McD | 2020-03-17 | Bobby Williams | Comm | 2020-03-26 | Bobby Williams | 2020-07-30 | Dave Goldak
FGS-02 | FGS-02 | PI17894 | Verified | See attached photo DSCN2011; guides not installed and support leg cut off, 1A-FGS-HGR-0165 | C | P | Tim Green | McD | 2020-03-17 | Tim Green | Comm | 2020-09-15 | Jason Ezell | 2021-05-27 | John Watts
FGS-02 | FGS-02 | PI17895 | Verified | See attached photo DSCN2014; spacer added and guides not installed and cold galv. Welds, 1A-FGS-HGR-0166 | C | X | Bobby Williams | McD | 2020-03-17 | Bobby Williams | Comm | 2020-03-26 | Bobby Williams | 2020-07-30 | Dave Goldak
FGS-02 | FGS-02 | PI17896 | Verified | See attached photo DSCN2017; Guides not installed, 1A-FGS-HGR-0175 | C | P | Bobby Williams | McD | 2020-03-17 | Bobby Williams | Comm | 2020-03-26 | Bobby Williams | 2020-07-30 | Dave Goldak
FGS-02 | FGS-02 | PI17897 | Verified | See attached photo DSCN2019; Guides not isntalled, 1A-FGS-HGR-0176 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-29 | James Beech | 2020-07-30 | Dave Goldak
FGS-02 | FGS-02 | PI17898 | Verified | See attached photo DSCN2021; Guides not isntalled, 1A-FGS-HGR-0185 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-29 | James Beech | 2020-07-30 | Dave Goldak
FGS-02 | FGS-02 | PI17899 | Verified | See attached photo DSCN2023; Guides not isntalled, 1A-FGS-HGR-0186 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-29 | James Beech | 2020-07-30 | Dave Goldak
FGS-02 | FGS-02 | PI17900 | Verified | See attached photo DSCN2026; extra u-bolt installed, 1A-FGS-HGR-0105 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-22 | Dave Goldak
FGS-02 | FGS-02 | PI17901 | Verified | See attached photo DSCN2028; Both nuts on bottom of u-bolt and cold galv. Welds, 1A-FGS-HGR-0104 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-06-22 | Dave Goldak
FGS-02 | FGS-02 | PI17902 | Verified | See attached photo DSCN2031; Cold galv. Welds, 1A-FGS-HGR-0103 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-22 | Dave Goldak
FGS-02 | FGS-02 | PI17903 | Verified | See attached photo DSCN2033; ground jumper missing on both flanges, 1A-FGS emergency vent valve | C | P | Tim Green | McD | 2020-03-17 | Tim Green | Comm | 2020-07-10 | Tim Green | 2020-07-22 | Dave Goldak
FGS-02 | FGS-02 | PI17904 | Verified | See attached photo DSCN2035; Nut missing on top of u-bolt, 1A-FGS-HGR-0102 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-22 | Dave Goldak
FGS-02 | FGS-02 | PI17905 | Verified | See attached photo DSCN2037; Both nuts on bottom of u-bolt and Cold galv. welds, 1A-FGS-HGR-0106 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-06-22 | Dave Goldak
FGS-02 | FGS-02 | PI17906 | Verified | See attached photo DSCN2039; Solenoid held on with tape and bent tubing and inadequate instrument air tube support, 1A-FGS emergency vent valve | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-27 | Albert Burge | 2020-06-22 | Satyam Gajjar
FGS-02 | FGS-02 | PI17907 | Verified | See attached photo DSCN2045; Cold galv. Welds, 1A-FGS-HGR-0131 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-22 | Dave Goldak
FGS-02 | FGS-02 | PI17908 | Verified | See attached photo DSCN2048; Cold galv. Welds and gap at guides, 1A-FGS-HGR-0132 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-08 | James Beech | 2020-06-22 | Dave Goldak
FGS-02 | FGS-02 | PI17909 | Verified | See attached photo DSCN2051; Handle zip tied, remove, 1A-FGS-SRV-250 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17910 | Verified | See attached photo DSCN2053; support installed backwards, 1A-FGS-HGR-0128 | C | P | Bobby Williams | McD | 2020-03-17 | Bobby Williams | Comm | 2020-03-31 | Michael Law | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17911 | Verified | See attached photo DSCN2057; Cold galv. Welds, 1A-FGS-HGR-0381 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17912 | Verified | See attached photo DSCN2059; support installed backwards, 1A-FGS-HGR-0449 | C | P | Gary Pickeral | McD | 2020-03-17 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17913 | Verified | See attached photo DSCN2061; Hanger not centered and not level, 1A-FGS-HGR-0488 | C | P | Tim Green | McD | 2020-03-17 | Tim Green | Comm | 2020-06-18 | Tim Green | 2020-06-18 | Dave Goldak
FGS-02 | FGS-02 | PI17914 | Verified | See attached photo DSCN2065; Loose nut on strut, 1A-FGS-HGR-0489 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-13 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17915 | Verified | See attached photo DSCN2067; support installed backwards and cold galv. Welds, 1A-FGS-HGR-0490 | C | X | Gary Pickeral | McD | 2020-03-17 | Gary Pickeral | Comm | 2020-05-26 | Gary Pickeral | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17916 | Verified | See attached photo DSCN2069; Support isntalled backwards and remove coiled cable, 1A-FGS-HGR-0494 | C | P | Gary Pickeral | McD | 2020-03-17 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17917 | Verified | See attached photo DSCN2071; Cold galv. Welds, 1A-FGS-HGR-0403 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17918 | Verified | See attached photo DSCN2073; Cold galv. Welds, 1A-FGS-HGR-0404 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17919 | Verified | See attached photo DSCN2075; Loose nut at base, 1A-FGS-HGR-0432 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17920 | Verified | See attached photo DSCN2077; Loose nut at base, 1A-FGS-HGR-0433 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17921 | Verified | See attached photo DSCN2079; shoe not sitting flat on support beam, 1A-FGS-HGR-0435 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17922 | Verified | See attached photo DSCN2081; loose nut at base, 1A-FGS-HGR-0436 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-13 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17923 | Verified | See attached photo DSCN2083; Missing vent hole, 1A-FGS-HGR-0437 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-13 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17924 | Verified | See attached photo DSCN2084; Guides not installed, 1A-FGS-HGR-0438 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-29 | James Beech | 2020-06-17 | Dave Goldak
FGS-02 | FGS-02 | PI17925 | Verified | See attached photo DSCN2086; Cold galv. Welds and remove spacer block, 1A-FGS-HGR-0352 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-21 | James Beech | 2020-06-18 | Dave Goldak
FGS-02 | FGS-02 | PI17926 | Verified | See attached photo DSCN2089; Clamp is not fastened, 1A-FGS-HGR-0353 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-13 | James Beech | 2020-06-18 | Dave Goldak
FGS-02 | FGS-02 | PI17927 | Verified | See attached photo DSCN2091; Cold galv. Weld, 1A-FGS-HGR-0354 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-18 | Dave Goldak
FGS-02 | FGS-02 | PI17928 | Verified | See attached photo DSCN2093; verital guides isntalled rather than hold downs per drawing and shoe is not flat on support, 1A-FGS-HGR-0355 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-18 | Dave Goldak
FGS-02 | FGS-02 | PI17929 | Verified | See attached photo DSCN2096; Hanger not installed, 1A-FGS-HGR-0356 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-27 | James Beech | 2020-06-18 | Dave Goldak
FGS-02 | FGS-02 | PI17930 | Verified | See attached photo DSCN2098; Cold galv. Welds, 1A-FGS-HGR-0230 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-18 | Dave Goldak
FGS-02 | FGS-02 | PI17931 | Verified | See attached photo DSCN2100; V-0224A stem east as built, V-0223B stem east as built, V-0223C stem west as built, 1A-FGS-V-0224A,B,C | D | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
FGS-02 | FGS-02 | PI17932 | Verified | See attached photo DSCN2102; V-0230A stem west as built, 1A-FGS-V-0230A | D | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
FGS-02 | FGS-02 | PI17933 | Verified | See attached photo DSCN2104; Cold galv. Welds, 1A-FGS-HGR-0203 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-18 | Dave Goldak
FGS-02 | FGS-02 | PI17934 | Verified | See attached photo DSCN2106; Cold galv. Welds, 1A-FGS-HGR-0204 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-18 | Dave Goldak
FGS-02 | FGS-02 | PI17935 | Verified | See attached photo DSCN2108; Cold galv. Welds, 1A-FGS-HGR-0218 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-18 | Dave Goldak
FGS-02 | FGS-02 | PI17936 | Verified | See attached photo DSCN2112; tighten clamp and shoe not sitting on support, 1A-FGS-HGR-0231 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-13 | James Beech | 2020-06-18 | Dave Goldak
FGS-03 | FGS-03 | PI04965 | Verified | Install 1B-FGS-LI-0220. | B | I | Gonzalo Pena | McD | 2019-09-10 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-10-05 | Mike Tabbert
FGS-03 | FGS-03 | PI05203 | Verified | Repair damaged piping on 1B fuel gas separator skid. | A | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const |  |  | 2019-09-18 | Kelvin Cook
FGS-03 | FGS-03 | PI07390 | Verified | Tighten u-bolt on the inlet at the fuel gas separator. | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-12-19 | J.L. Bickham
FGS-03 | FGS-03 | PI07393 | Verified | Grout all supports. | C | C | Johnny Campbell | McD | 2019-09-27 | Johnny Campbell | Const | 2019-10-10 | Jack Fields | 2019-10-30 | Joshua Sturgeon
FGS-03 | FGS-03 | PI07395 | Verified | Clean all fuel gas skids. | C | C | Alan Huntsman | McD | 2019-09-27 | Alan Huntsman | Const |  |  | 2019-12-31 | William Mitchell
FGS-03 | FGS-03 | PI07396 | Verified | Remove rigging at the feedwater platform. | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-12-31 | William Mitchell
FGS-03 | FGS-03 | PI07398 | Verified | Valve handles 1B-FGS-V-0264, 0263 at the duct burner skid have interference with handrail. | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-09-30 | Billy Williams | 2019-10-03 | Shannon Scott
FGS-03 | FGS-03 | PI07399 | Verified | During hydro restoration verify spring can at the inlet scrubber is centered on support 1BFGS0310. | A | P | Kelvin Cook | McD | 2019-09-27 | Kelvin Cook | Const | 2019-10-09 | Kelvin Cook | 2019-10-15 | Shannon Scott
FGS-03 | FGS-03 | PI07401 | Verified | Set all spring cans to cold setting & pull gags. | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-12-31 | William Mitchell
FGS-03 | FGS-03 | PI07403 | Verified | Replace CS nipple with SS nipple at 1BBMBA01CT026 at the fuel gas inlet filter. | A | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-10-30 | Gonzalo Pena | 2019-11-07 | Shannon Scott
FGS-03 | FGS-03 | PI07406 | Verified | Adjust high point vent valve for operator usage at the fuel gas scrubber. | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-05 | Charlie English | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07409 | Verified | Valve 1BEKC01AA103 at dew point heater skid has insufficient clearance with column. | B | P | Kelvin Cook | McD | 2019-09-27 | Kelvin Cook | Const | 2019-10-29 | Bobby Williams | 2019-11-07 | Shannon Scott
FGS-03 | FGS-03 | PI07411 | Verified | Tag all valves. | C | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2020-01-17 | Kelvin Cook
FGS-03 | FGS-03 | PI07413 | Verified | All level switches on EKC01AC101 and 102 flex need grounding | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07414 | Verified | Ground flex on all instruments at FG inlet filter MBP01AT101 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07418 | Verified | Low point drain or a bug screen needed for TE-MBP01CT026 - FG filter inlet | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-30 | Brad Stanford | 2019-12-30 | Chris Boudreaux
FGS-03 | FGS-03 | PI07419 | Verified | PI-EKE01CP302 not installed on to FG Scrubber unit | A | I | Joshua Sturgeon | McD | 2019-09-27 | Joshua Sturgeon | Const |  |  | 2019-10-24 | Albert Burge
FGS-03 | FGS-03 | PI07420 | Verified | LS-EKE01CL201 not mounted - FG Scrubber unit | A | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-10-30 | Gonzalo Pena | 2019-11-04 | Albert Burge
FGS-03 | FGS-03 | PI07434 | Verified | Ground 1st flange from UG to grid - FG Separator skid | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07435 | Verified | Ground 2nd flange from UG, to the next flange to grid - FG Separator skid | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07436 | Verified | Ground separator tanks to grid (2 each) | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-31 | Dustin Futrell | 2019-12-30 | Chris Boudreaux
FGS-03 | FGS-03 | PI07437 | Verified | FG Separator skid - ground duct bank | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-30 | Brad Stanford | 2019-12-30 | Chris Boudreaux
FGS-03 | FGS-03 | PI07438 | Verified | FG Separator skid - seal at duct banks | B | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-30 | Brad Stanford | 2019-12-30 | Chris Boudreaux
FGS-03 | FGS-03 | PI07439 | Verified | FG Separator skid - JB separator to ground | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-10-30 | Brad Stanford | 2019-12-30 | Chris Boudreaux
FGS-03 | FGS-03 | PI07440 | Verified | FG Separator skid - pour seal at stub ups. Comm to advise | B | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07441 | Verified | FG Separator skid - torque the level gauges on the separators, all level switches | A | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const |  |  | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07442 | Verified | EKC Heater Panel - ground the cable tray all the way | B | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-11-11 | Brad Stanford | 2019-12-13 | Mike Tabbert
FGS-03 | FGS-03 | PI07443 | Verified | EKC Heater Panel - ground the bushings and cable tray supports | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07444 | Verified | EKC Heater Panel - support need to install on the cable tray, 90 bend to panel | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07445 | Verified | EKC Heater Panel - replace ground wire on the flex (EKC01AC103) wire too small | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07446 | Verified | 1A-FGS-PID-0002 AA701 and AA702 valves need to ground flex | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07449 | Verified | FG Heater and FG Dew point heater skids - 4 x 2" conduits at the tray need seal off | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-31 | Fred Michael
FGS-03 | FGS-03 | PI07451 | Verified | General: Install all missing condulet covers | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-16 | Fred Michael
FGS-03 | FGS-03 | PI07454 | Verified | FGS-V-0280B valve not working, FGS-V-280C valve has a pinch point area, FGS-V-280A need to reach far to operate | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-11-04 | Albert Burge
FGS-03 | FGS-03 | PI07455 | Verified | FIT-8100 not installed | B | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-11-11 | Brad Stanford | 2019-12-20 | Albert Burge
FGS-03 | FGS-03 | PI07457 | Verified | 1BEKC01CA103 missing lock clip on panel | B | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-11-08 | Brad Stanford | 2019-12-30 | Chris Boudreaux
FGS-03 | FGS-03 | PI07458 | Verified | 1BEKE01CL101 missing latch lock on panel | B | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-11 | Bobby Williams | 2019-12-01 | Albert Burge
FGS-03 | FGS-03 | PI07460 | Verified | MBP01AA711 FG emergency vent valve - Rotate 90 degree | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-11-04 | Albert Burge
FGS-03 | FGS-03 | PI07482 | Verified | Relief valve at duct burner skid missing rain flapper. | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-28 | Albert Burge
FGS-03 | FGS-03 | PI07532 | Verified | Replace tank with new tank from entergy | A | M | Shane Crowe | McD | 2019-09-27 | Shane Crowe | Const | 2019-10-01 | Joshua Sturgeon | 2019-10-03 | Kelvin Cook
FGS-03 | FGS-03 | PI07533 | Verified | On ISO 1B-FGS-PD-P40-0208-01 install ground lug at 1B-CTS-EKE01AT101/EKE01-102 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07534 | Verified | On ISO 1B-FGS-PD-P40-0208-01 install ground wire 1B-CTS-EKE01AT101/EKE01-102 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07535 | Verified | On ISO 1B-FGS-PD-P40-0210-01 pipe support 1B-FGS-PD-HGR-0028 is not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-17 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07536 | Verified | On ISO 1B-FGS-PD-P40-0220-01 missing hardware at flange connection to 1B-CTS-MBP01CF001 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07537 | Verified | On ISO 1B-FGS-PD-P40-0210-02 install ground lug at 1B-FGS-PCV-0210 & at 1B-FGS-V-0210 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07538 | Verified | On ISO 1B-FGS-PD-P40-0210-02 install ground wire at 1B-FGS-PCV-0210 & at 1B-FGS-V-0211 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07539 | Verified | On ISO 1B-FGS-PD-P40-0210-03 Install ground lug at 1B-FGS-PCV-0210 & 1B-FGS-V-0211 and 1B-CTS-EKC01AC103/EKC01-101 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07540 | Verified | On ISO 1B-FGS-PD-P40-0210-03 Install ground wire at 1B-FGS-PCV-0210 & 1B-FGS-V-0211 and 1B-CTS-EKC01AC103/EKC01-102 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07541 | Verified | On ISO 1B-FGS-PD-P40-0220-01 install ground lug at 1B-CTS-MBP01CF001 & 1B-FGS-V-0222 & 1B-FGS-V-0227 & 1B-FGS-V-0226A | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07542 | Verified | On ISO 1B-FGS-PD-P40-0220-01 install ground wire at 1B-CTS-MBP01CF001 & 1B-FGS-V-0222 & 1B-FGS-V-0227 & 1B-FGS-V-0226A | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07543 | Verified | On ISO 1B-FGS-PD-P40-0225-01 install ground lug at 1B-CTS-MBP01CF001 & 1B-CTS-MBP01AA701 & 1B-FGS-V-0225A | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07544 | Verified | On ISO 1B-FGS-PD-P40-0225-01 install ground wire at 1B-CTS-MBP01CF001 & 1B-CTS-MBP01AA701 & 1B-FGS-V-0225A | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07545 | Verified | On ISO 1B-FGS-PD-P40-0225-01 install 1B-CTS-MBP01CF001 (FE) after hydro and degrease | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-12-04 | Kelvin Cook
FGS-03 | FGS-03 | PI07546 | Verified | On ISO 1B-FGS-PD-P40-0227-01 install ground lug at 1B-FGS-V-0227 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07547 | Verified | On ISO 1B-FGS-PD-P40-0227-01 install ground wire at 1B-FGS-V-0227 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07548 | Verified | On ISO 1B-FGS-PD-P40-0230-01 pipe support 1B-FGS-PD-HGR-0112 has loose nut at anchor bolts | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07549 | Verified | On ISO 1B-FGS-PD-P40-0230-01 install ground lug at 1B-CTS-MBP01AA701 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07550 | Verified | On ISO 1B-FGS-PD-P40-0230-01 install ground wire 1B-CTS-MBP01AA701 & 1B-CTS-EKC01AC101/MBP01-105 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07551 | Verified | On ISO 1B-FGS-PD-P40-0235-01 Install ground lug at 1B-CTS-EKC01AC101/MBP01-105 & 1B-CTS-MBP01AA702 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07552 | Verified | On ISO 1B-FGS-PD-P40-0235-01 Install ground wire 1B-CTS-MBP01AA702 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07553 | Verified | On ISO 1B-FGS-PD-P40-0236-01 remove blind flange after pipe test | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07554 | Verified | On ISO 1B-FGS-PD-P40-0236-01 install ground lug 1B-CTS-MBP01AA702 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07555 | Verified | On ISO 1B-FGS-PD-P40-0236-01 install ground wire 1B-CTS-MBP01AA702 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07556 | Verified | On ISO 1B-FGS-PD-P40-0236-02 instrument 1B-FGS-FO-0236 is not installed | B | P | John Schanno | McD | 2019-09-27 | John Schanno | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07557 | Verified | On ISO 1B-FGS-PD-P40-0236-02 install ground lug at flange connection to 1B-FGS-FO-0236 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07558 | Verified | On ISO 1B-FGS-PD-P40-0236-02 install ground wire at flange connection to 1B-FGS-FO-0236 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07559 | Verified | On ISO 1B-FGS-PD-P40-0236-02 missing bolts and gasket at flange connection to 1B-FGS-FO-0236 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-17 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07560 | Verified | On ISO 1B-FGS-PD-P40-0242-01 pipe support 1B-FGS-PD-HGR-0089 is not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-17 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07561 | Verified | On ISO 1B-FGS-PD-P40-0242-01 remove rigging from spool 0242-2 | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-17 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07562 | Verified | On ISO 1B-FGS-PD-P40-0242-0 install ground lug at 1B-FGS-T-0250/Y | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07563 | Verified | On ISO 1B-FGS-PD-P40-0242-0 install ground wire at 1B-FGS-T-0250/Y | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07564 | Verified | On ISO 1B-FGS-PD-P40-0242-02 pipe support 1B-FGS-PD-HGR-0090 & 0091 & 0092 are not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07565 | Verified | On ISO 1B-FGS-PD-P40-0242-02 field weld 1 not made | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07566 | Verified | On ISO 1B-FGS-PD-P40-0245-01 install ground lug at 1B-CTS-MBP01AA711 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-17 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07567 | Verified | On ISO 1B-FGS-PD-P40-0245-01 install ground wire at 1B-CTS-MBP01AA712 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07568 | Verified | On ISO 1B-FGS-PD-P40-0246-01 instrument 1B-FGS-FO-0245 is not installed | B | P | William Mitchell | McD | 2019-09-27 | William Mitchell | Const | 2019-12-23 | Michael Law | 2020-01-09 | Kelvin Cook
FGS-03 | FGS-03 | PI07569 | Verified | On ISO 1B-FGS-PD-P40-0246-02 remove rigging from spool 0246-2 | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-17 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07570 | Verified | On ISO 1B-FGS-PD-P40-0246-02 spool 0246-1 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07571 | Verified | On ISO 1B-FGS-PD-P40-0246-02 pipe support 1B-FGS-HGR-0126 & 0129 & 0130 are not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-17 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07572 | Verified | On ISO 1B-FGS-PD-P40-0246-03 pipe support 1B-FGS-PD-HGR-0123 ubolt is not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-17 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07573 | Verified | On ISO 1B-FGS-PD-P40-0250-01 install ground lug at 1B-CTS-EKE01AC101/102/ TP-1BMP01-107 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-17 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07574 | Verified | On ISO 1B-FGS-PD-P40-0250-01 install ground wire at 1B-CTS-EKE01AC101/102/ TP-1BMP01-107 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07575 | Verified | On ISO 1B-FGS-PD-P40-0250-02 remove blind flange after pipe test | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07576 | Verified | On ISO 1B-FGS-PD-P40-0250-02 install ground lug at 1B-CTS-EKE01BB101/MBP01-117 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07577 | Verified | On ISO 1B-FGS-PD-P40-0250-02 install ground wire at 1B-CTS-EKE01BB101/MBP01-117 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07578 | Verified | On ISO 1B-FGS-PD-P40-0260-01 pipe support 1B-FGS-PD-HGR-0082 install shim plate as needed to close gap at shoe | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-17 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07579 | Verified | On ISO 1B-FGS-PD-P40-0260-01 pipe support 1B-FGS-PD-HGR-0037 tighten clamp at shoe | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07580 | Verified | On ISO 1B-FGS-PD-P40-0260-01 remove valves and install sw cap at field weld 5 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07581 | Verified | On ISO 1B-FGS-PD-P40-0260-02 install ground lug at 1B-FGS-V-0260 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07582 | Verified | On ISO 1B-FGS-PD-P40-0260-02 install ground wire at 1B-FGS-V-0260 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07583 | Verified | On ISO 1B-FGS-PD-P40-0265-01 missing cap screws 8 total at flange connection to valve 1B-FGS-V-0263 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07584 | Verified | On ISO 1B-FGS-PD-P40-0265-01 install ground lug at 1B-FGS-V-0263 & 1B-FGS-PCV-0260A | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07585 | Verified | On ISO 1B-FGS-PD-P40-0265-01 install ground wire at 1B-FGS-V-0263 & 1B-FGS-PCV-0260A | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07586 | Verified | On ISO 1B-FGS-PD-P40-0265-02 install ground lug at 1B-FGS-PCV-0260A & 1B-FGS-V-0264 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07587 | Verified | On ISO 1B-FGS-PD-P40-0265-02 install ground wire at 1B-FGS-PCV-0260A & 1B-FGS-V-0265 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07588 | Verified | On ISO 1B-FGS-PD-P40-0270-01 anti seize bolts at flange connection to SRV-0270 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07589 | Verified | On ISO 1B-FGS-PD-P40-0270-01 install ground lug at 1B-FGS-SRV-0270 & 1B-FGS-FE-8100 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07590 | Verified | On ISO 1B-FGS-PD-P40-0270-01 install ground wire at 1B-FGS-SRV-0270 & 1B-FGS-FE-8100 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07591 | Verified | On ISO 1B-FGS-PD-P40-0270-01 missing bolts at flange connection to 1B-FGS-FE-8100 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07592 | Verified | On ISO 1B-FGS-PD-P40-0271-01 anti seize bolts at flange connection to SRV-0270 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-17 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07593 | Verified | On ISO 1B-FGS-PD-P40-0271-01 install ground lug at 1B-FGS-SRV-0270 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07594 | Verified | On ISO 1B-FGS-PD-P40-0271-01 install ground wire at 1B-FGS-SRV-0270 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07595 | Verified | On ISO 1B-FGS-PD-P40-0271-01 pipe support 1B-FGS-PD-HGR-0051 has loose ubolt | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07596 | Verified | On ISO 1B-FGS-PD-P40-0271-01 rain cap 1B-FGS-RC-0271 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07597 | Verified | On ISO 1B-FGS-PD-P40-0310-01 remove blind flange after pipe test | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07598 | Verified | On ISO 1B-FGS-PD-P40-0310-01 install ground lug at 1B-CTS-EKE01BB101/ MBP-01-118 & 1B-CTS-MBP01AT-101/ MBP01-110 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07599 | Verified | On ISO 1B-FGS-PD-P40-0310-01 install ground wire at 1B-CTS-EKE01BB101/ MBP-01-118 & 1B-CTS-MBP01AT-101/ MBP01-111 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07600 | Verified | On ISO 1B-FGS-PD-P40-0320-01 pipe support 1B-FGS-PD-HGr-0066 missing hose clamps | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-17 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07601 | Verified | On ISO 1B-FGS-PD-P40-0320-01 remove blind flange after pipe test | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07602 | Verified | On ISO 1B-FGS-PD-P40-0320-02 pipe support 1B-FGS-PD-HGr-0067 missing hose clamps | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-17 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07603 | Verified | On ISO 1B-FGS-PD-P40-0320-02 install ground lug at all flange connection | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07604 | Verified | On ISO 1B-FGS-PD-P40-0320-02 install ground wire at all flange connection | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07605 | Verified | On ISO 1B-FGS-PD-P40-0320-02 at flange connection 1BCTS-MBP02/MBP02-101 bend over lock washer after torque | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07606 | Verified | ISO 1B-FGS-PD-P41-0201-01 install bird screen | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07607 | Verified | ISO 1B-FGS-PD-P41-0201-01 install ground lug at 1B-CTS-EKE01AT101/ EKE01-104 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07608 | Verified | ISO 1B-FGS-PD-P41-0201-01 install ground wire at 1B-CTS-EKE01AT101/ EKE01-105 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07609 | Verified | ISO 1B-FGS-PD-P41-0202-01 install bird screen | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07610 | Verified | ISO 1B-FGS-PD-P41-0202-01 install ground lug at 1B-CTS-EKE01AT-101/EKE01-105 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07611 | Verified | ISO 1B-FGS-PD-P41-0202-01 install ground wire at 1B-CTS-EKE01AT-101/EKE01-106 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07612 | Verified | ISO 1B-FGS-PD-P41-0204-01 missing cap | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-11 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07613 | Verified | ISO 1B-FGS-PD-P41-0205-01 install ground lug at 10-FGS-T-0205/A2 & 1B-CTS-EKE01AT101/ EKE01-103 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07614 | Verified | ISO 1B-FGS-PD-P41-0205-01 install ground wire at 10-FGS-T-0205/A2 & 1B-CTS-EKE01AT101/ EKE01-104 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07615 | Verified | On ISO 1B-FGS-PD-P41-0210-01 pipe spool 0210-2 & 0210-3 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07616 | Verified | On ISO 1B-FGS-PD-P41-0210-01 valves 1B-FGS-V-0209B & 0209C rotate valve handle or stem to make it operator friendly | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-18 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07617 | Verified | On ISO 1B-FGS-PD-P41-0210-01 valves 1B-FGS-V-0209A replace rubber valve handle | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07618 | Verified | On ISO 1B-FGS-PD-P41-0210-01 missing threaded cap at valve 1B-FGS-V-0209B | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-18 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07619 | Verified | On ISO 1B-FGS-PD-P41-0210-02 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-18 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07620 | Verified | On ISO 1B-FGS-PD-P41-0210-03 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07621 | Verified | On ISO 1B-FGS-PD-P41-0211-01 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07622 | Verified | On ISO 1B-FGS-PD-P41-0212-01 pipe support 1B-FGS-PD-HGR-0290 & 0291 & 0292 are not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07623 | Verified | On ISO 1B-FGS-PD-P41-0212-01 pipe support 1B-FGS-PD-HGR-0293 & 0294 & 0295 verify double nuts are snug | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07624 | Verified | On ISO 1B-FGS-PD-P41-0212-01 anti seize bolts at flange connection to 1B-CTS-EKC01AC103/EKC01-103 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-18 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07625 | Verified | On ISO 1B-FGS-PD-P41-0215-01 pipe support 1B-FGS-PD-HGR-0145 & 0146 are not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07626 | Verified | On ISO 1B-FGS-PD-P41-0215-01 install ground lug at 1B-FGS-T-0250/L2 & 1B-CTS-EKEC01AC103/ EKC01-104 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07627 | Verified | On ISO 1B-FGS-PD-P41-0215-01 install ground wire at 1B-FGS-T-0250/L2 & 1B-CTS-EKEC01AC103/ EKC01-105 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07628 | Verified | On ISO 1B-FGS-PD-P41-0215-01 flange to 1B-FGS-T-0250/L2 is crooked and loose bolts | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07629 | Verified | On ISO 1B-FGS-PD-P41-0220-01 pipe support 1B-FGS-PD-HGR-0267 & 0265 & 0266 verify double nut are snug | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07630 | Verified | On ISO 1B-FGS-PD-P41-0220-01 pipe support 1B-FGS-PD-HGR-0262 & 0263 & 0264 is not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07631 | Verified | On ISO 1B-FGS-PD-P41-0220-01 pipe support 1B-FGS-PD-HGR-0258 & 0259 remove 2X4 install proper shim plate | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07632 | Verified | On ISO 1B-FGS-PD-P41-0220-01 valve 1B-FGS-V-0227A & 0227B & 0227C rotate handle to make them operator friendly | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-18 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07633 | Verified | On ISO 1B-FGS-PD-P41-0220-02 pipe support 1B-FGS-PD-HGR-0273 & 0272 & 0274 are not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07634 | Verified | On ISO 1B-FGS-PD-P41-0220-02 pipe support 1B-FGS-PD-HGR-0275 & 0276 & 0277 verify double nut are snug | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07635 | Verified | On ISO 1B-FGS-PD-P41-0220-02 pipe support 1B-FGS-PD-HGR-0268 & 0269 remove 2X4 install proper shim plate | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07636 | Verified | On ISO 1B-FGS-PD-P41-0220-02 valve 1B-FGS-V-0221A rotate stem to the east. Missing valve handle stop | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07637 | Verified | On ISO 1B-FGS-PD-P41-0220-03 pipe support 1B-FGS-PD-HGR-0284 & 0283 & 0282 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07638 | Verified | On ISO 1B-FGS-PD-P41-0220-03 pipe support 1B-FGS-PD-HGR-0285 & 0286 & 0287 verify double nut are snug | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07639 | Verified | On ISO 1B-FGS-PD-P41-0220-03 pipe support 1B-FGS-PD-HGR-0278 & 0279 remove 2X4 install proper shim plate | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07640 | Verified | On ISO 1B-FGS-PD-P41-0220-03 valve 1B-FGS-V-0220C & 0220B & 0220A rotate handle/stems to make them operator friendly | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07641 | Verified | On ISO 1B-FGS-PD-P41-0225-01 pipe support 1B-FGS-PD-HGr-0329 & 0327 have loose ubolt | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07642 | Verified | On ISO 1B-FGS-PD-P41-0225-01 pipe support 1B-FGS-PD-HGR-0326 slide shoe to top of support properly | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07643 | Verified | On ISO 1B-FGS-PD-P41-0225-01 pipe support 1B-FGS-PD-HGR-0325 slide shoe to top of beam | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07644 | Verified | On ISO 1B-FGS-PD-P41-0225-01 rotate valve 1B-FGS-V-0223C stem to the north | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07645 | Verified | On ISO 1B-FGS-PD-P41-0225-01 missing threaded cap at valve 1B-FGS-V-0223B | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07646 | Verified | On ISO 1B-FGS-PD-P41-0225-02 pipe support 1B-FGS-PD-HGR-0313 has loose ubolt | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07647 | Verified | On ISO 1B-FGS-PD-P41-0225-02 rotate valve 1B-FGS-V-0224A stem to the east | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07648 | Verified | On ISO 1B-FGS-PD-P41-0225-02 missing threaded cap at valve 1B-FGS-V-0224B | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07649 | Verified | On ISO 1B-FGS-PD-P41-0225-03 pipe support 1B-FGS-PD-HGR-0330 & 0331 & 0332 & 0334 are not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07650 | Verified | On ISO 1B-FGS-PD-P41-0225-03 pipe support 1B-FGS-PD-HGR-0336 & 0335 verify double nut are snug | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07651 | Verified | On ISO 1B-FGS-PD-P41-0225-04 pipe support 1B-FGS-PD-HGR-0319 & 0318 & 0317 & 0316 are not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07652 | Verified | On ISO 1B-FGS-PD-P41-0225-04 pipe support 1B-FGS-PD-HGR-0320 missing ubolt | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07653 | Verified | On ISO 1B-FGS-PD-P41-0225-03 pipe support 1B-FGS-PD-HGR-0322 & 0321 verify double nut are snug | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07654 | Verified | On ISO 1B-FGS-PD-P41-0230-01 pipe support 1B-FGS-PD-HGR-0299 has loose ubolt | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07655 | Verified | On ISO 1B-FGS-PD-P41-0230-01 rotate valve 1B-FGS-V-0230A stem to the east for operator friendly | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07656 | Verified | On ISO 1B-FGS-PD-P41-0230-01 missing threaded cap at valve 1B-FGS-V-0230B | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07657 | Verified | On ISO 1B-FGS-PD-P41-0230-02 pipe support 1B-FGS-PD-HGR-0305 & 0304 & 0303 & 0302 are not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07658 | Verified | On ISO 1B-FGS-PD-P41-0230-02 pipe support 1B-FGS-PD-HGR-0307 & 0306 & 0308 verify double nut are snug | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07659 | Verified | On ISO 1B-FGS-PD-P41-0235-01 pipe support 1B-FGS-PD-HGR-0371 is not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07660 | Verified | On ISO 1B-FGS-PD-P41-0235-01 pipe support 1B-FGS-PD-HGR-0367 tighten 2 bolt clamps shoe | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07661 | Verified | On ISO 1B-FGS-PD-P41-0235-01 missing threaded cap at valve 1B-FGS-V-0235B | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07662 | Verified | On ISO 1B-FGS-PD-P41-0235-02 pipe support 1B-FGS-PD-HGR-0377 & 0376 & 0375 & 0374 are not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07663 | Verified | On ISO 1B-FGS-PD-P41-0235-02 pipe support 1B-FGS-PD-HGR-0378 missing ubolt | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07664 | Verified | On ISO 1B-FGS-PD-P41-0235-02 pipe support 1B-FGS-PD-HGR-0380 has loose ubolt | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07665 | Verified | ISO 1B-FGS-PD-P41-0238-01 flange connection to 1B-CTS-EKC01A101/MBP01-108 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07666 | Verified | ISO 1B-FGS-PD-P41-0239-01 install ground lug at 1B-CTS-EKC01101/ MBP01-106 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07667 | Verified | ISO 1B-FGS-PD-P41-0239-01 install ground wire at 1B-CTS-EKC01101/ MBP01-106 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07668 | Verified | ISO 1B-FGS-PD-P41-0240-01 install ground lug at 1B-FGS-T-0250/A1 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07669 | Verified | ISO 1B-FGS-PD-P41-0240-01 install ground wire at 1B-FGS-T-0250/A1 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07670 | Verified | ISO 1B-FGS-PD-P41-0241-01 install ground lug at 1B-FGS-T-0250/A2 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07671 | Verified | ISO 1B-FGS-PD-P41-0241-01 install ground wire at 1B-FGS-T-0250/A2 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07672 | Verified | ISO 1B-FGS-PD-P41-0250-01 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07673 | Verified | On ISO 1B-FGS-PD-P41-0255-01 install ground lug at 1B-FGS-SRV-0250 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-18 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07674 | Verified | On ISO 1B-FGS-PD-P41-0255-01 install ground wire at 1B-FGS-SRV-0250 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07675 | Verified | On ISO 1B-FGS-PD-P41-0255-01 anti sieze bolts at flange connection to SRV-0250 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-18 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07676 | Verified | On ISO 1B-FGS-PD-P41-0260-01 remove tape and install bird screen | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07677 | Verified | On ISO 1B-FGS-PD-P41-0260-01 need pipe dope at thread cap on valve 1B-FGS-V-0261B | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07678 | Verified | On ISO 1B-FGS-PD-P41-0260-01 valve 1B-FGS-V-0261B & 0261A & 1A-FGS-V-0261C make handles operator friendly | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07679 | Verified | ISO 1B-FGS-PD-P41-0260-02 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07680 | Verified | On ISO 1B-FGS-PD-P41-0265-01 pipe support 1B-FGS-PD-HGR-0136 has no ubolt | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07681 | Verified | On ISO 1B-FGS-PD-P41-0265-01 install ground lug at 1B-FGS-PCV-0260B | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-18 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07682 | Verified | On ISO 1B-FGS-PD-P41-0265-01 install ground wire at 1B-FGS-PCV-0260B | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07683 | Verified | On ISO 1B-FGS-PD-P41-0265-01 anti sieze bolts at flange connection to 1B-FGS-PCV-0260B | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-18 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07684 | Verified | On ISO 1B-FGS-PD-P41-0265-01 pipe support 1B-FGS-PD-HGR-0054 has loose ubolt | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-18 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07685 | Verified | On ISO 1B-FGS-PD-P41-0270-03 install bird screen | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07686 | Verified | On ISO 1B-FGS-PD-P41-0270-03 pipe support 1B-FGS-PD-HGr-0053 has loose ubolt and missing nuts | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07687 | Verified | On ISO 1B-FGS-PD-P41-0270-03 pipe support 1B-FGS-PD-HGR-0052 shorten spool so HGR-0052 sits on top of steel approx 2" | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07688 | Verified | On ISO 1B-FGS-PD-P41-0270-03 missing threaded cap on valve 1B-FGS-V-0280B | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07689 | Verified | On ISO 1B-FGS-PD-P41-0270-03 rotate valve 1B-FGS-V-0280B stem up | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07690 | Verified | On ISO 1B-FGS-PD-P41-0285-01 pipe support 1B-FGS-V-0140 & 0141 & 0142 are not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07691 | Verified | On ISO 1B-FGS-PD-P41-0285-01 install ground lug at 1B-FGS-T-0250/B1 & at pump out connection | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07692 | Verified | On ISO 1B-FGS-PD-P41-0285-01 install ground wire at 1B-FGS-T-0250/B1 & at pump out connection | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07693 | Verified | On ISO 1B-FGS-PD-P41-0285-01 valve handle for 1B-FGS-V-0285 is damaged | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07694 | Verified | On ISO 1B-FGS-PD-P41-0285-01 no blind installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07695 | Verified | On ISO 1B-FGS-PD-P41-0300-01 spool 0300-2 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07696 | Verified | On ISO 1B-FGS-PD-P41-0300-01 install ground lug at 1B-CTS-EKE01BB101/EKE01-120 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-18 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07697 | Verified | On ISO 1B-FGS-PD-P41-0300-01 install ground wire at 1B-CTS-EKE01BB101/EKE01-121 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-30 | Brad Stanford | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07698 | Verified | On ISO 1B-FGS-PD-P41-0300-01 pipe support 1B-FGS-PD-HGr-0392 has no ubolt | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI07699 | Verified | On ISO 1B-FGS-PD-P41-0300-01 at flange connection to 1B-CTS-EKE01BB101/EK01-120 bolts are extremly long, need to be replaced. And gasket as well | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07700 | Verified | ISO 1B-FGS-PD-P41-0300-02 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07701 | Verified | ISO 1B-FGS-PD-P41-0301-01 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07702 | Verified | ISO 1B-FGS-PD-P41-0301-01 install ground wire at 1B-CTS-EKE01BB101/EKE01-119 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07703 | Verified | ISO 1B-FGS-PD-P41-0301-02 spool 0301-1 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07704 | Verified | ISO 1B-FGS-PD-P41-0301-02 pipe support 1B-FGS-PD-HGR-0483 & 0484 & 0486 are not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07705 | Verified | ISO 1B-FGS-PD-P41-0301-02 install ground lug at 1B-FGS-T-0250/A3 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07706 | Verified | ISO 1B-FGS-PD-P41-0301-02 install ground wire at 1B-FGS-T-0250/A3 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07707 | Verified | ISO 1B-FGS-PD-P41-0302-01 install ground lug at 1B-CTS-EKE01BB101/QJA01-101 | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-15 | Bobby Williams | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI07708 | Verified | ISO 1B-FGS-PD-P41-0302-01 install ground wire at 1B-CTS-EKE01BB101/QJA01-101 | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07709 | Verified | ISO 1B-FGS-PD-P41-0310-01 missing threaded cap on valve 1B-FGS-V-0310B | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07710 | Verified | ISO 1B-FGS-PD-P41-0310-02 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07711 | Verified | ISO 1B-FGS-PD-P41-0310-02 missing threaded cap on valve 1B-FGS-V-0319B | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07712 | Verified | ISO 1B-FGS-PD-P41-0320-04 pipe support 1B-FGS-PD-HGR-0498 & 0499 & 0497 & 0500 are not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07713 | Verified | ISO 1B-FGS-PD-P41-0320-04 pipe support 1B-FGS-PD-HGR-0501 missing ss wrap and hose clamp | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07714 | Verified | ISO 1B-FGS-PD-P41-0320-04 pipe support 1B-FGS-PD-HGR-0502 missing ss wrap and hose clamp | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07715 | Verified | ISO 1B-FGS-PD-P41-0320-04 pipe support 1B-FGS-PD-HGR-0503 is not installed | B | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07716 | Verified | ISO 1B-FGS-PD-P41-0320-04 spool 0320-4 is not installed | A | P | Bobby Williams | McD | 2019-09-27 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI07751 | Verified | 1BFGSX0002, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-02 | Michael Law | 2019-10-02 | Michael Law
FGS-03 | FGS-03 | PI07752 | Verified | 1BFGSX0003, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-03 | FGS-03 | PI07753 | Verified | 1BFGSX0004, Pull Cable | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FGS-03 | FGS-03 | PI07754 | Verified | 1BFGSC0010, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-03 | FGS-03 | PI07755 | Verified | 1BFGSX0003, From Termination | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
FGS-03 | FGS-03 | PI07756 | Verified | 1BFGSX0004, From Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07757 | Verified | 1BCTSL0007A1, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-03 | FGS-03 | PI07758 | Verified | 1BCTSL0007A2, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-03 | FGS-03 | PI07759 | Verified | 1BCTSL0007A3, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-03 | FGS-03 | PI07760 | Verified | 1BCTSL0007B1, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-03 | FGS-03 | PI07761 | Verified | 1BCTSL0007B2, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-03 | FGS-03 | PI07762 | Verified | 1BCTSL0007B3, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-03 | FGS-03 | PI07763 | Verified | 1BCTSL0007C1, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-03 | FGS-03 | PI07764 | Verified | 1BCTSL0007C2, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-03 | FGS-03 | PI07765 | Verified | 1BCTSL0007C3, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-03 | FGS-03 | PI07766 | Verified | 1BCTSL0007G1, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-03 | FGS-03 | PI07767 | Verified | 1BCTSL0007G2, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-03 | FGS-03 | PI07768 | Verified | 1BCTSL0007G3, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const | 2019-10-01 | Dustin Futrell | 2019-10-01 | Michael Law
FGS-03 | FGS-03 | PI07769 | Verified | 1BFGSC0010, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07770 | Verified | 1BFGSX0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI07771 | Verified | 1BFGSX0002, To Termination | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
FGS-03 | FGS-03 | PI07772 | Verified | 1BFGSX0003, To Termination | A | E | Chris Colvin | McD | 2019-09-27 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
FGS-03 | FGS-03 | PI07773 | Verified | 1BFGSX0004, To Termination | A | E | Dustin Futrell | McD | 2019-09-27 | Dustin Futrell | Const |  |  | 2019-10-30 | Fred Michael
FGS-03 | FGS-03 | PI08461 | Verified | Valve handles 1B-FGS-V-0264 & 0263 position indication is incorrect. Open is closed & closed is open. | B | P | Bobby Williams | McD | 2019-10-03 | Bobby Williams | Const | 2019-12-06 | Bobby Williams | 2019-12-11 | Shannon Scott
FGS-03 | FGS-03 | PI09334 | Verified | Test Package FGS-T-19 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI09335 | Verified | Test Package FGS-T-23 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-30 | Kelvin Cook
FGS-03 | FGS-03 | PI09336 | Verified | Test Package FGS-T-24 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI09337 | Verified | Test Package FGS-T-25 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI09338 | Verified | Test Package FGS-T-26 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI09339 | Verified | Test Package FGS-T-29 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI09340 | Verified | Test Package FGS-T-30 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-19 | Kelvin Cook
FGS-03 | FGS-03 | PI09341 | Verified | Test Package FGS-T-31 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const |  |  | 2019-10-28 | Kelvin Cook
FGS-03 | FGS-03 | PI09342 | Verified | Test Package FGS-T-32 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const | 2019-10-10 | Kelvin Cook | 2019-10-10 | Kelvin Cook
FGS-03 | FGS-03 | PI09343 | Verified | Test Package FGS-T-33 need to be tested | A | P | Kelvin Cook | McD | 2019-10-09 | Kelvin Cook | Const | 2019-10-10 | Kelvin Cook | 2019-10-10 | Kelvin Cook
FGS-03 | FGS-03 | PI09359 | Verified | LK-1B-FGS-PD-P40-0242-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const |  |  | 2019-10-15 | Tom Noble
FGS-03 | FGS-03 | PI09360 | Verified | LK-1B-FGS-PD-P40-0242-02 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const |  |  | 2019-10-15 | Tom Noble
FGS-03 | FGS-03 | PI09361 | Verified | LK-1B-FGS-PD-P41-0210-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-24 | Tom Noble
FGS-03 | FGS-03 | PI09362 | Verified | LK-1B-FGS-PD-P41-0210-02 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-23 | Tom Noble
FGS-03 | FGS-03 | PI09363 | Verified | LK-1B-FGS-PD-P41-0210-03 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-24 | Tom Noble
FGS-03 | FGS-03 | PI09364 | Verified | LK-1B-FGS-PD-P41-0240-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const |  |  | 2019-10-17 | Tom Noble
FGS-03 | FGS-03 | PI09365 | Verified | LK-1B-FGS-PD-P41-0241-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-15 | Tom Noble
FGS-03 | FGS-03 | PI09366 | Verified | LK-1B-FGS-PD-P41-0301-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-10-15 | Tom Noble
FGS-03 | FGS-03 | PI09367 | Verified | LK-1B-FGS-PD-P41-0301-02 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const |  |  | 2019-10-17 | Tom Noble
FGS-03 | FGS-03 | PI09368 | Verified | LK-1B-FGS-PD-P41-0310-02 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-24 | Tom Noble
FGS-03 | FGS-03 | PI09369 | Verified | LK-1B-FGS-PD-P41-0320-04 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-10-23 | Tom Noble
FGS-03 | FGS-03 | PI09355 | Verified | LK-1B-FGS-PD-P40-0271-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const |  |  | 2019-10-15 | Tom Noble
FGS-03 | FGS-03 | PI09356 | Verified | LK-1B-FGS-PD-P41-0300-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-16 | Bobby Williams | 2019-10-16 | Tom Noble
FGS-03 | FGS-03 | PI09357 | Verified | LK-1B-FGS-PD-P41-0300-02 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-09 | Bobby Williams | Const | 2019-10-16 | Bobby Williams | 2019-10-16 | Tom Noble
FGS-03 | FGS-03 | PI09630 | Verified | LK-1B-FGS-PD-P41-0286-01 - Needs Welds Cleared | A | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Const |  |  | 2019-10-29 | Tom Noble
FGS-03 | FGS-03 | PI10247 | Verified | Install 1B-FGS-LSH-0221 | A | I | Gonzalo Pena | McD | 2019-10-23 | Gonzalo Pena | Const | 2019-10-30 | Gonzalo Pena | 2019-10-30 | Michael Law
FGS-03 | FGS-03 | PI12661 | Verified | Install 1B-FGS-TE-8100. | B | I | Gonzalo Pena | McD | 2019-10-31 | Gonzalo Pena | Const | 2019-12-07 | Gonzalo Pena | 2019-12-20 | Albert Burge
FGS-03 | FGS-03 | PI16198 | Verified | 1BEKC01BC103 - Corrosion inside Dew Point panel | B | E | Mike Tabbert | McD | 2020-01-20 | Mike Tabbert | Comm | 2020-02-07 | Mike Tabbert | 2020-02-10 | Fred Michael
FGS-03 | FGS-03 | PI16199 | Verified | The purge/vent valves are installed close to the safety relief valve (1B-FGS-SRV-0270). Valve handles hits the connection flange (1B-FGS-V-0280B & 1B-FGS-V-0280C) | B | P | James Beech | McD | 2020-01-20 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-03-09 | Nelson Eichelberger
FGS-03 | FGS-03 | PI16266 | Verified | Red line LK-1B-FGS-ME-PID-0001; Piping & Instrumentation Diagram Fuel Gas System to indicate 1B-FGS-FIT-8100; Duct Burner Supply Pressure Transmitter | C | P | Charles Worthington | McD | 2020-01-28 | Charles Worthington | Comm | 2020-04-28 | Charles Worthington | 2020-06-16 | Dave Goldak
FGS-03 | FGS-03 | PI16267 | Verified | Dew Point Heater Unit valves 1B-EKC01AA904, 1B-EKC01AA905, 1B-EKC01AA906, 1B-EKC01AA907 are inaccessible | D | P | Michael Law | McD | 2020-01-28 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-08-20 | Nelson Eichelberger
FGS-03 | FGS-03 | PI16268 | Verified | Replace rusted screws and remove rust from inside panel panels at 1BEKC01BC103; Dew Point Heater Panel | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Fred Michael
FGS-03 | FGS-03 | PI16269 | Verified | U-Bolt Support needed on vertical Fuel Gas 12" piping between first above ground flange to horizontal turn at pipe rack Line No. 12-1B-FGS-0210 | B | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-02-21 | John Watts
FGS-03 | FGS-03 | PI16270 | Verified | 1st horizontal support on 12" fuel gas header in pipe rack is not installed according to ISO | B | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-12 | Joseph Lamb | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16271 | Verified | 1B-FGS-V-0209C; FG Header Vent Valve, 1" line needs missing support installed | C | P | Kelvin Cook | McD | 2020-01-28 | Kelvin Cook | Comm | 2020-02-10 | Kelvin Cook | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16272 | Verified | 1B-FGS-V-0209B; FG Header Nitrogen Purge Valve, 1" line needs cap | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-05-08 | James Beech | 2020-05-08 | Michael Law
FGS-03 | FGS-03 | PI16273 | Verified | Flange ground not connected downstream of 1B-FGS-V-0211; Fuel Gas Isolation Valve | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16274 | Verified | Remove plastic from Dew Point Heater Panel | C | C | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Fred Michael
FGS-03 | FGS-03 | PI16275 | Verified | Need sign for Dew Point Heater Panel indicating "DO NOT OPEN WHEN SYSTEM IS IN OPERATION" | D | E | Michael Law | McD | 2020-01-28 | Michael Law | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16276 | Verified | Clean carbon contamination from 1B Fuel Gas Dew Point Heater Panel | C | X | Jorge Alexander | McD | 2020-01-28 | Jorge Alexander | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Shannon Scott
FGS-03 | FGS-03 | PI16277 | Verified | Remove dents in 1B Fuel Gas Dew Point Heater Panel west door | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-10 | Fred Michael
FGS-03 | FGS-03 | PI16278 | Verified | Pour all conduit seals at 1B Fuel Gas Dew Point Heater | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-07 | Mike Tabbert | 2020-02-07 | Shannon Scott
FGS-03 | FGS-03 | PI16279 | Verified | Replace phenolic label on 1B Fuel Gas Dew Point Heater Panel | C | E | Mike Tabbert | McD | 2020-01-28 | Mike Tabbert | Comm | 2020-02-07 | Fred Michael | 2020-03-04 | Dave Goldak
FGS-03 | FGS-03 | PI16280 | Verified | Entergy to inspect inside 1B Fuel Gas Dew Point Heater Panel during outage | C | E | Shannon Scott | McD | 2020-01-28 | Shannon Scott | Comm |  |  | 2020-02-02 | Shannon Scott
FGS-03 | FGS-03 | PI16281 | Verified | Remove temporary fitting from 1B-FGS-V-0227B; Fuel Gas Header Nitrogen Purge Valve | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-05-08 | James Beech | 2020-05-08 | Michael Law
FGS-03 | FGS-03 | PI16282 | Verified | Ground not connected at 1B Fuel Gas Dew Point Heater outlet flange | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16283 | Verified | Shorten Instrument Air tubing vertical support baseplate anchor bolts at 1B Fuel Gas Dew Point Heater | C | I | Gonzalo Pena | McD | 2020-01-28 | Gonzalo Pena | Comm | 2020-01-30 | Gonzalo Pena | 2020-02-05 | Shannon Scott
FGS-03 | FGS-03 | PI16284 | Verified | Plug all unused conduit at 1B GT Fuel Gas Flow Meter | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16285 | Verified | Inlet flange to 1B GT Fuel Gas Flow Meter, ground not connected | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16286 | Verified | Face plate missing on Instrument Air regulator at 1B GT Fuel Gas Emergency Shutoff Valve | C | I | Gonzalo Pena | McD | 2020-01-28 | Gonzalo Pena | Comm | 2020-01-30 | Gonzalo Pena | 2020-02-05 | Shannon Scott
FGS-03 | FGS-03 | PI16287 | Verified | Replace bent tubing at 1B GT Fuel Gas Emergency Shutoff Valve | C | I | Gonzalo Pena | McD | 2020-01-28 | Gonzalo Pena | Comm | 2020-01-30 | Gonzalo Pena | 2020-02-05 | Shannon Scott
FGS-03 | FGS-03 | PI16288 | Verified | Square up conduit at E side of 1B GT Fuel Gas Emergency Shutoff Valve | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16289 | Verified | Conduit at E side of 1B GT Fuel Gas Emergency Shutoff Valve is loose, needs additional support | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16290 | Verified | Conduit at E side of 1B GT Fuel Gas Emergency Shutoff Valve missing condolet cover | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16291 | Verified | Complete insulation on 1B-FGS-V-0230C; Vent Valve 1" line, downstream of 1B GT Fuel Gas Emergency Shutoff Valve | C | Q | Richard McSpadden | PCI | 2020-01-28 | Richard McSpadden | Comm | 2020-08-07 | Richard McSpadden | 2020-08-20 | Nelson Eichelberger
FGS-03 | FGS-03 | PI16292 | Verified | Replace/Straighten Instrument Air tubing tray to 1B GT Fuel Gas Temperature Control Valve | C | I | Gonzalo Pena | McD | 2020-01-28 | Gonzalo Pena | Comm | 2020-01-30 | Gonzalo Pena | 2020-02-05 | Shannon Scott
FGS-03 | FGS-03 | PI16293 | Verified | Replace bent and crimped tubing at upper N side of 1B GT Fuel Gas Temperature Control Valve | C | I | Gonzalo Pena | McD | 2020-01-28 | Gonzalo Pena | Comm | 2020-01-30 | Gonzalo Pena | 2020-02-05 | Shannon Scott
FGS-03 | FGS-03 | PI16294 | Verified | Flex conduit to 1B GT Fuel Gas Temperature Control Valve is broken, repair and pour seal | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-17 | Mike Tabbert | 2020-02-21 | John Watts
FGS-03 | FGS-03 | PI16295 | Verified | Clean paint splatter off of 1B-FGS-TI-0235; Fuel Gas Header Temperature Indicator | C | X | Jerry Smith | McD | 2020-01-28 | Jerry Smith | Comm | 2020-03-11 | Alan Huntsman | 2020-04-06 | Bernard Stasse
FGS-03 | FGS-03 | PI16296 | Verified | Condolet covers missing from 1B GT Fuel Gas Heater A/B to cable tray | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16297 | Verified | Ground missing at 1B Fuel Gas Inlet Scrubber outlet flange | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-10 | Fred Michael
FGS-03 | FGS-03 | PI16298 | Verified | Condolet cover screws missing on E side of 1B GT Fuel Gas Inlet Filter | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16299 | Verified | Replace 1B Fuel Gas Inlet Scrubber bottom drain blind flange | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-02-12 | Shannon Scott
FGS-03 | FGS-03 | PI16300 | Verified | Remove plastic from valves at top of Fuel Gas Inlet Scrubber | C | C | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16301 | Verified | 1B Fuel Gas Inlet Scrubber vent line needs supported according to the ISO, Line No. 2-1B-FGS-0300 | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-12 | Joseph Lamb | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16302 | Verified | 1BEKE01CL101 Level Controller tubing is bent at 1B Fuel Gas Inlet Scrubber | C | I | Gonzalo Pena | McD | 2020-01-28 | Gonzalo Pena | Comm | 2020-01-30 | Gonzalo Pena | 2020-02-05 | Shannon Scott
FGS-03 | FGS-03 | PI16303 | Verified | Replace Instrument Air needle valve handle at 1BEKE01CL101 Level Controller tubing | C | I | Gonzalo Pena | McD | 2020-01-28 | Gonzalo Pena | Comm | 2020-01-30 | Gonzalo Pena | 2020-02-10 | Shannon Scott
FGS-03 | FGS-03 | PI16304 | Verified | Condolet cover is missing at West side of 1B GT Fuel Gas Inlet Filter Skid | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-15 | Shannon Scott
FGS-03 | FGS-03 | PI16305 | Verified | Ground missing at 1B Fuel Gas Inlet Filter outlet flange | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16306 | Verified | Spool piece flange ground jumpers missing at inlet to GT Fuel Gas Enclosure | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-13 | Mike Tabbert | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16307 | Verified | MBP01CL220; 1B GT Fuel Gas Heater Level Switch is loose | C | I | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16308 | Verified | MBP01CL223; 1B GT Fuel Gas Heater Level Switch is loose | C | I | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16309 | Verified | Straighten conduit & fitting at 1B GT Fuel Gas Heater Level Swith rack | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16310 | Verified | Tighten all ground cables at 1B GT Fuel Gas Heater Level Switch rack | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-15 | Shannon Scott
FGS-03 | FGS-03 | PI16311 | Verified | Finish installing insulation Duct Burner Fuel Gas Header piping to Duct Burner Skid | C | Q | Richard McSpadden | PCI | 2020-01-28 | Richard McSpadden | Comm | 2020-10-06 | Eric Policarpio | 2020-10-06 | Dave Goldak
FGS-03 | FGS-03 | PI16312 | Verified | Seal caps at Duct Burner Skid not painted red | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-15 | Shannon Scott
FGS-03 | FGS-03 | PI16313 | Verified | Install uni-strut caps throughout sub-system | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16314 | Verified | Flange grounds missing at 1B-FGS-PCV-0260A; Duct Burner Gas Supply Pressure Control Valve inlet and outlet flange | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16315 | Verified | Flange jumper grounds missing at 1B-FGS-V-0264; Duct Burner Gas Supply Header Isolation Valve | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16316 | Verified | All ground cables downstream of 1B-FGS-V-0264; Duct Burner Gas Supply Header Isolation Valve are disconnected | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16317 | Verified | Ground cable loose at downstream flange of 1B-SRV-0270; Duct Burner Gas Supply Header Safety Relief Valve | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16318 | Verified | All U-bolts need washers at Duct Burner Gas Supply Header piping, Line No. 6-1B-FGS-0265, 8-1B-FGS-0270, and 8-1B-FGS-0275 | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-12 | Joseph Lamb | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16319 | Verified | Conduit needs condolet covers at 1B-FIT-8100; Duct Burner Gas Supply Header Pressure Transmitter | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16320 | Verified | Flange ground loose downstream of 1B-FGS-TE-8100; Duct Burner Gas Supply Header Temperature Element | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16321 | Verified | Ground cable is loose at Check Valve, inlet to Duct Burner Skid | B | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-12 | Fred Michael | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16322 | Verified | U-Bolt needs double nuts at Check Valve, inlet to Duct Burner Skid | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-12 | Joseph Lamb | 2020-02-13 | Shannon Scott
FGS-03 | FGS-03 | PI16323 | Verified | 1B Fuel Gas Filter Separator (1B-CTS-EKE01AT101): Complete insulation, balance of skid piping and equipment. Freeze protection specified. Verify not supposed to be anti-sweat. | C | Q | Richard McSpadden | PCI | 2020-01-28 | Richard McSpadden | Comm | 2021-05-12 | Eric Policarpio | 2021-05-12 | John Watts
FGS-03 | FGS-03 | PI16324 | Verified | 1B Fuel Gas Dew Point Heater (1B-CTS-EKC01AC103) Fuel Gas Heater (1B-CTS-EKC01AC101) Fuel Gas Inlet Scrubber (1B-CTS-EKE01BB101) and Fuel Gas Inlet Air Filter (1B-CTS-MBP01AT101): Complete PP insulation, balance of skid piping and equipment. | C | Q | Richard McSpadden | PCI | 2020-01-28 | Richard McSpadden | Comm | 2021-07-08 | Eric Policarpio | 2021-07-08 | John Watts
FGS-03 | FGS-03 | PI16325 | Verified | Install Anti-Sweat insulation 12-1B-FGS-0208-601D2-AS-1.0 | C | Q | Sheri Fritz | PCI | 2020-01-28 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-08-14 | Dave Goldak
FGS-03 | FGS-03 | PI16326 | Verified | Install Anti-Sweat insulation 12-1B-FGS-0210-601D2-AS-1.0 | C | Q | Sheri Fritz | PCI | 2020-01-28 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-11-11 | Dave Goldak
FGS-03 | FGS-03 | PI16327 | Verified | Incorrect insulation installed 6-1B-FGS-0260-601D2-AS-1.0 Thermal (HC) installed. PID indicated Anti-sweat. | C | Q | Josh Koerner | PCI | 2020-01-28 | Josh Koerner | Comm | 2020-06-18 | Josh Koerner | 2020-07-30 | Dave Goldak
FGS-03 | FGS-03 | PI16328 | Verified | 1B-HGR-0028 missing ubolt and nuts | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-02-21 | John Watts
FGS-03 | FGS-03 | PI16329 | Verified | 1B-HGR-0029 missing longitudinal restraints. See drawings | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-02-21 | John Watts
FGS-03 | FGS-03 | PI16330 | Verified | 1B-HGR-0033 missing restraints. See drawings | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-02-21 | John Watts
FGS-03 | FGS-03 | PI16331 | Verified | 1B-HGR-0034 missing guides. See drawings | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-02-21 | John Watts
FGS-03 | FGS-03 | PI16332 | Verified | 1B-HGR-0034 loose nuts at anchor bolts | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-02-21 | John Watts
FGS-03 | FGS-03 | PI16333 | Verified | 1B-FGS-PD-HGR-0030 install guides, not visible | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-02-21 | John Watts
FGS-03 | FGS-03 | PI16334 | Verified | 1B-FGS-PD-HGR-0032 install guides, not visible | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-03-04 | Dave Goldak
FGS-03 | FGS-03 | PI16335 | Verified | Install tag 1B-FGS-PCV-0210 | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-02-21 | John Watts
FGS-03 | FGS-03 | PI16336 | Verified | Install cap at valve 1B-FGS-V-0210B | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-04-09 | James Beech | 2020-05-27 | Dave Goldak
FGS-03 | FGS-03 | PI16337 | Verified | Install cap at valve 1B-FGS-V-0227B | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-04-09 | James Beech | 2021-04-26 | Keith Pollock
FGS-03 | FGS-03 | PI16338 | Verified | Detached ground jumper at 1B FGS Dew Point Heater skid inlet flange | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-17 | Shannon Scott
FGS-03 | FGS-03 | PI16339 | Verified | Verify presence of TE EKCO1CT003 and 004 in dewpoint heater cabinet (not open during walkdown) | D | E | Dave Goldak | ENT | 2020-01-28 | Dave Goldak | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
FGS-03 | FGS-03 | PI16340 | Verified | Unidentified orifice installed in 1B FGS Flow Meter vendor spool. Update PID and assign equipment number. Hang equipment tag. | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-05-20 | James Beech | 2021-05-07 | John Watts
FGS-03 | FGS-03 | PI16341 | Verified | 1B FGS Flow Meter: Install tag - Valve MBP01AA801 | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-05-26 | James Beech | 2021-04-26 | Keith Pollock
FGS-03 | FGS-03 | PI16342 | Verified | 1B FGS Flow Meter: Install tag - Valve MBP01AA802 | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-05-26 | James Beech | 2021-04-26 | Keith Pollock
FGS-03 | FGS-03 | PI16343 | Verified | 1B FGS Flow Meter: Install tag - TE MBP01CT001 | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-19 | Bobby Williams | 2020-03-10 | John Watts
FGS-03 | FGS-03 | PI16344 | Verified | 1B FGS Flow Meter: Isolation kit installed at inlet and outlet flanges. Remove ground jumpers if not needed | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16345 | Verified | 1B FGS Flow Meter: Remove unused flex connector at end of conduit run. Install plug. | C | I | Gonzalo Pena | McD | 2020-01-28 | Gonzalo Pena | Comm | 2020-01-30 | Gonzalo Pena | 2020-02-06 | Dave Goldak
FGS-03 | FGS-03 | PI16346 | Verified | Extra weldolet and plug installed on bypass line 8-1B-FGS-0227-601D2-AS-1.0. Red line PID. | C | P | Kelvin Cook | McD | 2020-01-28 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2021-05-07 | John Watts
FGS-03 | FGS-03 | PI16347 | Verified | Install Anti-Sweat insulation 8-1B-FGS-0227-601D2-AS-1.0 | C | Q | Richard McSpadden | PCI | 2020-01-28 | Richard McSpadden | Comm | 2020-08-07 | Richard McSpadden | 2020-08-07 | Dave Goldak
FGS-03 | FGS-03 | PI16348 | Verified | Vent at valve 1B-FGS-V-0261C not in safe area. Operator of valve will be in line of fire when vent valve opened. | D | P | Tim Green | McD | 2020-01-28 | Tim Green | Comm | 2021-05-27 | Eric Policarpio | 2021-05-27 | John Watts
FGS-03 | FGS-03 | PI16349 | Verified | Install tag 1B-FGS-STN-0260 | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-03 | FGS-03 | PI16350 | Verified | Complete Insulation Line 6-1B-FGS-0265-601D2-FP-2.0-ET / 8-1B-FGS-0270-301D1-FP-2.0-ET / 8-1B-FGS-0275-301D1-FP-2.0-ET / 1-1B-FGS-0265-601D2-FP-2.0-ET / 2-1B-FGS-0270-301D2-FP-2.0-ET | C | Q | Richard McSpadden | PCI | 2020-01-28 | Richard McSpadden | Comm | 2020-07-28 | Eric Policarpio | 2020-07-28 | Dave Goldak
FGS-03 | FGS-03 | PI16351 | Verified | Install tag 1B-FGS-V-0263 | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-19 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-03 | FGS-03 | PI16352 | Verified | Loose bolts at 1B-FGS-V-0263 | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16353 | Verified | Missing grounds 1B-FGS-PCV-0260A | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-11 | Dave Goldak
FGS-03 | FGS-03 | PI16354 | Verified | Pilot valve connections not 6 pipe diameters from 1B-FGS-PCV-0260A | C | P | Charles Worthington | McD | 2020-01-28 | Charles Worthington | Comm | 2020-06-26 | Bryan Sturgies | 2021-05-07 | John Watts
FGS-03 | FGS-03 | PI16355 | Verified | One flange bolt missing, 1B-FGS-PCV-0260B | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16356 | Verified | Broken ground jumper, 1B-FGS-PCV-0260B | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-11 | Dave Goldak
FGS-03 | FGS-03 | PI16358 | Verified | Install tag 1B-FGS-FE-8100 (ZINK vendor spool - before duct burner skid) | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-03 | FGS-03 | PI16359 | Verified | 1B FGS Emergency Shut-off Valve: Install valve tag 1B-CTS-MBP01AA701 | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-05-27 | James Beech | 2020-06-16 | Dave Goldak
FGS-03 | FGS-03 | PI16360 | Verified | 1B FGS Emergency Shut-off Valve: Broken ground jumper at inlet and outlet flanges | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16361 | Verified | 1B FGS Emergency Shut-off Valve: Numerous missing conduit covers and fasteners | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16362 | Verified | Incomplete welds, pipe support on Line 8-1B-FGS-0236-601D2-HC-1.0 | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16363 | Verified | 12x8 reducer is concentric on PID (Prior to FGS Heaters). Eccentric reducer installed. Red line PID. | C | P | Kelvin Cook | McD | 2020-01-28 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-07-28 | Keith Pollock
FGS-03 | FGS-03 | PI16364 | Verified | Install equipment ID tags Valves 1B-FGS-V-0238 (A&B) | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-03 | FGS-03 | PI16365 | Verified | Complete Insulation Line 1-1B-FGS-0238-601D2-FP-2.0-ET / 1-1B-FGS-0239-601D2-FP-2.0-ET / 1-1B-FGS-0301-601D2-FP-2.0-ET / 1-1B-FGS-0215-601D2-FP-2.0-ET | C | Q | Richard McSpadden | PCI | 2020-01-28 | Richard McSpadden | Comm | 2020-10-06 | Eric Policarpio | 2020-10-06 | Dave Goldak
FGS-03 | FGS-03 | PI16366 | Verified | 1B FGS Drains Tank: Ground jumper missing at flex conduit 1B-FGS-LIT-0220 | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-11 | Dave Goldak
FGS-03 | FGS-03 | PI16367 | Verified | 1B FGS Drains Tank: Conduit cover missing 1B-FGS-LIT-0220 | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-11 | Dave Goldak
FGS-03 | FGS-03 | PI16368 | Verified | 1B-FGS-V-0287 not piped to drain as shown on PID. Cap installed. Red line ? | C | P | Kelvin Cook | McD | 2020-01-28 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-06-16 | Dave Goldak
FGS-03 | FGS-03 | PI16369 | Verified | 1B FGS Heater B: Clean trash and debris from platform | C | C | Tim Gallegos | McD | 2020-01-28 | Tim Gallegos | Comm | 2020-06-16 | Tim Gallegos | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI16370 | Verified | 1B FGS Heater B: Platform missing knee brace (west side)? | C | S | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-12 | Joseph Lamb | 2020-02-17 | Shannon Scott
FGS-03 | FGS-03 | PI16371 | Verified | 1B FGS Heater B: missing ground jumper at flange upstream of Valves MBP01-108 | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16372 | Verified | 1B FGS Heater B: Loose U-bolt and missing nuts, support to manifold (supply and return) for level switches | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16373 | Verified | 1B FGS Heater B: Loose cover LS MBP01CL222 | C | I | Gonzalo Pena | McD | 2020-01-28 | Gonzalo Pena | Comm | 2020-02-13 | James Tanner | 2020-02-17 | Shannon Scott
FGS-03 | FGS-03 | PI16374 | Verified | 1B FGS Heater B: Loose cover LS MBP01CL223 | C | I | Gonzalo Pena | McD | 2020-01-28 | Gonzalo Pena | Comm | 2020-01-30 | Gonzalo Pena | 2020-02-06 | Dave Goldak
FGS-03 | FGS-03 | PI16375 | Verified | 1B FGS Heater B: Loose valve handle MBP01AA831 | C | I | Gonzalo Pena | McD | 2020-01-28 | Gonzalo Pena | Comm | 2020-01-30 | Gonzalo Pena | 2020-02-06 | Dave Goldak
FGS-03 | FGS-03 | PI16376 | Verified | 1B FGS Heater B: Loose valve handle MBP01AA833 | C | I | Gonzalo Pena | McD | 2020-01-28 | Gonzalo Pena | Comm | 2020-01-30 | Gonzalo Pena | 2020-02-06 | Dave Goldak
FGS-03 | FGS-03 | PI16377 | Verified | 1B FGS Heater A and B: Damaged lagging/cladding on top of tank. Used as step. | C | Q | Josh Koerner | PCI | 2020-01-28 | Josh Koerner | Comm | 2020-06-19 | Jason Ezell | 2020-06-19 | Jason Ezell
FGS-03 | FGS-03 | PI16378 | Verified | 1B FGS Heater A: Loose cover LS MBP01CL216 | C | I | Gonzalo Pena | McD | 2020-01-28 | Gonzalo Pena | Comm | 2020-01-30 | Gonzalo Pena | 2020-02-06 | Dave Goldak
FGS-03 | FGS-03 | PI16379 | Verified | 1B FGS Heater A: Install ID tag valve MBP01AA820 | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-02-21 | John Watts
FGS-03 | FGS-03 | PI16380 | Verified | 1B FGS Heater A: Install ID tag valve MBP01AA827 | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-02-21 | John Watts
FGS-03 | FGS-03 | PI16381 | Verified | 1B FGS Heater A: Loose valve handle MBP01AA821 | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-03 | FGS-03 | PI16382 | Verified | Hanger between valves 0240 A/B and TI 0240. Loose clevis bolt. (Line # 8-1B-FGS-0250-601D2-HC-1.0 ) | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-02-21 | John Watts
FGS-03 | FGS-03 | PI16383 | Verified | Hanger between valves 0240 A/B and TI 0240. Loose threaded rod lock nut. (Line # 8-1B-FGS-0250-601D2-HC-1.0 ) | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16384 | Verified | 1B-FGS-V-240 A & B install equip. tag | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-03 | FGS-03 | PI16385 | Verified | Move TI 1B-FGS-TI-0240 to ground level. Cannot be read - no access. | D | I | Michael Law | McD | 2020-01-28 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-04-26 | Keith Pollock
FGS-03 | FGS-03 | PI16386 | Verified | Complete Heat Conservation insulation, Line # 8-1B-FGS-0250-601D2-HC-1.0 / 3-1B-FGS-0245-601D2-HC-1.0 /4-1B-FGS-0246-601D2-HC-1.0 / 3-1B-FGS-0246-601D2-HC-1.0 | C | Q | Richard McSpadden | PCI | 2020-01-28 | Richard McSpadden | Comm | 2021-05-12 | Eric Policarpio | 2021-05-12 | John Watts
FGS-03 | FGS-03 | PI16387 | Verified | 1B-FGS-V-0248B Loose handle nut | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-12 | Joseph Lamb | 2020-03-10 | John Watts
FGS-03 | FGS-03 | PI16388 | Verified | Install tag 1B-FGS-FO-0245 | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-10 | John Watts
FGS-03 | FGS-03 | PI16389 | Verified | Loose and/or missing nuts, supports at Vent lines to 1B FGS Emergency Vent Valve | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-03-10 | John Watts
FGS-03 | FGS-03 | PI16390 | Verified | 1B FGS Emergency Vent Valve: Loose ground jumper, outlet flange | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16391 | Verified | 1B FGS Emergency Vent Valve: Conduit cover missing | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16392 | Verified | 1B FGS Emergency Vent Valve: Install tag to valve MBP01AA711 | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-10 | John Watts
FGS-03 | FGS-03 | PI16393 | Verified | Ground jumpers disonnected 1B-FGS-FO-0236 | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16394 | Verified | 1B FGS Inlet Scrubber: Disconnected grounds - inlet and outlet flanges | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-11 | Dave Goldak
FGS-03 | FGS-03 | PI16395 | Verified | 1B FGS Inlet Scrubber: Complete insulation on FGS Scrubber vessel and manways | C | Q | Richard McSpadden | PCI | 2020-01-28 | Richard McSpadden | Comm | 2020-07-28 | Eric Policarpio | 2020-07-28 | Dave Goldak
FGS-03 | FGS-03 | PI16396 | Verified | 1B FGS Inlet Scrubber: Conduit covers missing to scrubber Control panel | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16397 | Verified | 1B FGS Inlet Scrubber: Install ID tag, EKE01AA144 valve | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-03 | FGS-03 | PI16398 | Verified | 1B FGS Inlet Scrubber: Install ID tag, QEF11AA307 valve | C | P | Tim Green | McD | 2020-01-28 | Tim Green | Comm | 2020-06-01 | Tim Green | 2021-04-26 | Keith Pollock
FGS-03 | FGS-03 | PI16399 | Verified | 1B FGS Inlet Scrubber: Remove plastic and bubble wrap at Relief Valve EKE01AA171. Verify settings. | C | C | Johnny Campbell | McD | 2020-01-28 | Johnny Campbell | Comm | 2020-03-31 | Johnny Campbell | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI16400 | Verified | 1B FGS Inlet Scrubber: Add support clip to Instrument air service supply. Currently shimmed with folded paper. | C | P | James Beech | McD | 2020-01-28 | James Beech | Comm | 2020-02-11 | Charlie English | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16401 | Verified | 1B-FGS-V-310 A, B, & C install equipment tags | C | P | Bobby Williams | McD | 2020-01-28 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-03-04 | Dave Goldak
FGS-03 | FGS-03 | PI16402 | Verified | Missing fasteners, conduit cover at 1B-FGS-TE-1BMP01CT026 | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Comm |  |  | 2020-02-12 | Dave Goldak
FGS-03 | FGS-03 | PI16403 | Verified | Install insulation blanket at inlet flange to 1B CTG | C | Q | Richard McSpadden | PCI | 2020-01-28 | Richard McSpadden | Comm | 2020-07-27 | Eric Policarpio | 2020-07-27 | Dave Goldak
FGS-03 | FGS-03 | PI16449 | Verified | 1A FGS Inlet Scrubber: valve QEF11AA307 not lockable | C | P | Kelvin Cook | McD | 2020-01-29 | Kelvin Cook | Comm | 2020-02-10 | Kelvin Cook | 2020-08-07 | Dave Goldak
FGS-03 | FGS-03 | PI16450 | Verified | 1A FGS Inlet Scrubber: valve QJA01AA105 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-03 | FGS-03 | PI16451 | Verified | 1A FGS Inlet Scrubber: valve QJA01AA107 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-03 | FGS-03 | PI16452 | Verified | 1A FGS Inlet Scrubber: valve QJA01AA115 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-03 | FGS-03 | PI16453 | Verified | 1A FGS Inlet Scrubber: valve EKE01AA961 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-03 | FGS-03 | PI16454 | Verified | 1A FGS Inlet Scrubber: valve EKE01AA959 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-03 | FGS-03 | PI16455 | Verified | 1A FGS Inlet Scrubber: valve QJA01AA110 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-03 | FGS-03 | PI16456 | Verified | 1A FGS Inlet Scrubber: valve QJA01AA108 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-03 | FGS-03 | PI16457 | Verified | 1A FGS Inlet Scrubber: valve QJA01AA109 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-03 | FGS-03 | PI16458 | Verified | 1A FGS Inlet Scrubber: valve EKE01AA960 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-03 | FGS-03 | PI16459 | Verified | 1A FGS Inlet Scrubber: valve QEF11AA306 not lockable | D | P | Kevin Leppert | McD | 2020-01-29 | Kevin Leppert | Comm | 2020-02-10 | Kelvin Cook | 2020-03-11 | John Watts
FGS-03 | FGS-03 | PI16518 | Verified | 1BEKC01GH001 Fuel Gas Dew Point Heater Control Panel - Inside panel needs to be cleaaned (rags, papers, dirt, packing material) | C | E | Chris Colvin | McD | 2020-02-04 | Chris Colvin | Comm |  |  | 2020-02-10 | Fred Michael
FGS-03 | FGS-03 | PI16519 | Verified | 1BEKC01GH001 Fuel Gas Dew Point Heater Control Panel - Cable & wire Tags need heat shrink | C | E | Chris Colvin | McD | 2020-02-04 | Chris Colvin | Comm |  |  | 2020-02-10 | Fred Michael
FGS-03 | FGS-03 | PI16520 | Verified | 1BEKC01GH001 Fuel Gas Dew Point Heater Control Panel - Top of the control panel has hole, the vent has been damaged and is laying on the skid. | C | E | Chris Colvin | McD | 2020-02-04 | Chris Colvin | Comm |  |  | 2020-02-04 | Mike Tabbert
FGS-03 | FGS-03 | PI17842 | Verified | The GT Main B Fuel Gas FCV has a small control oil leak. | C | M | William Mitchell | McD | 2020-03-16 | William Mitchell | Const | 2020-03-31 | William Mitchell | 2021-05-07 | John Watts
FGS-03 | FGS-03 | PI17937 | Verified | See attached photo DSCN2115; Loose nut at base plate, 1B-FGS-HGR-0078 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17938 | Verified | See attached photo DSCN2117; Cold galv. welds, 1B-FGS-HGR-0342 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17939 | Verified | See attached photo DSCN2121; Cold galv. Welds and shoe not centered north/south, 1B-FGS-HGR-0037 | C | X | Tim Green | McD | 2020-03-17 | Tim Green | Comm | 2020-06-30 | Dave Goldak | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17940 | Verified | See attached photo DSCN2124; Nut not installed, 1B-FGS-HGR-0041 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI17941 | Verified | See attached photo DSCN2126; Cold galv. Welds and guides not installed, 1B-FGS-HGR-0042 | C | X | Tim Green | McD | 2020-03-17 | Tim Green | Comm | 2020-06-30 | Mike Tabbert | 2020-07-30 | Dave Goldak
FGS-03 | FGS-03 | PI17942 | Verified | See attached photo DSCN2130; Nut on top of u-bolt not installed, 1B-FGS-HGR-0043 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI17943 | Verified | See attached photo DSCN2132; Cold galv. Welds, 1B-FGS-HGR-0044 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI17944 | Verified | See attached photo DSCN2134; V-0280B stem up as built, V-0280C stem up as built, 1B-FGS-V-0280B,C | D | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
FGS-03 | FGS-03 | PI17945 | Verified | See attached photo DSCN2136; Cold galv. Welds, 1B-FGS-HGR-0044 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI17946 | Verified | See attached photo DSCN2138; Cold galv. Welds, 1B-FGS-HGR-0046 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI17947 | Verified | See attached photo DSCN2140; Cold galv. Welds, 1B-FGS-HGR-0047 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI17948 | Verified | See attached photo DSCN2142; Cold galv. Welds, 1B-FGS-HGR-0048 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI17949 | Verified | See attached photo DSCN2144; Shoe not in contact with support, 1B-FGS-HGR-0035 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17950 | Verified | See attached photo DSCN2146; loose nut at base plate, 1B-FGS-HGR-0036 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17951 | Verified | See attached photo DSCN2149; Different clamp type used, 1B-FGS-HGR-0110 | C | P | Bobby Williams | McD | 2020-03-17 | Bobby Williams | Comm | 2020-03-31 | Bobby Williams | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17952 | Verified | See attached photo DSCN2151; West clamp is loose, 1B-FGS-HGR-0012 | C | P | Tim Green | McD | 2020-03-17 | Tim Green | Comm | 2020-06-30 | Dave Goldak | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17953 | Verified | See attached photo DSCN2153; Cold galv. Welds, 1B-FGS-HGR-0116 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17954 | Verified | See attached photo DSCN2155; Cold galv. Welds and hanger not plumb, 1B-FGS-HGR-0117 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-26 | James Beech | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17955 | Verified | See attached photo DSCN2158; Cold galv. Welds, 1B-FGS-HGR-0018 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17956 | Verified | See attached photo DSCN2160; Loose nuts at anchor for heater A, 1B-FGS heater A | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-12 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17957 | Verified | See attached photo DSCN2162; Loose nut at base plate, 1B-FGS-HGR-0474 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17958 | Verified | See attached photo DSCN2164; Cold galv. Welds, 1B-FGS-HGR-0475 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17959 | Verified | See attached photo DSCN2166; Support installed backwards, 1B-FGS-HGR-0477 | C | P | Gary Pickeral | McD | 2020-03-17 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI17960 | Verified | See attached photo DSCN2168; Guides not installed, 1B-FGS-HGR-0479 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17961 | Verified | See attached photo DSCN2170; Remove valve and weld cap, 1"-1B-FGS-0301-02 | C | P | Tim Green | McD | 2020-03-17 | Tim Green | Comm | 2020-09-15 | Jason Ezell | 2021-04-26 | Keith Pollock
FGS-03 | FGS-03 | PI17962 | Verified | See attached photo DSCN2172; Cold galv. Welds, 1B-FGS-HGR-0410 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17963 | Verified | See attached photo DSCN2174; Cold galv. Welds, 1B-FGS-HGR-0415 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17964 | Verified | See attached photo DSCN2177; Cold galv. Welds and tighten nut, 1B-FGS-HGR-0064 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17965 | Verified | See attached photo DSCN2177; Cold galv. Welds and tighten nut, 1B-FGS-HGR-0065 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI17966 | Verified | See attached photo DSCN2182; hanger not centered on support, 1B-FGS-HGR-0067 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-26 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI17967 | Verified | See attached photo DSCN2184; hanger not centered on support and shims added, 1B-FGS-HGR-0066 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-26 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI17968 | Verified | See attached photo DSCN2186; guides not installed, 1B-FGS-HGR-0511 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI17969 | Verified | See attached photo DSCN2188; Cold galv. Welds, 1B-FGS-HGR-0497 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17970 | Verified | See attached photo DSCN2190; Shoe not welded and not centered, two missing nuts on hanger, 1B-FGS-HGR-0498 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-12 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17971 | Verified | See attached photo DSCN2192; Cold galv. Welds, 1B-FGS-HGR-0501 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17972 | Verified | See attached photo DSCN2194; loose nut at base plate and gap at shoe is less and 1/2", 1B-FGS-HGR-0470 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17973 | Verified | See attached photo DSCN2197; loose nut at base plate, 1B-FGS-HGR-0461 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17974 | Verified | See attached photo DSCN2199; Cold galv. Welds, 1B-FGS-HGR-0459 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17975 | Verified | See attached photo DSCN2201; Cold galv. Welds, 1B-FGS-HGR-0466 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI17976 | Verified | See attached photo DSCN2203; V-0223C stem north as built, 1B-FGS-V-0223C | D | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
FGS-03 | FGS-03 | PI17977 | Verified | See attached photo DSCN2205; V-0224A stem east as built, 1B-FGS-V-0224A | D | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
FGS-03 | FGS-03 | PI17978 | Verified | See attached photo DSCN2207; guides not installed, 1B-FGS-HGR-0310 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-05-19 | John Watts
FGS-03 | FGS-03 | PI17979 | Verified | See attached photo DSCN2209; Cold galv. Welds, 1B-FGS-HGR-0311 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-22 | James Beech | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17980 | Verified | See attached photo DSCN2211; guides not installed and shoe not in contact with support, 1B-FGS-HGR-0312 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-05-19 | John Watts
FGS-03 | FGS-03 | PI17981 | Verified | See attached photo DSCN2213; guides not installed, 1B-FGS-HGR-0324 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-05-19 | John Watts
FGS-03 | FGS-03 | PI17982 | Verified | See attached photo DSCN2215; guides not installed and shoe not in contact with support, 1B-FGS-HGR-0326 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-05-19 | John Watts
FGS-03 | FGS-03 | PI17983 | Verified | See attached photo DSCN2217; supported welded in wrong location(too high) and guides not installed and no gap under shoe (support too high), 1B-FGs-HGR-0367 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17984 | Verified | See attached photo DSCN2219; Cold galv. Welds, 1B-FGS-HGR-0369 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17985 | Verified | See attached photo DSCN2221; guides not installed, 1B-FGS-HGR-0370 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17986 | Verified | See attached photo DSCN2223; V-0227A stem east as built, 1B-FGS-V-0227A | D | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
FGS-03 | FGS-03 | PI17987 | Verified | See attached photo DSCN2225; V-0221A stem west as built, 1B-FGS-V-0221A | D | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
FGS-03 | FGS-03 | PI17988 | Verified | See attached photo DSCN2227; Cross member added and leg removed, shim added under shoe and guides not installed, 1B-FGS-HGR-0258 | C | P | Tim Green | McD | 2020-03-17 | Tim Green | Comm | 2020-09-15 | Jason Ezell | 2021-05-27 | John Watts
FGS-03 | FGS-03 | PI17989 | Verified | See attached photo DSCN2230; guides not installed and shim added, 1B-FGS-HGR-0259 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-05-19 | John Watts
FGS-03 | FGS-03 | PI17990 | Verified | See attached photo DSCN2232; guides not visible, 1B-FGS-HGR-0268 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-05-19 | John Watts
FGS-03 | FGS-03 | PI17991 | Verified | See attached photo DSCN2234; guides not visible, 1B-FGS-HGR-0269 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-05-19 | John Watts
FGS-03 | FGS-03 | PI17992 | Verified | See attached photo DSCN2236; V-0220A stem west as built and line not insulated, 1B-FGS-P41-0220-03 | D | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
FGS-03 | FGS-03 | PI17993 | Verified | See attached photo DSCN2238; guides not visible, 1B-FGS-HGR-0278 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-05-19 | John Watts
FGS-03 | FGS-03 | PI17994 | Verified | See attached photo DSCN2240; guides not visible, 1B-FGS-HGR-0279 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-05-19 | John Watts
FGS-03 | FGS-03 | PI17995 | Verified | See attached photo DSCN2242; Extra hanger added, 1B-FGS-P41-0212-01 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17996 | Verified | See attached photo DSCN2244; cap has plumbers tape, remove, 1B-FGS-V-0210B | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-09 | James Beech | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17997 | Verified | See attached photo DSCN2246; Cold galv. Welds and both nuts on the bottom of u-bolt, 1B-FGS-HGR-0244 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-05 | James Beech | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI17998 | Verified | See attached photo DSCN2250; V-0230A stem east as built, 1B-FGS-V-0230A | D | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
FGS-03 | FGS-03 | PI17999 | Verified | See attached photo DSCN2252; Cold galv. Welds, 1B-FGS-HGR-0297 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI18000 | Verified | See attached photo DSCN2254; guides not installed, 1B-FGS-HGR-0298 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-24 | Dave Goldak
FGS-03 | FGS-03 | PI18001 | Verified | See attached photo DSCN2256; Cold galv. Welds, 1B-FGS-HGR-0133 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI18002 | Verified | See attached photo DSCN2258; both nuts on the bottom of u-bolt, 1B-FGS-HGR-0019 | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI18003 | Verified | See attached photo DSCN2261; Cold galv. Welds and plate steel support not installed, 1B-FGS-HGR-0121 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-27 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI18004 | Verified | See attached photo DSCN2263; Cold galv. Welds and pipe not ins contact with support, 1B-FGS-HGR-0122 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-07 | James Beech | 2020-06-22 | Dave Goldak
FGS-03 | FGS-03 | PI18005 | Verified | See attached photo DSCN2268; remove ziptie restraint from valve, 1B-FGS-SRV-0245 | C | P | Tim Green | McD | 2020-03-17 | Tim Green | Comm | 2020-06-30 | Dave Goldak | 2020-06-30 | Dave Goldak
FGS-03 | FGS-03 | PI18006 | Verified | See attached photo DSCN2270; Cold galv. Welds, 1B-FGS-HGR-0124 | C | X | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-04-14 | James Beech | 2020-06-22 | Dave Goldak
FPA-01 | FPA-01 | PI09376 | Verified | Tag all Janus Fire Protection panels. | C | E | Sheri Fritz | JAN | 2019-10-10 | Sheri Fritz | Const | 2020-01-09 | Sheri Fritz | 2020-01-29 | Fred Michael
FPA-01 | FPA-01 | PI12593 | Verified | Ground fire protection cabinets on Units A & B. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-21 | Shannon Scott
FPA-01 | FPA-01 | PI12819 | Verified | Plug spare knock in in control room panel LFAP-01. | C | E | Sheri Fritz | JAN | 2019-11-07 | Sheri Fritz | Const | 2020-01-09 | Sheri Fritz | 2020-01-14 | Mike Tabbert
FPA-01 | FPA-01 | PI12820 | Verified | Clean out / wipe down all panels. | B | E | Sheri Fritz | JAN | 2019-11-07 | Sheri Fritz | Const | 2019-12-23 | Michael Law | 2020-01-01 | Albert Burge
FPA-01 | FPA-01 | PI12821 | Verified | Blank the spare box in the IT Room in the control room and install busing for nipple in N1L1M70, 71. | B | E | Sheri Fritz | JAN | 2019-11-07 | Sheri Fritz | Const | 2020-01-09 | Sheri Fritz | 2020-01-14 | Mike Tabbert
FPA-01 | FPA-01 | PI12822 | Verified | Ground the conduit bushing at the unit A & B gas turbine control packages | A | E | Sheri Fritz | JAN | 2019-11-07 | Sheri Fritz | Const | 2019-11-13 | Chris Karnes | 2019-12-13 | Mike Tabbert
FPA-01 | FPA-01 | PI12823 | Verified | Missing condulet covers throughout subsystem. | B | E | Sheri Fritz | JAN | 2019-11-07 | Sheri Fritz | Const | 2019-11-13 | Chris Karnes | 2019-11-20 | Fred Michael
FPA-01 | FPA-01 | PI12824 | Verified | Install plastic end caps on unistrut at panels. | C | E | Sheri Fritz | JAN | 2019-11-07 | Sheri Fritz | Const | 2020-02-05 | Sheri Fritz | 2020-02-07 | Mike Tabbert
FPA-01 | FPA-01 | PI12825 | Verified | The cables from the cable tray to the A & B CEMs buildings need to be routed in conduit. | A | E | Sheri Fritz | JAN | 2019-11-07 | Sheri Fritz | Const | 2019-11-13 | Chris Karnes | 2019-12-13 | Mike Tabbert
FPA-01 | FPA-01 | PI12826 | Verified | Label all "non-Janus" fire detection panels (including fire pump house exterior). | C | E | Mike Tabbert | McD | 2019-11-07 | Mike Tabbert | Const | 2020-02-19 | Mike Tabbert | 2020-02-21 | Mike Tabbert
FPA-01 | FPA-01 | PI12827 | Verified | Pour seal offs at the 1A & 1B sample buildings. | A | E | Chris Colvin | JAN | 2019-11-07 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
FPA-01 | FPA-01 | PI12828 | Verified | Grout the fire panel panel at the 1B gas turbine control package. | C | C | Alan Huntsman | McD | 2019-11-07 | Alan Huntsman | Const | 2020-02-20 | Alan Huntsman | 2020-02-21 | Mike Tabbert
FPA-01 | FPA-01 | PI12829 | Verified | Cold galvanize all conduit threads. | C | E | Sheri Fritz | JAN | 2019-11-07 | Sheri Fritz | Const | 2019-11-13 | Chris Karnes | 2019-12-14 | Mike Tabbert
FPA-01 | FPA-01 | PI12830 | Verified | Ground the bushings at the southeast corner in the water treatment building. | A | E | Sheri Fritz | JAN | 2019-11-07 | Sheri Fritz | Const | 2019-11-13 | Chris Karnes | 2019-11-20 | Fred Michael
FPA-01 | FPA-01 | PI12831 | Verified | Complete the installation at the STG bearings detection. | B | E | Sheri Fritz | JAN | 2019-11-07 | Sheri Fritz | Const | 2020-02-05 | Eric Czajka | 2020-02-25 | Michael Law
FPA-01 | FPA-01 | PI12832 | Verified | Ground the seal tite at the north & south sides of the STG operating deck, at the STG mezz south stairs, and at the south side ground level. | A | E | Sheri Fritz | JAN | 2019-11-07 | Sheri Fritz | Const | 2019-11-13 | Chris Karnes | 2019-12-14 | Mike Tabbert
FPA-01 | FPA-01 | PI13854 | Verified | Smoke detector in battery room (Main PDC) is not complete & not wired. | A | E | Mike Tabbert | McD | 2019-12-02 | Mike Tabbert | Const | 2020-01-10 | Mike Tabbert | 2020-01-13 | Shannon Scott
FPA-01 | FPA-01 | PI13855 | Verified | Need additional smoke detector in main PDC, outside of battery room. | D | E | Michael Law | McD | 2019-12-02 | Michael Law | Const |  |  | 2019-12-20 | Mike Tabbert
FPA-01 | FPA-01 | PI17772 | Verified | Main PDC: Missing j-box cover and condulet cover to smoke detector system, south east corner of battery room wall in main room. | C | E | Chris Colvin | McD | 2020-03-12 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-10-06 | Dave Goldak
FPA-01 | FPA-01 | PI19258 | Verified | Fire Pump House, Tamper panels are wired incorrectly, causing ground fualts in fire alarm panel. | C | E | Scott McCall | RUH | 2020-08-20 | Scott McCall | Const | 2020-08-24 | Mike Tabbert | 2020-08-24 | Mike Tabbert
FPA-01 | FPA-01 | PI19259 | Verified | Replace Printed Circuit Board in unit A, is causing alarms in CO2 system - requires outage | C | E | James Seany | JAN | 2020-08-20 | James Seany | Const | 2021-04-21 | Eric Policarpio | 2021-04-21 | John Watts
FPA-01 | FPA-01 | PI19260 | Verified | Make wiring change in Diesel Fire Pump Controler, getting wrong signal in fire alarm panel. | C | E | James Seany | JAN | 2020-08-20 | James Seany | Const | 2021-04-21 | Eric Policarpio | 2021-04-21 | John Watts
FPA-01 | FPA-01 | PI19261 | Verified | Confirm Correct signal from Tamper Panels after wiring correction. | C | E | James Seany | JAN | 2020-08-20 | James Seany | Const | 2021-04-21 | Eric Policarpio | 2021-04-21 | John Watts
FPS-01 | FPS-01 | PI00873 | Verified | Tag valves 10-FPS-V-0105, 0106 & 0107 | C | P | Kelvin Cook | McD | 2019-05-01 | Kelvin Cook | Const | 2020-02-10 | Kelvin Cook | 2020-07-28 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00874 | Verified | Grout all supports. | C | C | Johnny Campbell | McD | 2019-05-01 | Johnny Campbell | Const | 2019-08-19 | Jack Fields | 2019-08-29 | Shannon Scott
FPS-01 | FPS-01 | PI00875 | Verified | Fire Dept. Connection needs tag, 10-FPS-FDC-1000. | C | P | Justin Houdeshell | McD | 2019-05-01 | Justin Houdeshell | Const | 2019-06-21 | Justin Houdeshell | 2019-07-02 | Dave Goldak
FPS-01 | FPS-01 | PI00876 | Verified | Complete restoration of pipe for yard loop. | A | P | Terry Deaton | McD | 2019-05-01 | Terry Deaton | Const | 2019-05-02 | Justin Houdeshell | 2019-05-02 | Justin Houdeshell
FPS-01 | FPS-01 | PI00877 | Verified | Install diesel fire pump drains. | B | P | Terry Deaton | McD | 2019-05-01 | Terry Deaton | Const | 2019-06-07 | Terry Deaton | 2019-06-11 | Shannon Scott
FPS-01 | FPS-01 | PI00878 | Verified | Install diesel fuel fill piping. | A | P | Shane Crowe | McD | 2019-05-01 | Shane Crowe | Const | 2019-05-02 | Joshua Sturgeon | 2019-05-14 | Dave Goldak
FPS-01 | FPS-01 | PI00879 | Verified | Install flame arrestors at the diesel fuel tank. | A | M | Shane Crowe | McD | 2019-05-01 | Shane Crowe | Const | 2019-05-02 | Joshua Sturgeon | 2019-05-08 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00880 | Verified | Install fuel fill platform | C | C | Tim Gallegos | McD | 2019-05-01 | Tim Gallegos | Const | 2020-08-06 | Tim Gallegos | 2021-01-05 | Keith Pollock
FPS-01 | FPS-01 | PI00881 | Verified | Exhaust fan needs manual switch. | D | P | Charles Worthington | McD | 2019-05-01 | Charles Worthington | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
FPS-01 | FPS-01 | PI00882 | Verified | Provide secondary containment for the diesel fuel tank. | D | P | Charles Worthington | McD | 2019-05-01 | Charles Worthington | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
FPS-01 | FPS-01 | PI00883 | Verified | Diesel exhaust needs weep hole. Spec 5.3.4.4.3. | A | M | Shane Crowe | McD | 2019-05-01 | Shane Crowe | Const | 2019-05-02 | Joshua Sturgeon | 2019-05-08 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00884 | Verified | Insulate the diesel exhaust | C | Q | Richard McSpadden | PCI | 2019-05-01 | Richard McSpadden | Const | 2021-02-22 | Eric Policarpio | 2021-02-22 | Dave Goldak
FPS-01 | FPS-01 | PI00885 | Verified | Replace fire extinguisher in the diesel fire pump room (discharged). | A | M | Shane Crowe | McD | 2019-05-01 | Shane Crowe | Const | 2019-05-07 | Joshua Sturgeon | 2019-05-14 | Dave Goldak
FPS-01 | FPS-01 | PI00886 | Verified | Tag V-1010 on fire pump skid | C | P | Kelvin Cook | McD | 2019-05-01 | Kelvin Cook | Const | 2020-02-10 | Kelvin Cook | 2020-07-28 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00887 | Verified | Seal the fire proofing in the diesel compartment. | C | M | Shane Crowe | McD | 2019-05-01 | Shane Crowe | Const | 2020-01-24 | Shane Crowe | 2020-07-28 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00888 | Verified | Receptacles in the diesel compartment should have weather proof covers. | C | E | Shannon Savoy | McD | 2019-05-01 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-06-06 | Shannon Scott
FPS-01 | FPS-01 | PI00889 | Verified | Complete grounding the the diesel compartment. | A | E | Shannon Savoy | McD | 2019-05-01 | Shannon Savoy | Const | 2019-05-15 | Shannon Savoy | 2019-05-20 | Shannon Scott
FPS-01 | FPS-01 | PI00890 | Verified | Vent fan should be belt driven (per spec) | D | M | Michael Law | McD | 2019-05-01 | Michael Law | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
FPS-01 | FPS-01 | PI00891 | Verified | Complete hydro & restoration of the supply & return piping. | A | P | Terry Deaton | McD | 2019-05-01 | Terry Deaton | Const | 2019-06-07 | Terry Deaton | 2019-06-10 | Justin Houdeshell
FPS-01 | FPS-01 | PI00893 | Verified | Assign equipment ID # and tag to the exhaust fan. | C | P | Tim Green | RUH | 2019-05-02 | Tim Green | Const | 2021-02-24 | Eric Policarpio | 2021-02-24 | John Watts
FPS-01 | FPS-01 | PI00894 | Verified | Install sprinkler heads. | B | P | Shane Crowe | McD | 2019-05-02 | Shane Crowe | Const | 2019-05-07 | Joshua Sturgeon | 2019-05-14 | Dave Goldak
FPS-01 | FPS-01 | PI00895 | Verified | Assign equipment ID # and tag to the diesel fuel tank. | C | P | Tim Green | RUH | 2019-05-02 | Tim Green | Const | 2021-02-24 | Eric Policarpio | 2021-02-24 | John Watts
FPS-01 | FPS-01 | PI00896 | Verified | Connect batteries. | B | M | Danny Pase | McD | 2019-05-02 | Danny Pase | Const | 2019-07-17 | Michael Law | 2019-07-22 | Dave Goldak
FPS-01 | FPS-01 | PI00897 | Verified | Install exhaust rain cap. | B | M | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-08-16 | Joshua Sturgeon | 2019-08-29 | Shannon Scott
FPS-01 | FPS-01 | PI00898 | Verified | Reinstall weather stripping on the south doors of the enclosure. | C | M | Shane Crowe | McD | 2019-05-02 | Shane Crowe | Const | 2020-01-15 | Shane Crowe | 2020-07-28 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00899 | Verified | Drain line downstream from SV-101 in incomplete. | B | P | James Beech | RUH | 2019-05-02 | James Beech | Const | 2020-03-05 | Tim Green | 2020-03-09 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00900 | Verified | Check valve installed upstream from SV-101 instead of indicated PT. | C | P | Charles Worthington | McD | 2019-05-02 | Charles Worthington | Const | 2020-06-10 | Charles Worthington | 2020-07-24 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00901 | Verified | Install tag V-1029. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00902 | Verified | Install tag on V-1028. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00903 | Verified | CHK-1005 installed in incorrect location (after tee). | B | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-08-16 | Joshua Sturgeon | 2019-09-11 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00904 | Verified | Install tag on CHK-1004. | C | P | Kelvin Cook | RUH | 2019-05-02 | Kelvin Cook | Const | 2019-12-17 | Joshua Sturgeon | 2020-01-15 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00905 | Verified | Install tag on CHK-1005. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00906 | Verified | Install tag on V-1031.. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00907 | Verified | Install tag on V-1030. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00908 | Verified | Air cooler drain missing sight glass indicated on PID. | C | P | Charles Worthington | RUH | 2019-05-02 | Charles Worthington | Const | 2020-06-19 | Charles Worthington | 2020-07-24 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00909 | Verified | Install tag on V-1012. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00910 | Verified | Install tag on PI-0006. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00911 | Verified | Install tag on V-1010 (air release). | C | P | James Beech | RUH | 2019-05-02 | James Beech | Const | 2020-05-26 | James Beech | 2020-07-28 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00912 | Verified | Install tag on CHV-1000. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00913 | Verified | Install tag on PI-0005. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00914 | Verified | Install tag on V-1011. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00915 | Verified | Verify orientation of check valve CHV-1003 (installed backwards?). | B | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-08-16 | Joshua Sturgeon | 2019-09-11 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00916 | Verified | Install tag on CHV-1003. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00917 | Verified | Piping from FDC to supply pipe not installed according to PID. | C | P | Mike Tabbert | RUH | 2019-05-02 | Mike Tabbert | Const | 2020-06-23 | Mike Tabbert | 2020-07-30 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00918 | Verified | Temp. sensor and temp. sensor installed (not shown of PID). Assing tag #s and update PID. | C | P | Tim Green | RUH | 2019-05-02 | Tim Green | Const | 2021-02-24 | Eric Policarpio | 2021-02-24 | John Watts
FPS-01 | FPS-01 | PI00919 | Verified | Install tag on V-1022. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00920 | Verified | Install tag on SV-1050. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00921 | Verified | Install tag on V-1027. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00922 | Verified | Install tag on V-1025. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Johnny Campbell | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00923 | Verified | Install tag on STN-001 filter. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00924 | Verified | Install tag on STN-1000 filter. | C | P | Joshua Sturgeon | RUH | 2019-05-02 | Joshua Sturgeon | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-21 | Shannon Scott
FPS-01 | FPS-01 | PI00925 | Verified | Assign tag # and install tag (none indicated on PID) to ball valve upstream from LS-0001. | C | P | Tim Green | RUH | 2019-05-02 | Tim Green | Const | 2021-02-24 | Eric Policarpio | 2021-02-24 | John Watts
FPS-01 | FPS-01 | PI00926 | Verified | Assign Tag # and install tag (none indicated on PID) to ball valve - inner wall drain. | C | P | Tim Green | RUH | 2019-05-02 | Tim Green | Const | 2021-04-21 | Eric Policarpio | 2021-04-21 | John Watts
FPS-01 | FPS-01 | PI00927 | Verified | Assign Tag # and install tag (none indicated on PID) to ball valve - outer wall drain. | C | P | Tim Green | RUH | 2019-05-02 | Tim Green | Const | 2021-02-24 | Eric Policarpio | 2021-02-24 | John Watts
FPS-01 | FPS-01 | PI00928 | Verified | Plug drain - ball valve - inner wall drain. | C | P | James Beech | McD | 2019-05-02 | James Beech | Const | 2020-05-26 | James Beech | 2020-07-28 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00929 | Verified | Plug drain - ball valve - outer wall drain. | C | P | James Beech | McD | 2019-05-02 | James Beech | Const | 2020-05-27 | James Beech | 2020-07-28 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00930 | Verified | Install tag on CHK-1010. | C | P | Kelvin Cook | RUH | 2019-05-02 | Kelvin Cook | Const | 2020-02-10 | Kelvin Cook | 2020-07-28 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00931 | Verified | Install tag on SV-1051. | C | P | Kelvin Cook | RUH | 2019-05-02 | Kelvin Cook | Const | 2020-02-10 | Kelvin Cook | 2020-07-28 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00932 | Verified | Pipe connection from Engine instument panel to fuel tank vent line installed (not indicated on PID). | C | P | Charles Worthington | RUH | 2019-05-02 | Charles Worthington | Const | 2020-06-19 | Charles Worthington | 2020-07-24 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00933 | Verified | Install tag on CHK-1010 | C | P | Kelvin Cook | RUH | 2019-05-02 | Kelvin Cook | Const | 2020-02-10 | Kelvin Cook | 2020-07-28 | Nelson Eichelberger
FPS-01 | FPS-01 | PI00934 | Verified | Ball valve installed at fuel fill. Not indicated on PID. Assign Tag # and add to PID. | C | P | Tim Green | RUH | 2019-05-02 | Tim Green | Const | 2021-02-24 | Eric Policarpio | 2021-02-24 | John Watts
FPS-01 | FPS-01 | PI00935 | Verified | Pipe between V-1025 and V-1027 used as a step and bent. Repair as necessary. | A | P | Shane Crowe | McD | 2019-05-02 | Shane Crowe | Const | 2019-05-06 | Joshua Sturgeon | 2019-05-14 | Dave Goldak
FPS-01 | FPS-01 | PI01178 | Verified | 10FPSC0001, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01179 | Verified | 10FPSC0002, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-06-07 | Mike Tabbert
FPS-01 | FPS-01 | PI01180 | Verified | 10FPSC0003, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-06-07 | Mike Tabbert
FPS-01 | FPS-01 | PI01181 | Verified | 10FPSC0004, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-30 | Shannon Savoy | 2019-06-07 | Mike Tabbert
FPS-01 | FPS-01 | PI01182 | Verified | 10FPSC0006, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01183 | Verified | 10FPSH0001A, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01184 | Verified | 10FPSH0001B, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01185 | Verified | 10FPSH0001C, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01186 | Verified | 10FPSH0001G, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01187 | Verified | 10FPSK0001, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01188 | Verified | 10FPSK0002, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01189 | Verified | 10FPSK0004, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01190 | Verified | 10FPSK0005, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01191 | Verified | 10FPSL0001A1, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01192 | Verified | 10FPSL0001B1, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01193 | Verified | 10FPSL0001C1, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01194 | Verified | 10FPSL0001G1, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01195 | Verified | 10FPSX0001, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-06-07 | Mike Tabbert
FPS-01 | FPS-01 | PI01196 | Verified | two valves share same tag number V-1041 | C | P | Kelvin Cook | RUH | 2019-05-28 | Kelvin Cook | Const |  |  | 2020-02-06 | Kelvin Cook
FPS-01 | FPS-01 | PI01197 | Verified | Valve V-1041 Missing Tag (duplicate on P&ID, need correct #) | C | P | Kelvin Cook | RUH | 2019-05-28 | Kelvin Cook | Const |  |  | 2020-02-06 | Kelvin Cook
FPS-01 | FPS-01 | PI01198 | Verified | Valve CHK-1008 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01199 | Verified | Valve V-1043 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01200 | Verified | Valve V-1044 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01201 | Verified | Valve CHK-1009 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01202 | Verified | Valve V-1036 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01203 | Verified | Valve V-1035 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01204 | Verified | Valve CHK-1006 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01205 | Verified | Valve V-1038 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01206 | Verified | Valve V-1037 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01207 | Verified | Valve CHK1007 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01208 | Verified | Valve V-1002 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01209 | Verified | Valve V-1013 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01210 | Verified | Valve V-1014 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01211 | Verified | Valve CHK-1002 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01212 | Verified | Valve V-1003 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01213 | Verified | Valve installed between V-1040 and PI-0016 not on P&ID | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01214 | Verified | Valve installed between V-1040 and PI-0016 not on P&ID missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01215 | Verified | Valve CHK-1003 Missing Tag | C | P | Kelvin Cook | RUH | 2019-05-28 | Kelvin Cook | Const |  |  | 2020-02-06 | Kelvin Cook
FPS-01 | FPS-01 | PI01216 | Verified | Valve V-1040 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01217 | Verified | FE-0018 Missing Tag | C | P | Kelvin Cook | RUH | 2019-05-28 | Kelvin Cook | Const |  |  | 2020-02-06 | Kelvin Cook
FPS-01 | FPS-01 | PI01218 | Verified | FT-0018 Missing Tag | C | P | Kelvin Cook | RUH | 2019-05-28 | Kelvin Cook | Const |  |  | 2020-02-06 | Kelvin Cook
FPS-01 | FPS-01 | PI01219 | Verified | Valve V-1039 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01220 | Verified | Valve V-1046 Missing Tag | C | P | Kelvin Cook | RUH | 2019-05-28 | Kelvin Cook | Const |  |  | 2020-02-06 | Kelvin Cook
FPS-01 | FPS-01 | PI01221 | Verified | Valve V-1017 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01222 | Verified | PI-0008 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01223 | Verified | Valve V-1018 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01224 | Verified | PI-0007 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01225 | Verified | Valve V-1016 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01226 | Verified | Valve CHK-1001 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01227 | Verified | Valve V-1046 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01228 | Verified | Valve V-1006 is not in system | C | P | Kelvin Cook | RUH | 2019-05-28 | Kelvin Cook | Const |  |  | 2020-02-06 | Kelvin Cook
FPS-01 | FPS-01 | PI01229 | Verified | FE-0014 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01230 | Verified | FI-0014 Missing Tag | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-18 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01231 | Verified | Jockey Pump suction line is tied in before V-1001 not after as the P&ID shows | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-07 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01232 | Verified | Jockey Pump Discharge line is tied in before reducer not after as the P&ID shows | C | P | Joshua Sturgeon | RUH | 2019-05-28 | Joshua Sturgeon | Const |  |  | 2019-12-07 | Joshua Sturgeon
FPS-01 | FPS-01 | PI01233 | Verified | 10-TD-P42-0125-01 - install 4" drain (external) | B | P | Terry Deaton | McD | 2019-05-28 | Terry Deaton | Const | 2019-06-07 | Terry Deaton | 2019-06-10 | Justin Houdeshell
FPS-01 | FPS-01 | PI01234 | Verified | 10-TD-P42-0126-01 - install 4" drain (external) | B | P | Terry Deaton | McD | 2019-05-28 | Terry Deaton | Const | 2019-06-07 | Terry Deaton | 2019-06-10 | Justin Houdeshell
FPS-01 | FPS-01 | PI01235 | Verified | Firestop all penetrations in the fire pump house. | A | E | Luis Cantu | McD | 2019-05-28 | Luis Cantu | Const | 2019-06-10 | Luis Cantu | 2019-06-12 | Mike Tabbert
FPS-01 | FPS-01 | PI01236 | Verified | Tighten flex at service transformer in the fire pump house. | B | E | Luis Cantu | McD | 2019-05-28 | Luis Cantu | Const | 2019-05-28 | Shannon Savoy | 2019-06-26 | Logan Holland
FPS-01 | FPS-01 | PI01237 | Verified | Caulk expansion joint between fire pump building and pipe support on southeast side. | C | C | Johnny Campbell | McD | 2019-05-28 | Johnny Campbell | Const | 2019-09-12 | Jack Fields | 2019-12-12 | Michael Law
FPS-01 | FPS-01 | PI01238 | Verified | Clean burn mark on west wall in the fire pump house. | C | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-31 | Shannon Savoy | 2019-06-06 | Shannon Scott
FPS-01 | FPS-01 | PI01239 | Verified | Confirm On/Off switch for louver in the fire pump house. | C | E | Mike Tabbert | RUH | 2019-05-28 | Mike Tabbert | Const | 2020-04-06 | Michael Law | 2020-04-06 | Michael Law
FPS-01 | FPS-01 | PI01240 | Verified | Rub down exterior wall of the fire pump house. | C | C | Johnny Campbell | McD | 2019-05-28 | Johnny Campbell | Const | 2019-09-06 | Johnny Campbell | 2019-12-12 | Michael Law
FPS-01 | FPS-01 | PI01241 | Verified | Torque secondary feeder cables. | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-06-03 | Mike Tabbert
FPS-01 | FPS-01 | PI01242 | Verified | Bond grounding for duct bank. | B | E | Luis Cantu | McD | 2019-05-28 | Luis Cantu | Const | 2019-05-31 | Shannon Savoy | 2019-06-26 | Logan Holland
FPS-01 | FPS-01 | PI01243 | Verified | Tighten conduit for window louver. | B | E | Luis Cantu | McD | 2019-05-28 | Luis Cantu | Const | 2019-05-28 | Shannon Savoy | 2019-06-26 | Logan Holland
FPS-01 | FPS-01 | PI01244 | Verified | Service transformer needs a secondary ground. | A | E | Luis Cantu | McD | 2019-05-28 | Luis Cantu | Const | 2019-05-29 | Shannon Savoy | 2019-06-21 | Logan Holland
FPS-01 | FPS-01 | PI01245 | Verified | Seal conduits in 10-FPS-XFM-0001. | B | E | Luis Cantu | McD | 2019-05-28 | Luis Cantu | Const | 2019-07-18 | Ken Mundy | 2019-07-24 | Mike Tabbert
FPS-01 | FPS-01 | PI01246 | Verified | Missing lid bolts on 10-FPS-XFM-0001. | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-29 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01247 | Verified | Terminate permanent heat cables in 10-FPS-XFM-0001. | B | E | Luis Cantu | McD | 2019-05-28 | Luis Cantu | Const | 2019-06-19 | Luis Cantu | 2019-07-15 | Fred Michael
FPS-01 | FPS-01 | PI01248 | Verified | Ground braids for stress cones in 10-FPS-XFM-0001. | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-29 | Shannon Savoy | 2019-06-03 | Mike Tabbert
FPS-01 | FPS-01 | PI01249 | Verified | Tie permanent ground to transformer frame & the HRD. | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-29 | Shannon Savoy | 2019-06-03 | Mike Tabbert
FPS-01 | FPS-01 | PI01250 | Verified | Complete ground at manhole at transformer. | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01251 | Verified | Clean out manhole at transformer. | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-31 | Shannon Savoy | 2019-06-03 | Mike Tabbert
FPS-01 | FPS-01 | PI01252 | Verified | Form up cables in manhole at transformer. | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-29 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01253 | Verified | Tighten flex in transformer control panel. | B | E | Luis Cantu | McD | 2019-05-28 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-06-17 | Shannon Scott
FPS-01 | FPS-01 | PI01254 | Verified | Anchor transformer 10-FPS-XFM-0001. | A | E | Luis Cantu | McD | 2019-05-28 | Luis Cantu | Const | 2019-05-29 | Shannon Savoy | 2019-06-11 | Shannon Scott
FPS-01 | FPS-01 | PI01255 | Verified | Add two anchors to HRD at transformer 10-FPS-XFM-0001. | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-29 | Shannon Savoy | 2019-05-30 | Mike Tabbert
FPS-01 | FPS-01 | PI01256 | Verified | Complete wiring to 10-FPS-AOV-0100 at tank. | A | E | Shannon Savoy | McD | 2019-05-28 | Shannon Savoy | Const | 2019-05-31 | Shannon Savoy | 2019-06-07 | Mike Tabbert
FPS-01 | FPS-01 | PI01425 | Verified | Change out bolts on flanges at the fire pump house to B7 studs. | A | P | Terry Deaton | McD | 2019-06-07 | Terry Deaton | Const | 2019-06-10 | Terry Deaton | 2019-06-10 | Kelvin Cook
FPS-01 | FPS-01 | PI01426 | Verified | Complete weld on pedestal support - between tank and pump house. | B | P | Terry Deaton | McD | 2019-06-07 | Terry Deaton | Const | 2019-06-14 | Terry Deaton | 2019-06-17 | Shannon Scott
FPS-01 | FPS-01 | PI01439 | Verified | Dog ears missing bolts at the fire pump house. | A | P | Terry Deaton | McD | 2019-06-07 | Terry Deaton | Const | 2019-06-10 | Terry Deaton | 2019-06-12 | Danny Pase
FPS-01 | FPS-01 | PI01473 | Verified | Complete Concrete for duct bank stub-ups at south side of fire water storage tank and northeast corner of fire pump house. | B | C | Johnny Campbell | McD | 2019-06-19 | Johnny Campbell | Const | 2019-07-31 | Johnny Campbell | 2019-08-21 | Fred Michael
FPS-01 | FPS-01 | PI01474 | Verified | Complete grounding of conduit stub-ups for duct bank at south side of fire water storage tank and northeast corner of fire pump house. | B | E | Dustin Futrell | McD | 2019-06-19 | Dustin Futrell | Const | 2019-07-09 | Luis Cantu | 2019-08-07 | Mike Tabbert
FPS-01 | FPS-01 | PI01475 | Verified | Clean threads and apply contact paste, plug conduits at south side of fire water storage tank and northeast corner of fire pump house. | B | E | Dustin Futrell | McD | 2019-06-19 | Dustin Futrell | Const | 2019-07-09 | Luis Cantu | 2019-08-07 | Mike Tabbert
FPS-01 | FPS-01 | PI01536 | Verified | The diesel fuel fill connection for the diesel fire pump tank is in a shared cabinet with a 120VAC alarm panel with exposed terminal strip and relay cluster. The only barrier is a piece of sheet metal, that is not sealed, between the fuel inlet and the alarm panel. If the cabinet were to fill with diesel fuel vapors, it could potentially cause a fire. | C | E | Joshua Sturgeon | RUH | 2019-06-21 | Joshua Sturgeon | Comm | 2019-07-22 | Joshua Sturgeon | 2019-07-23 | Shannon Scott
FPS-01 | FPS-01 | PI04722 | Verified | 10-FPS-AOV-0100 - air leaking from Fire Protection Service Water Tank Inlet flow control valve. Air leaking from the mechanism sending air to the valve. | B | P | William Mitchell | McD | 2019-09-03 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-04-06 | Bernard Stasse
FPS-01 | FPS-01 | PI09375 | Verified | 10-FPS-AOV-0100 on the filtered water clearwell to FPS/SWS tank T-100 needs a bypass in case it fails closed & cannot be reopened. Add bypass to FW/SW tank inlet valve FC-100. | D | P | Kevin Leppert | McD | 2019-10-10 | Kevin Leppert | Const | 2020-02-07 | Michael Law | 2020-03-04 | Dave Goldak
FPS-01 | FPS-01 | PI12702 | Verified | 10-FPS-P-0002 Discharge valve for the jockey fire pump has a packing leak. | C | M | William Mitchell | McD | 2019-11-01 | William Mitchell | Comm |  |  | 2020-01-23 | Shannon Scott
FPS-01 | FPS-01 | PI14859 | Verified | Check valve CHK-1009 installed in reverse direction. Reinstall. (Correct direction per P&ID is flow AWAY from Controller | A | P | Kelvin Cook | McD | 2019-12-20 | Kelvin Cook | Comm | 2019-12-23 | Kelvin Cook | 2019-12-24 | Shannon Scott
FPS-01 | FPS-01 | PI14860 | Verified | Check valve CHK-1006 installed in reverse direction. Reinstall. (Correct direction per P&ID is flow AWAY from Controller | A | P | Kelvin Cook | McD | 2019-12-20 | Kelvin Cook | Comm | 2019-12-23 | Kelvin Cook | 2019-12-24 | Shannon Scott
FPS-01 | FPS-01 | PI14861 | Verified | Check valve CHK-1007 installed in reverse direction. Reinstall. (Correct direction per P&ID is flow AWAY from Controller | A | P | Kelvin Cook | McD | 2019-12-20 | Kelvin Cook | Comm | 2019-12-23 | Kelvin Cook | 2019-12-24 | Shannon Scott
FPS-01 | FPS-01 | PI14862 | Verified | PI-0016 (Fire Pump House Electric Motor Pump area Sprinkler System) pressure gauge does not register pressure change when Jockey Pump cycles. Verify PI is working and operating correctly. | A | P | William Mitchell | McD | 2019-12-20 | William Mitchell | Comm | 2020-03-17 | William Mitchell | 2020-07-30 | Nelson Eichelberger
FPS-01 | FPS-01 | PI15899 | Verified | 10-FPS-P-0001B (Diesel Fire Pump) & 10-FPS-0001A (Electrica Fire Pump) - Packing glands are not guarded for rotating equipment | C | M | Shane Crowe | McD | 2020-01-13 | Shane Crowe | Comm | 2020-02-06 | Shane Crowe | 2020-02-10 | Shannon Scott
FPS-01 | FPS-01 | PI15900 | Verified | 10-FPS-V-1003 - Packing leak is slow while pump is off. While pump is on, it has a steady stream of water coming from top of packing nut. | C | M | Shane Crowe | McD | 2020-01-13 | Shane Crowe | Comm | 2020-03-19 | Shane Crowe | 2020-04-06 | Bernard Stasse
FPS-01 | FPS-01 | PI15901 | Verified | 10-FPS-XFM-0001 - The grounding wire is not mounted on the flex conduit going to 10-FPS-XFM-0001 temperature display monitor | D | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Comm | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
FPS-01 | FPS-01 | PI15902 | Verified | 10-FPS-SRV-1001 - The safety valve, 10-FPS-SRV-1001, is lifting in the field. According to the sticker on the safety valve, it is set to 60 PSI; however, the documentation from the OEM states it should be 135 PSI. | C | P | William Mitchell | McD | 2020-01-13 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2021-04-21 | John Watts
FPS-01 | FPS-01 | PI16200 | Verified | 10-FPS-CAB-0003 - There is a steady leak from the piping to the left side of the diesel fire pump | B | P | William Mitchell | McD | 2020-01-20 | William Mitchell | Comm | 2020-03-17 | William Mitchell | 2020-04-06 | Bernard Stasse
FPS-01 | FPS-01 | PI16731 | Verified | Fire department connection leaking - west side of fire pump house. | C | M | William Mitchell | McD | 2020-02-13 | William Mitchell | Comm | 2020-04-14 | William Mitchell | 2020-06-18 | Dave Goldak
FPS-01 | FPS-01 | PI17156 | Verified | Clean up inside Diesel Pump enclosure | C | C | Johnny Campbell | McD | 2020-02-22 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-07-28 | Keith Pollock
FPS-01 | FPS-01 | PI17157 | Verified | Clean up inside Electric Pump enclosure | C | C | Johnny Campbell | McD | 2020-02-22 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-07-28 | Keith Pollock
FPS-01 | FPS-01 | PI17656 | Verified | The diesel fire pump 1/2 inch sensing line has a leak on the tee and the union. | C | P | Tim Green | McD | 2020-03-04 | Tim Green | Comm | 2020-05-29 | James Beech | 2021-02-01 | Dave Goldak
FPS-01 | FPS-01 | PI17660 | Verified | 10-FPS-T-0001 - Diesel is on the outside of the plug on the valve at the bottom of the diesel tank (the Plant North valve). Check for diesel leak. | C | M | William Mitchell | McD | 2020-03-04 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2020-05-06 | John Watts
FPS-01 | FPS-01 | PI18028 | Verified | 10-FPS-CHK-1004, 10-FPS-CHK-1005, and 10-FPS-CHK-1008 - The check valves are installed correctly, but the valve body has been installed incorrectly. | C | P | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-21 | James Beech | 2021-07-08 | John Watts
FPS-02 | FPS-02 | PI00602 | Verified | Repair Hydrant SE of STG. | A | P | Terry Deaton | McD | 2019-04-15 | Terry Deaton | Const | 2019-04-23 | Terry Deaton | 2019-04-23 | Justin Houdeshell
FPS-02 | FPS-02 | PI00638 | Verified | Install all bollards. | B | C | Johnny Campbell | McD | 2019-04-22 | Johnny Campbell | Const | 2019-06-14 | Justin Houdeshell | 2019-06-14 | Justin Houdeshell
FPS-02 | FPS-02 | PI00639 | Verified | Hydrotest entire system and restore. | A | P | Terry Deaton | McD | 2019-04-22 | Terry Deaton | Const | 2019-04-23 | Terry Deaton | 2019-04-23 | Justin Houdeshell
FPS-02 | FPS-02 | PI00640 | Verified | Backfill around all hydrants/roadway boxes/post indicators. | B | P | Terry Deaton | McD | 2019-04-22 | Terry Deaton | Const | 2019-05-16 | Terry Deaton | 2019-05-20 | Justin Houdeshell
FPS-02 | FPS-02 | PI00641 | Verified | Tag all Hydrants / Valves / PIVs. | B | P | Justin Houdeshell | McD | 2019-04-22 | Justin Houdeshell | Const | 2019-05-20 | Terry Deaton | 2019-05-20 | Justin Houdeshell
FPS-02 | FPS-02 | PI00642 | Verified | Install concrete roadway valve boxes. | C | C | Johnny Campbell | McD | 2019-04-22 | Johnny Campbell | Const | 2019-05-20 | Terry Deaton | 2019-05-20 | Justin Houdeshell
FPS-02 | FPS-02 | PI00643 | Verified | Replace roadway valve lids with the word "Fire" instead of "Water". | C | P | Justin Houdeshell | McD | 2019-04-22 | Justin Houdeshell | Const | 2019-06-21 | Justin Houdeshell | 2019-08-29 | Nelson Eichelberger
FPS-02 | FPS-02 | PI00644 | Verified | Turn over hydrant handles and a valve "T" handle to commissioning at time of turnover. | B | P | Justin Houdeshell | McD | 2019-04-22 | Justin Houdeshell | Const | 2019-04-30 | Justin Houdeshell | 2019-05-20 | Danny Pase
FPS-02 | FPS-02 | PI00645 | Verified | Touch up paint required on all hydrants & PIVs and the flange southeast of STG. | C | X | Jerry Smith | McD | 2019-04-22 | Jerry Smith | Const | 2020-02-20 | Alan Huntsman | 2020-04-06 | Bernard Stasse
FPS-02 | FPS-02 | PI00646 | Verified | Rotate 10-FPS-HYD-0262 180 deg. to face road - south of admin. bldg. | A | P | Terry Deaton | McD | 2019-04-22 | Terry Deaton | Const | 2019-04-23 | Terry Deaton | 2019-04-23 | Justin Houdeshell
FPS-02 | FPS-02 | PI00647 | Verified | Rusted chain for cap on 10-FPS-HYD-0242 - at demin. tank. (replace) | C | P | Terry Deaton | McD | 2019-04-22 | Terry Deaton | Const | 2019-04-23 | Terry Deaton | 2019-04-23 | Justin Houdeshell
FPS-02 | FPS-02 | PI00648 | Verified | Rusted chain for cap on 10-FPS-HYD-0246 - at west of demin. bldg. (replace) | C | P | Terry Deaton | McD | 2019-04-22 | Terry Deaton | Const | 2019-04-23 | Terry Deaton | 2019-04-23 | Justin Houdeshell
FPS-02 | FPS-02 | PI00649 | Verified | Add rocks & roadway box at 10-FPS-HYD-0246 - west of demin. bldg. | B | P | Terry Deaton | McD | 2019-04-22 | Terry Deaton | Const | 2019-05-16 | Terry Deaton | 2019-05-20 | Shannon Scott
FPS-02 | FPS-02 | PI00650 | Verified | Rusted chain for cap on 10-FPS-HYD-0218 - south of STG switchyard. (replace) | C | P | Terry Deaton | McD | 2019-04-22 | Terry Deaton | Const | 2019-04-23 | Terry Deaton | 2019-04-23 | Justin Houdeshell
FPS-02 | FPS-02 | PI00651 | Verified | Install valve 10-FPS-V-0300 - southwest STG area. | B | P | Sheri Fritz | JAN | 2019-04-22 | Sheri Fritz | Const | 2019-06-14 | Michael Law | 2020-01-01 | Lonnie Peters
FPS-02 | FPS-02 | PI00652 | Verified | Clean all hydrants (dirt & rocks) | C | P | Terry Deaton | McD | 2019-04-22 | Terry Deaton | Const | 2019-04-23 | Terry Deaton | 2019-04-23 | Justin Houdeshell
FPS-02 | FPS-02 | PI09720 | Verified | Remove concrete splatter and dirt, paint all Fire Hydrants and PIVs | C | X | Jerry Smith | McD | 2019-10-18 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-04-08 | Bernard Stasse
FPS-02 | FPS-02 | PI09721 | Verified | Commissioning to turnover Fire Hydrant Valve wrenches Fire Hydrant Isolation Valve T-Handles to Entergy Operations | C | M | William Mitchell | McD | 2019-10-18 | William Mitchell | Comm | 2020-04-14 | William Mitchell | 2021-05-07 | John Watts
FPS-02 | FPS-02 | PI09722 | Verified | 10-FPS-V-0222; is buried, no concrete pad visible | C | C | Johnny Campbell | McD | 2019-10-18 | Johnny Campbell | Comm | 2019-11-21 | Jerry Smith | 2019-12-13 | Blake Boudreaux
FPS-02 | FPS-02 | PI09723 | Verified | Establish correct grade around all Hydrants, Isolation Valves, and PIVs system wide | C | C | Brooks Baker | McD | 2019-10-18 | Brooks Baker | Comm | 2020-04-09 | Michael Law | 2020-04-09 | Michael Law
FPS-02 | FPS-02 | PI09724 | Verified | 10-FPS-PIV-0225 tag number is incorrect | C | P | James Beech | McD | 2019-10-18 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-31 | Blake Boudreaux
FPS-02 | FPS-02 | PI09725 | Verified | 10-FPS-HYD-0216 is out of plumb needs to be squared up | C | P | James Beech | McD | 2019-10-18 | James Beech | Comm | 2020-02-02 | James Beech | 2020-02-05 | Blake Boudreaux
FPS-02 | FPS-02 | PI09726 | Verified | 10-FPS-PIV-0230; needs tag | C | P | James Beech | McD | 2019-10-18 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-31 | Blake Boudreaux
FPS-02 | FPS-02 | PI09727 | Verified | Install bollards at 10-FPS-HYD-0226, 10-FPS-HYD-0212, 10-FPS-HYD-0242, 10-FPS-HYD-0240,10-FPS-HYD-0256, 10-FPS-HYD-0236, 10-FPS-HYD-0254, 10-FPS-HYD-0252, 10-FPS-HYD-0234 | C | C | Johnny Campbell | McD | 2019-10-18 | Johnny Campbell | Comm | 2019-11-21 | Jerry Smith | 2019-12-13 | Blake Boudreaux
FPS-02 | FPS-02 | PI09728 | Verified | Pour concrete pads around Hydrant Isolation Valve manway at 10-FPS-V-0222, 10-FPS-V-0218, 10-FPS-V-0212, 10-FPS-V-0216, 10-FPS-V-0234 | C | C | Johnny Campbell | McD | 2019-10-18 | Johnny Campbell | Comm |  |  | 2019-12-14 | Jack Fields
FPS-03 | FPS-03 | PI09797 | Verified | Test Package FPS-T-09 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-11 | Kelvin Cook
FPS-03 | FPS-03 | PI12682 | Verified | Ground the STG valve house at opposing corners. | A | E | Dustin Futrell | McD | 2019-11-01 | Dustin Futrell | Const | 2019-11-11 | Brad Stanford | 2019-11-15 | Fred Michael
FPS-03 | FPS-03 | PI12683 | Verified | Tag all components in the STG valve house (with numbers). | C | P | Kelvin Cook | McD | 2019-11-01 | Kelvin Cook | Const | 2020-02-10 | Kelvin Cook | 2020-03-09 | Michael Law
FPS-03 | FPS-03 | PI12684 | Verified | Grout all supports in the STG valve house. | C | C | Johnny Campbell | McD | 2019-11-01 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2019-12-15 | Kelvin Cook
FPS-03 | FPS-03 | PI12685 | Verified | Complete all tamper switch terminations in the STG valve house. | A | E | Sheri Fritz | ITS | 2019-11-01 | Sheri Fritz | Const | 2019-11-14 | Chris Karnes | 2019-12-16 | Randy Carpenter
FPS-03 | FPS-03 | PI12686 | Verified | Tag all valves in the STG building. | C | P | Kelvin Cook | McD | 2019-11-01 | Kelvin Cook | Const |  |  | 2020-02-06 | Kelvin Cook
FPS-03 | FPS-03 | PI12687 | Verified | Review design for sprinkler under condenser (FW service). | A | P | Kelvin Cook | McD | 2019-11-01 | Kelvin Cook | Const |  |  | 2019-11-11 | Kelvin Cook
FPS-03 | FPS-03 | PI12688 | Verified | Install toe-plate at fire protection piping penetrations on the STG mezz level (total of 4). | C | C | Tim Gallegos | McD | 2019-11-01 | Tim Gallegos | Const | 2020-05-07 | Tim Gallegos | 2020-05-07 | Michael Law
FPS-03 | FPS-03 | PI12689 | Verified | Install heads on bearings prior to STG operation. | B | P | Sheri Fritz | JAN | 2019-11-01 | Sheri Fritz | Const | 2020-02-05 | Eric Czajka | 2020-02-27 | Michael Law
FPS-03 | FPS-03 | PI12690 | Verified | Southwest corner of mezz level - cross section of pipe requires minimal gap between headers. | B | P | Sheri Fritz | JAN | 2019-11-01 | Sheri Fritz | Const | 2019-11-13 | Chris Karnes | 2019-11-23 | Kelvin Cook
FPS-03 | FPS-03 | PI12691 | Verified | Additional support required on 1" drain line - mezz level, east wall. | B | P | Sheri Fritz | JAN | 2019-11-01 | Sheri Fritz | Const | 2019-11-13 | Chris Karnes | 2019-11-23 | Kelvin Cook
FPS-03 | FPS-03 | PI12692 | Verified | Additional support required on 1" drain line - mezz level, northwest corner. | B | P | Sheri Fritz | JAN | 2019-11-01 | Sheri Fritz | Const | 2019-11-13 | Chris Karnes | 2019-11-23 | Kelvin Cook
FPS-03 | FPS-03 | PI12693 | Verified | Additional support required on 1" drain line - mezz level, north central. | B | P | Sheri Fritz | JAN | 2019-11-01 | Sheri Fritz | Const | 2019-11-13 | Chris Karnes | 2019-11-23 | Kelvin Cook
FPS-03 | FPS-03 | PI12694 | Verified | Provide hydrotest report. | B | P | Sheri Fritz | JAN | 2019-11-01 | Sheri Fritz | Const | 2019-11-14 | Chris Karnes | 2019-12-04 | Kelvin Cook
FPS-03 | FPS-03 | PI12695 | Verified | Provide bolt torquing report. | A | P | David West | JAN | 2019-11-01 | David West | Const |  |  | 2019-11-13 | Michael Law
FPS-03 | FPS-03 | PI17153 | Verified | No lighting inside STG Unit 1C Fire Protection Valve House, complete wiring | C | E | Chris Colvin | McD | 2020-02-22 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-04-08 | Bernard Stasse
FPS-03 | FPS-03 | PI17336 | Verified | GFCI for Duplex outlets not installed, inside Valve house. | C | E | Chris Colvin | McD | 2020-02-28 | Chris Colvin | Comm | 2020-07-10 | Mike Tabbert | 2020-07-10 | Dave Goldak
FWS-01 | FWS-01 | PI04452 | Verified | Complete the fuel gas heater feed water return pipe. | A | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2019-09-05 | Damon Turner | 2019-10-24 | Brian Ballard
FWS-01 | FWS-01 | PI03928 | Verified | 1ACTSC0275, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI03929 | Verified | 1ACTSC0276, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI03930 | Verified | 1ACTSC0277, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI03931 | Verified | 1ACTSC0278, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI03932 | Verified | 1ACTSC0279, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI03933 | Verified | 1ACTSC0280, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI03934 | Verified | 1ACTSC0281, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI03935 | Verified | 1ACTSC0282, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI03936 | Verified | 1ACTSC0283, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI03937 | Verified | 1ACTSC0284, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04063 | Verified | 1ACTSX0390, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
FWS-01 | FWS-01 | PI04062 | Verified | 1ACTSX0389, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
FWS-01 | FWS-01 | PI04061 | Verified | 1ACTSX0388, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
FWS-01 | FWS-01 | PI04060 | Verified | 1ACTSX0387, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Michael Law
FWS-01 | FWS-01 | PI04059 | Verified | 1ACTSX0386, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI04058 | Verified | 1ACTSX0385, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04057 | Verified | 1ACTSX0384, From Termination, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI04056 | Verified | 1ACTSX0383, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04065 | Verified | 1ACTSX0399, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI04066 | Verified | 1ACTSX0400, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Michael Law
FWS-01 | FWS-01 | PI04067 | Verified | 1ACTSX0401, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Michael Law
FWS-01 | FWS-01 | PI04064 | Verified | 1ACTSX0398, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI04076 | Verified | 1ACTSX0432, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI04077 | Verified | 1ACTSX0433, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Michael Law
FWS-01 | FWS-01 | PI04078 | Verified | 1ACTSX0434, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI04079 | Verified | 1ACTSX0435, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI04080 | Verified | 1ACTSX0436, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04081 | Verified | 1ACTSX0438, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-10-22 | Michael Law
FWS-01 | FWS-01 | PI04082 | Verified | 1ACTSX0439, From Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04225 | Verified | 1ACTSX0383, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04226 | Verified | 1ACTSX0385, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04227 | Verified | 1ACTSX0391, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04228 | Verified | 1ACTSX0392, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04229 | Verified | 1ACTSX0393, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04230 | Verified | 1ACTSX0394, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04231 | Verified | 1ACTSX0395, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04232 | Verified | 1ACTSX0396, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04233 | Verified | 1ACTSX0397, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04240 | Verified | 1ACTSX0438, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI04241 | Verified | 1ACTSX0439, To Termination | A | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI03888 | Verified | 1ACTSX0438, Pull Cable | A | E | Mike Tabbert | McD | 2019-08-14 | Mike Tabbert | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI03889 | Verified | 1ACTSX0439, Pull Cable | A | E | Mike Tabbert | McD | 2019-08-14 | Mike Tabbert | Const |  |  | 2019-09-17 | Michael Law
FWS-01 | FWS-01 | PI07775 | Verified | Seal BFW pump enclosures & flash. After de-greasing. | C | M | Shane Crowe | McD | 2019-09-28 | Shane Crowe | Const | 2020-03-19 | Shane Crowe | 2020-04-06 | Bernard Stasse
FWS-01 | FWS-01 | PI07776 | Verified | Clean BFW pump skids. Pump A can be done now. Pump B after comm. lube oil flush. | B | M | Shane Crowe | McD | 2019-09-28 | Shane Crowe | Const | 2019-10-18 | Shane Crowe | 2020-01-13 | Michael Law
FWS-01 | FWS-01 | PI07777 | Verified | Re-install insulation on pump A after alignment. | B | M | Shane Crowe | McD | 2019-09-28 | Shane Crowe | Const |  |  | 2019-11-22 | Joshua Sturgeon
FWS-01 | FWS-01 | PI07778 | Verified | Grout all supports at feedwater and under condenser. | C | C | Johnny Campbell | McD | 2019-09-28 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2020-01-09 | Kelvin Cook
FWS-01 | FWS-01 | PI07779 | Verified | Install casing drain piping on pump A. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-16 | James Beech | 2019-12-19 | J.L. Bickham
FWS-01 | FWS-01 | PI07780 | Verified | Install casing drain piping on pump B. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-16 | James Beech | 2019-12-19 | J.L. Bickham
FWS-01 | FWS-01 | PI07781 | Verified | Restore all piping after hydros. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-11-23 | Michael Law | 2020-01-13 | Michael Law
FWS-01 | FWS-01 | PI07782 | Verified | Tie in CCW piping at pump A. | A | P | Kelvin Cook | McD | 2019-09-28 | Kelvin Cook | Const | 2019-10-23 | Joshua Sturgeon | 2020-01-13 | Michael Law
FWS-01 | FWS-01 | PI07783 | Verified | 1A-FWS-SRV-0075A - bolts too long / incorrect, incorrect gasket. Pump A. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const |  |  | 2019-10-28 | Alex Isaac
FWS-01 | FWS-01 | PI07784 | Verified | Verify pump assembly data (all). | A | M | Joshua Sturgeon | McD | 2019-09-28 | Joshua Sturgeon | Const | 2019-10-01 | Joshua Sturgeon | 2019-10-03 | Shannon Scott
FWS-01 | FWS-01 | PI07785 | Verified | Line 1A-FWS-0075 missing supports. Pump A | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-28 | Alex Isaac
FWS-01 | FWS-01 | PI07787 | Verified | Tag all valves. | C | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2020-02-27 | James Beech | 2020-02-27 | Kelvin Cook
FWS-01 | FWS-01 | PI07788 | Verified | Clean feedwater strainer platform. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-11 | James Beech | 2020-01-13 | Michael Law
FWS-01 | FWS-01 | PI07789 | Verified | Repair bent stem on 1A-FWS-V-0209A. FW strainer platform. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2020-02-10 | Tim Green | 2020-03-03 | Michael Law
FWS-01 | FWS-01 | PI07790 | Verified | Set all spring cans to cold setting & pull gags. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-12-17 | James Beech | 2020-01-13 | Michael Law
FWS-01 | FWS-01 | PI07791 | Verified | Rotate valve 1A-FWS-V-0209B 180 deg. FW strainer platform. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-16 | Alex Isaac
FWS-01 | FWS-01 | PI07792 | Verified | Valve 1A-FWS-V-0209B has incorrect tag. FW strainer platform. | C | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2020-05-04 | Michael Law | 2020-05-04 | Michael Law
FWS-01 | FWS-01 | PI07793 | Verified | Update vendor document in iDocsw for valves 1A-FWS-V-0209B, 1B-FWS-V-0209A & B. | C | P | Kelvin Cook | McD | 2019-09-28 | Kelvin Cook | Const | 2020-02-28 | Kelvin Cook | 2020-04-07 | Randy Carpenter
FWS-01 | FWS-01 | PI07794 | Verified | Supports at 1A-FWS-V-0208A & B need adjusting. Need to touch before hydro. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-11 | James Beech | 2020-01-13 | Michael Law
FWS-01 | FWS-01 | PI07795 | Verified | 1A-FWS-V-0220 missing handwheel. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07796 | Verified | Install 1A-FWS-FE-8002 after degrease. FW strainer platform. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-11-06 | James Beech | 2020-01-13 | Michael Law
FWS-01 | FWS-01 | PI07797 | Verified | Adjust support 1A-FWS-PD-HGR-0528. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-11 | James Beech | 2020-01-21 | Michael Law
FWS-01 | FWS-01 | PI07798 | Verified | Install 1A-FWS-SRV-0549. FW strainer platform. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-12 | Shane Copeland
FWS-01 | FWS-01 | PI07799 | Verified | Install 1A-FWS-FE-0520 after degrease. FW strainer platform. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-12 | Shane Copeland
FWS-01 | FWS-01 | PI07800 | Verified | Install stem indicator on 1A-FWS-V-0521. FW strainer platform. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2020-01-06 | James Beech | 2020-01-08 | Ethan Byrd
FWS-01 | FWS-01 | PI07801 | Verified | Install 1A-FWS-SRV-0540. FW strainer platform. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-23 | Alex Isaac
FWS-01 | FWS-01 | PI07802 | Verified | Drain line for 1A-FWS-SRV-0540 needs support. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-15 | James Beech | 2020-01-21 | Michael Law
FWS-01 | FWS-01 | PI07803 | Verified | Support under 1A-FWS-AOV-0531 incomplete. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07804 | Verified | Line 1A-FWS-0150 missing supports / hangers. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07805 | Verified | Line 1A-FWS-0155 missing supports. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const |  |  | 2019-10-28 | Alex Isaac
FWS-01 | FWS-01 | PI07806 | Verified | Valve 1A-FWS-V-0155B missing handwheel. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-11 | James Beech | 2020-01-21 | Michael Law
FWS-01 | FWS-01 | PI07807 | Verified | Line 1A-FWS-0150 - vent line not installed. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const |  |  | 2019-10-28 | Alex Isaac
FWS-01 | FWS-01 | PI07808 | Verified | Install 1A-FWS-FE-0072A after degrease. FW strainer platform. | B | P | William Mitchell | McD | 2019-09-28 | William Mitchell | Const | 2019-12-23 | Michael Law | 2020-01-01 | Kelvin Cook
FWS-01 | FWS-01 | PI07809 | Verified | Install 1A-FWS-FE-0072B after degrease. FW strainer platform. | B | P | William Mitchell | McD | 2019-09-28 | William Mitchell | Const | 2019-12-23 | Michael Law | 2020-01-01 | Kelvin Cook
FWS-01 | FWS-01 | PI07810 | Verified | Support FWS-0590 incomplete. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07811 | Verified | 1A-FWS-STN-0050A missing bolts. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-15 | Shannon Scott
FWS-01 | FWS-01 | PI07812 | Verified | Line FWS-0278 - vent line not installed. FW strainer platform. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-12 | Shane Copeland
FWS-01 | FWS-01 | PI07813 | Verified | Line FWS-0052 - missing bolts at strainer connection. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07814 | Verified | 1A-FWS-STN-0050B missing bolts. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07815 | Verified | Line FWS-0353 - vent line not installed. FW strainer platform. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-12 | Shane Copeland
FWS-01 | FWS-01 | PI07816 | Verified | Line FWS-0062 missing bolts at strainer connection. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07817 | Verified | Support FWS-0547 incomplete. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07818 | Verified | 1A-FWS-SRV-0548 missing / wrong bolts. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07819 | Verified | Support under 1A-FWS-PV-0513 incomplete. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07820 | Verified | Complete installation of lines at 1A-FWS-PV-0513 & install valve handwheel. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const |  |  | 2019-10-28 | Alex Isaac
FWS-01 | FWS-01 | PI07821 | Verified | Line FWS-0011 missing supports. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07822 | Verified | 1A-FWS-SRV-0049 missing bolts. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07823 | Verified | Valves 1A-FWS-V-0201A & B need handweel pins. Under condenser. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2020-01-06 | James Beech | 2020-03-09 | Michael Law
FWS-01 | FWS-01 | PI07824 | Verified | Supports on lines 236 & 237 incomplete. Under condenser. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-11-04 | James Beech | 2019-11-06 | Alex Isaac
FWS-01 | FWS-01 | PI07825 | Verified | Line 1A-FWS-0541 & 0542 incomplete. At condenser. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-11-08 | James Beech | 2019-11-23 | Alex Isaac
FWS-01 | FWS-01 | PI07826 | Verified | Remove temporary support on line at the FG performance heater. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-12-02 | James Beech | 2020-01-27 | Michael Law
FWS-01 | FWS-01 | PI07827 | Verified | Support 0122 not installed per design. At FG performance heater. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-28 | Alex Isaac
FWS-01 | FWS-01 | PI07828 | Verified | Line 250 supports incomplete. At FG performance heater. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const |  |  | 2019-10-28 | Alex Isaac
FWS-01 | FWS-01 | PI07829 | Verified | Install 1A-FWS-FE-0250 after degrease. FW strainer platform. | B | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-12 | Shane Copeland
FWS-01 | FWS-01 | PI07830 | Verified | Line 0250 - vent line not installed. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07831 | Verified | Line 0250 - remove dunnage & install support. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07832 | Verified | Line 0260 incomplete. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07833 | Verified | Line 0262 - missing support. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07834 | Verified | Valve 1A-FWS-V-0271 - rotate head east. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07835 | Verified | Valve 1A-FWS-V-0271 - missing handwheel. FW strainer platform. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI07836 | Verified | Line 0525 incomplete. At TCA. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-16 | James Beech | 2019-11-02 | Alex Isaac
FWS-01 | FWS-01 | PI07837 | Verified | Line 0505 incomplete. At TCA. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-16 | James Beech | 2019-11-02 | Alex Isaac
FWS-01 | FWS-01 | PI07838 | Verified | Support 1A-FWS-PD-HGR-0962 not per design, angle iron not correct. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-16 | James Beech | 2019-11-02 | Alex Isaac
FWS-01 | FWS-01 | PI07839 | Verified | High point vent on line 1A-FWS-0150 not installed. | A | P | James Beech | McD | 2019-09-28 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-28 | Alex Isaac
FWS-01 | FWS-01 | PI08512 | Verified | 1AFWSK0015, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
FWS-01 | FWS-01 | PI08513 | Verified | 1AFWSK0028, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08514 | Verified | 1AFWSK0029, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-21 | Mike Tabbert
FWS-01 | FWS-01 | PI08515 | Verified | 1AFWSK0030, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-21 | Mike Tabbert
FWS-01 | FWS-01 | PI08516 | Verified | 1AFWSX0031, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08517 | Verified | 1AFWSX0066, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08518 | Verified | 1ACTSC0275, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08519 | Verified | 1ACTSC0276, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08520 | Verified | 1ACTSC0277, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08521 | Verified | 1ACTSC0278, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08522 | Verified | 1ACTSX0383, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08523 | Verified | 1ACTSX0384, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08524 | Verified | 1ACTSX0385, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08525 | Verified | 1ACTSX0386, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08526 | Verified | 1ACTSX0387, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08527 | Verified | 1ACTSX0398, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08528 | Verified | 1ACTSX0399, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08529 | Verified | 1ACTSX0400, From Termination. Valve 1A-FWS-2T-0537. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-03 | Michael Law
FWS-01 | FWS-01 | PI08530 | Verified | 1ACTSX0401, From Termination. Valve 1A-FWS-ZT-0570. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-03 | Michael Law
FWS-01 | FWS-01 | PI08531 | Verified | 1ACTSX0432, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08532 | Verified | 1ACTSX0433, From Termination. Valve 1A-FWS-FT-0256. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-03 | Michael Law
FWS-01 | FWS-01 | PI08533 | Verified | 1ACTSX0434, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08534 | Verified | 1ACTSX0435, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08535 | Verified | 1ACTSX0436, From Termination. Valve 1A-FWS-FY-0531. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-03 | Michael Law
FWS-01 | FWS-01 | PI08536 | Verified | 1ACTSX0438, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08537 | Verified | 1ACTSX0439, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
FWS-01 | FWS-01 | PI08538 | Verified | 1AFWSC0001, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08539 | Verified | 1AFWSC0003, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08540 | Verified | 1AFWSC0007, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08541 | Verified | 1AFWSC0009, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08542 | Verified | 1AFWSC0011, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08543 | Verified | 1AFWSC0012, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08544 | Verified | 1AFWSC0018, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08545 | Verified | 1AFWSC0022, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08546 | Verified | 1AFWSC0026, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08547 | Verified | 1AFWSC0030, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08548 | Verified | 1AFWSC0031, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08549 | Verified | 1AFWSC0036, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08550 | Verified | 1AFWSK0008, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08551 | Verified | 1AFWSK0010, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08552 | Verified | 1AFWSK0011, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08553 | Verified | 1AFWSK0012, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08554 | Verified | 1AFWSK0013, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08555 | Verified | 1AFWSK0014, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
FWS-01 | FWS-01 | PI08556 | Verified | 1AFWSK0015, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08557 | Verified | 1AFWSK0017, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08558 | Verified | 1AFWSK0023, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08559 | Verified | 1AFWSK0024, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08560 | Verified | 1AFWSK0028, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08561 | Verified | 1AFWSK0029, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08562 | Verified | 1AFWSK0030, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08563 | Verified | 1AFWSX0016, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08564 | Verified | 1AFWSX0017, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08565 | Verified | 1AFWSX0019, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Michael Law | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08566 | Verified | 1AFWSX0020, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08567 | Verified | 1AFWSX0025, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08568 | Verified | 1AFWSX0026, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-22 | Mike Tabbert
FWS-01 | FWS-01 | PI08569 | Verified | 1AFWSX0029, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08570 | Verified | 1AFWSX0030, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08571 | Verified | 1AFWSX0031, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08572 | Verified | 1AFWSX0032, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08573 | Verified | 1AFWSX0033, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08574 | Verified | 1AFWSX0034, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08575 | Verified | 1AFWSX0035, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08576 | Verified | 1AFWSX0036, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08577 | Verified | 1AFWSX0037, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08578 | Verified | 1AFWSX0047, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08579 | Verified | 1AFWSX0048, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08580 | Verified | 1AFWSX0051, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08581 | Verified | 1AFWSX0052, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08582 | Verified | 1AFWSX0060, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08583 | Verified | 1AFWSX0066, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08584 | Verified | 1ACTSX0383, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08585 | Verified | 1ACTSX0385, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08586 | Verified | 1ACTSX0391, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08587 | Verified | 1ACTSX0392, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08588 | Verified | 1ACTSX0393, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08589 | Verified | 1ACTSX0394, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08590 | Verified | 1ACTSX0395, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-04 | Mike Tabbert
FWS-01 | FWS-01 | PI08591 | Verified | 1ACTSX0396, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-04 | Mike Tabbert
FWS-01 | FWS-01 | PI08592 | Verified | 1ACTSX0397, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-04 | Mike Tabbert
FWS-01 | FWS-01 | PI08593 | Verified | 1AFWSC0001, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08594 | Verified | 1AFWSC0003, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
FWS-01 | FWS-01 | PI08595 | Verified | 1AFWSC0007, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08596 | Verified | 1AFWSC0008, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08597 | Verified | 1AFWSC0009, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08598 | Verified | 1AFWSC0010, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08599 | Verified | 1AFWSC0011, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08600 | Verified | 1AFWSC0012, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08601 | Verified | 1AFWSC0019, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08602 | Verified | 1AFWSC0020, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08603 | Verified | 1AFWSC0021, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08604 | Verified | 1AFWSC0023, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08605 | Verified | 1AFWSC0024, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08606 | Verified | 1AFWSC0026, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08607 | Verified | 1AFWSC0027, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08608 | Verified | 1AFWSC0028, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08609 | Verified | 1AFWSC0029, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08610 | Verified | 1AFWSC0030, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
FWS-01 | FWS-01 | PI08611 | Verified | 1AFWSC0031, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
FWS-01 | FWS-01 | PI08612 | Verified | 1AFWSC0036, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08613 | Verified | 1AFWSC0039, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08614 | Verified | 1AFWSH0001G1, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08615 | Verified | 1AFWSK0014, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
FWS-01 | FWS-01 | PI08616 | Verified | 1AFWSK0015, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
FWS-01 | FWS-01 | PI08617 | Verified | 1AFWSK0017, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08618 | Verified | 1AFWSK0022, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
FWS-01 | FWS-01 | PI08619 | Verified | 1AFWSK0023, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08620 | Verified | 1AFWSK0024, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08621 | Verified | 1AFWSK0028, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
FWS-01 | FWS-01 | PI08622 | Verified | 1AFWSK0029, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08623 | Verified | 1AFWSK0030, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08624 | Verified | 1AFWSX0002, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08625 | Verified | 1AFWSX0003, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08626 | Verified | 1AFWSX0013, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08627 | Verified | 1AFWSX0014, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08628 | Verified | 1AFWSX0016, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08629 | Verified | 1AFWSX0017, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-04 | Mike Tabbert
FWS-01 | FWS-01 | PI08630 | Verified | 1AFWSX0018, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-04 | Mike Tabbert
FWS-01 | FWS-01 | PI08631 | Verified | 1AFWSX0019, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-01 | FWS-01 | PI08632 | Verified | 1AFWSX0023, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08633 | Verified | 1AFWSX0024, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08634 | Verified | 1AFWSX0025, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-01 | FWS-01 | PI08635 | Verified | 1AFWSX0026, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08636 | Verified | 1AFWSX0029, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08637 | Verified | 1AFWSX0030, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-01 | FWS-01 | PI08638 | Verified | 1AFWSX0031, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08639 | Verified | 1AFWSX0032, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08640 | Verified | 1AFWSX0033, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08641 | Verified | 1AFWSX0034, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-01 | FWS-01 | PI08642 | Verified | 1AFWSX0035, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-01 | FWS-01 | PI08643 | Verified | 1AFWSX0036, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-04 | Mike Tabbert
FWS-01 | FWS-01 | PI08644 | Verified | 1AFWSX0037, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08645 | Verified | 1AFWSX0051, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08646 | Verified | 1AFWSX0063, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-01 | FWS-01 | PI08647 | Verified | 1AFWSX0064, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08648 | Verified | 1AFWSX0065, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08649 | Verified | 1AFWSX0066, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-01 | FWS-01 | PI08650 | Verified | Instrument stand on west side of the B pump enclosure needs to be moved for B feed pump removal. | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-10-09 | Gonzalo Pena | 2019-10-16 | Albert Burge
FWS-01 | FWS-01 | PI08651 | Verified | 1A-FWS-CP-0200B - ground panel. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-09 | Dustin Futrell | 2020-01-13 | Fred Michael
FWS-01 | FWS-01 | PI08652 | Verified | 1A-FWS-CP-0200B - label panel. | C | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Fred Michael | 2019-10-16 | Fred Michael
FWS-01 | FWS-01 | PI08653 | Verified | 1A-FWS-CP-0200B - seal penetrations. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-09 | Dustin Futrell | 2020-01-13 | Fred Michael
FWS-01 | FWS-01 | PI08654 | Verified | 1A-FWS-M-0100B - ground duct bank (both sides). | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2020-01-13 | Fred Michael
FWS-01 | FWS-01 | PI08655 | Verified | 1A-FWS-M-0100B - remove unused conduit. | C | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-31 | Brad Stanford | 2020-01-13 | Fred Michael
FWS-01 | FWS-01 | PI08656 | Verified | 1A-FWS-M-0100B - ground motor. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2020-01-13 | Fred Michael
FWS-01 | FWS-01 | PI08657 | Verified | 1A-FWS-M-0100B - ground cable tray. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2019-12-08 | Scott Davis
FWS-01 | FWS-01 | PI08658 | Verified | 1A-FWS-M-0100B - ground bushings. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2019-12-13 | Mike Tabbert
FWS-01 | FWS-01 | PI08659 | Verified | 1A-FWS-M-0100B - add jumpers to CT secondary. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
FWS-01 | FWS-01 | PI08660 | Verified | 1A-FWS-M-0100B - ground motor connection box. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2020-01-13 | Fred Michael
FWS-01 | FWS-01 | PI08661 | Verified | 1A-FWS-TB-0101B - clean out. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2019-12-08 | Scott Davis
FWS-01 | FWS-01 | PI08662 | Verified | 1A-FWS-M-0100A - remove unused conduit. | C | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-12-14 | Fred Michael | 2020-01-13 | Fred Michael
FWS-01 | FWS-01 | PI08663 | Verified | 1A-FWS-TB-0101A - clean out. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2019-12-08 | Scott Davis
FWS-01 | FWS-01 | PI08664 | Verified | 1A-FWS-M-0100A - ground cable tray. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2019-12-08 | Scott Davis
FWS-01 | FWS-01 | PI08665 | Verified | 1A-FWS-M-0100A - ground bushings. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2019-12-13 | Mike Tabbert
FWS-01 | FWS-01 | PI08666 | Verified | 1A-FWS-M-0100A - add jumpers to CT secondary. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-01 | Brad Stanford | 2020-01-13 | Fred Michael
FWS-01 | FWS-01 | PI08667 | Verified | 1A-FWS-TI-1224A is broken. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-30 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08668 | Verified | 1A-FWS-TI-1224B is broken. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-30 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08693 | Verified | Complete instrument tubing in 1A-HTS-CAB-0202. FW strainer deck. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08694 | Verified | Complete instrument tubing in 1A-HTS-CAB-0304. FW strainer deck. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08695 | Verified | Complete instrument tubing in 1A-HTS-CAB-0200. FW strainer deck. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08696 | Verified | Ground seal tite for 1A-HTS-CAB-0307. FW strainer deck. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08697 | Verified | Ground seal tite for 1A-HTS-CAB-0202. FW strainer deck. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08698 | Verified | Ground seal tite for 1A-HTS-CAB-0304. FW strainer deck. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08699 | Verified | Ground seal tite for 1A-HTS-CAB-0200. FW strainer deck. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08700 | Verified | Install 1A-FWS-ZSO-0054A & B, 0055A & B and 0070A&B. FW strainer deck. | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-19 | Albert Burge
FWS-01 | FWS-01 | PI08701 | Verified | Run conduit to 1A-FWS-ZSO-0054A & B, 0055A & B and 0070A&B. FW strainer deck. | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Gonzalo Pena | 2019-11-19 | Albert Burge
FWS-01 | FWS-01 | PI08702 | Verified | Complete tubing to 1A-FWS-AOV-0530. FW strainer deck. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-19 | James Tanner | 2019-11-21 | Albert Burge
FWS-01 | FWS-01 | PI08703 | Verified | Complete tubing to 1A-FWS-AOV-0531. FW strainer deck. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2019-12-09 | Albert Burge
FWS-01 | FWS-01 | PI08704 | Verified | Complete raceway to 1A-FWS-AOV-0530. FW strainer deck. | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Brad Stanford | 2019-11-21 | Albert Burge
FWS-01 | FWS-01 | PI08705 | Verified | Complete raceway to 1A-FWS-AOV-0531. FW strainer deck. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-18 | Brad Stanford | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08706 | Verified | Complete instrument tubing in 1A-HTS-CAB-0201. FW strainer deck. | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-05 | Albert Burge
FWS-01 | FWS-01 | PI08707 | Verified | Ground seal tite for 1A-HTS-CAB-0201. FW strainer deck. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-18 | Brad Stanford | 2019-12-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08708 | Verified | Complete instrument tubing in 1A-HTS-CAB-0204. FW strainer deck. After degrease. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08709 | Verified | Complete raceway to 1A-HTS-CAB-0204. FW strainer deck. After steam blows. | B | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-13 | Mike Tabbert
FWS-01 | FWS-01 | PI08710 | Verified | Complete raceway to 1A-FWS-FV-0269. FW strainer deck. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-18 | Brad Stanford | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08711 | Verified | Complete tubing to 1A-FWS-AOV-0265. FW strainer deck. | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-10-09 | Gonzalo Pena | 2019-10-16 | Albert Burge
FWS-01 | FWS-01 | PI08712 | Verified | Complete raceway to 1A-FWS-AOV-0265. FW strainer deck. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-18 | Brad Stanford | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08713 | Verified | Install 1A-FWS-LSL-0262. FW strainer deck. | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-10-09 | Gonzalo Pena | 2019-10-16 | Albert Burge
FWS-01 | FWS-01 | PI08714 | Verified | Complete raceway to 1A-FWS-LSL-0262. FW strainer deck. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-18 | Brad Stanford | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08715 | Verified | Complete tubing to 1A-FWS-AOV-0263. FW strainer deck. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2019-12-09 | Albert Burge
FWS-01 | FWS-01 | PI08716 | Verified | Complete raceway to 1A-FWS-AOV-0263. FW strainer deck. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-13 | Michael Law | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08717 | Verified | Complete tubing to 1A-FWS-AOV-0256. FW strainer deck. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2019-12-09 | Albert Burge
FWS-01 | FWS-01 | PI08718 | Verified | Complete raceway to 1A-FWS-AOV-0256. FW strainer deck. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-13 | Michael Law | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08719 | Verified | Complete tubing to 1A-FWS-AOV-0252. FW strainer deck. | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-10-09 | Gonzalo Pena | 2019-10-28 | Albert Burge
FWS-01 | FWS-01 | PI08720 | Verified | Complete raceway to 1A-FWS-AOV-0252. FW strainer deck. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-18 | Brad Stanford | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08721 | Verified | Complete raceway to 1A-FWS-TE-0251. FW strainer deck. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-18 | Brad Stanford | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08722 | Verified | Run conduit to 1AFW-TE-0261. At FG heater. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-18 | Brad Stanford | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08723 | Verified | Complete instrument tubing in 1AHTS-CAB-0309. At TCA. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08724 | Verified | Complete raceway to 1AHTS-CAB-0309. At TCA. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-18 | Brad Stanford | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08725 | Verified | Complete instrument tubing in 1AHTS-CAB-0308. At TCA. | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-10-09 | Gonzalo Pena | 2019-10-28 | Albert Burge
FWS-01 | FWS-01 | PI08692 | Verified | Complete instrument tubing in 1A-HTS-CAB-0307. FW strainer deck. | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-05 | Albert Burge
FWS-01 | FWS-01 | PI08691 | Verified | Move / modify scaffold at north end of feedwater strainer deck. Blocking instrument enclosure access. | B | C | Jerry Smith | McD | 2019-10-04 | Jerry Smith | Const | 2019-11-11 | Gonzalo Pena | 2019-12-13 | Gonzalo Pena
FWS-01 | FWS-01 | PI08690 | Verified | Complete tubing in inst. enclosure north side of pump A enclosure (1A-FWS-FIT-0072A, PDIT-0050, PIT-0513). | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-10-16 | Gonzalo Pena | 2019-10-28 | Albert Burge
FWS-01 | FWS-01 | PI08689 | Verified | Redo conduit for instrument enclosure on north side of the pump A enclosure. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-18 | Brad Stanford | 2019-12-08 | Scott Davis
FWS-01 | FWS-01 | PI08688 | Verified | Reverse rotation indicator module broken on 1A-FWS-M-0100A. | B | I | Albert Burge | McD | 2019-10-04 | Albert Burge | Const | 2020-01-16 | Albert Burge | 2020-01-20 | Mike Tabbert
FWS-01 | FWS-01 | PI08687 | Verified | Run tubing 1A-FWS-TI-0130A - not req'd | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-10-10 | Gonzalo Pena | 2019-10-16 | Albert Burge
FWS-01 | FWS-01 | PI08686 | Verified | Run tubing 1A-FWS-TI-0131A - Not req'd | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-10-10 | Gonzalo Pena | 2019-10-16 | Albert Burge
FWS-01 | FWS-01 | PI08685 | Verified | Install 1A-FWS-TI-0130A | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08684 | Verified | Install 1A-FWS-TI-0131A. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08683 | Verified | Run tubing for 1A-FWS-PI-0202A. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08682 | Verified | Run tubing for 1A-FWS-PI-0152A. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08681 | Verified | Install 1A-FWS-PI-0202A. | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-10-10 | Gonzalo Pena | 2019-10-16 | Albert Burge
FWS-01 | FWS-01 | PI08680 | Verified | Install 1A-FWS-PI-0152A. | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-10-10 | Gonzalo Pena | 2019-10-16 | Albert Burge
FWS-01 | FWS-01 | PI08679 | Verified | Install stand for 1A-FWS-TB-0101B at FW motor. | A | M | Shane Crowe | McD | 2019-10-04 | Shane Crowe | Const | 2019-10-16 | Shane Crowe | 2020-01-13 | Michael Law
FWS-01 | FWS-01 | PI08678 | Verified | Install stand for 1A-FWS-TB-0101A at FW motor. | A | M | Shane Crowe | McD | 2019-10-04 | Shane Crowe | Const | 2019-10-16 | Shane Crowe | 2020-01-13 | Michael Law
FWS-01 | FWS-01 | PI08677 | Verified | 1A-FWS-CP-0200A - label. | C | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Fred Michael | 2019-10-16 | Fred Michael
FWS-01 | FWS-01 | PI08676 | Verified | 1A-FWS-CP-0200A - seal penetrations. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2020-01-13 | Fred Michael
FWS-01 | FWS-01 | PI08675 | Verified | 1A-FWS-CP-0200A - clean out. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2019-12-08 | Scott Davis
FWS-01 | FWS-01 | PI08674 | Verified | 1A-FWS-M-0100A - missing condulet covers. | B | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-17 | Fred Michael
FWS-01 | FWS-01 | PI08673 | Verified | Install 1A-FWS-TI-0130B. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08672 | Verified | Install 1A-FWS-TI-0131B. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08671 | Verified | Complete tubing on 1A-FWS-PI-0152B. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08670 | Verified | Complete tubing on 1A-FWS-PI-0074B. | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-10-10 | Gonzalo Pena | 2019-10-16 | Albert Burge
FWS-01 | FWS-01 | PI08669 | Verified | Complete tubing on 1A-FWS-PI-0202B. | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI08726 | Verified | Complete raceway to 1AHTS-CAB-0308. At TCA. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-18 | Brad Stanford | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08727 | Verified | Complete raceway to 1A-FWS-PIT-0555. At TCA. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-18 | Brad Stanford | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI08728 | Verified | Install 1A-FWS-TE-0550. At TCA. | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-10-09 | Gonzalo Pena | 2019-10-28 | Albert Burge
FWS-01 | FWS-01 | PI08729 | Verified | Run conduit to 1A-FWS-ZT-0570 (FV). At TCA. After degrease. | B | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-14 | Mike Tabbert
FWS-01 | FWS-01 | PI08730 | Verified | Install 1A-FWS-FV-0537. Under condenser. | B | P | James Beech | McD | 2019-10-04 | James Beech | Const | 2020-01-06 | James Beech | 2020-01-15 | Albert Burge
FWS-01 | FWS-01 | PI08731 | Verified | Install 1A-FWS-FV-0235A. Under condenser. | B | P | James Beech | McD | 2019-10-04 | James Beech | Const |  |  | 2019-11-15 | Alex Isaac
FWS-01 | FWS-01 | PI08732 | Verified | Install 1A-FWS-FV-0235B. Under condenser. | B | P | James Beech | McD | 2019-10-04 | James Beech | Const |  |  | 2019-11-15 | Alex Isaac
FWS-01 | FWS-01 | PI08733 | Verified | Install 1A-FWS-LV-8002A. Top of HRSG. After degrease. | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const |  |  | 2019-11-15 | Alex Isaac
FWS-01 | FWS-01 | PI08734 | Verified | Install 1A-FWS-LV-8002B. Top of HRSG. After degrease. | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const |  |  | 2019-11-15 | Alex Isaac
FWS-01 | FWS-01 | PI08735 | Verified | Run conduit to 1A-FWS-MOV-8003. Top of HRSG. | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2019-12-08 | Mike Tabbert
FWS-01 | FWS-01 | PI06613 | Verified | Handwheel not installed on valve 1A-FWS-V-0220 | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-16 | James Beech | 2019-10-22 | Alex Isaac
FWS-01 | FWS-01 | PI06614 | Verified | Support 1A-MSS-PD-HGR-0001 not on centerline of steel, not touching steel | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-04 | James Beech | 2019-11-06 | Alex Isaac
FWS-01 | FWS-01 | PI06615 | Verified | Support 1A-MSS-PD-HGR-0002 not on centerline of steel, not touching steel, guides not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-04 | James Beech | 2019-11-06 | Alex Isaac
FWS-01 | FWS-01 | PI06616 | Verified | Support 1A-MSS-PD-HGR-0003 not on centerline of steel, guides not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-04 | James Beech | 2019-11-06 | Alex Isaac
FWS-01 | FWS-01 | PI06617 | Verified | Support 1A-MSS-PD-HGR-0004 not on centerline of steel, guides not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-04 | James Beech | 2019-11-06 | Alex Isaac
FWS-01 | FWS-01 | PI06618 | Verified | Guides not installed on support 1A-MSS-PD-HGR-0006 | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-04 | James Beech | 2019-11-06 | Alex Isaac
FWS-01 | FWS-01 | PI06619 | Verified | Guides not installed on support 1A-MSS-PD-HGR-0008 | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-13 | Ethan Byrd
FWS-01 | FWS-01 | PI06620 | Verified | Support 1A-MSS-PD-HGR-0009 not installed | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-13 | Ethan Byrd
FWS-01 | FWS-01 | PI09132 | Verified | Cable tray rack west of HRSG 1A PDC, need hold down clamps as tray turns south towards riser all levels. | B | E | Chris Colvin | McD | 2019-10-05 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-13 | Mike Tabbert
FWS-01 | FWS-01 | PI09134 | Verified | Cable tray rack west of HRSG 1A PDC, after waterfall headed south all the way to pipe rack, need hold down clamps and Cable Tray Labels. | B | E | Chris Colvin | McD | 2019-10-05 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-14 | Mike Tabbert
FWS-01 | FWS-01 | PI09135 | Verified | Cable tray rack west of HRSG 1A PDC, from HRSG PDC to pipe rack cable tray grounding needs to be completed, tie each level of tray to ground and take to grid every 100 feet. | B | E | Chris Colvin | McD | 2019-10-05 | Chris Colvin | Const | 2019-10-24 | Brad Stanford | 2019-12-14 | Mike Tabbert
FWS-01 | FWS-01 | PI09136 | Verified | Cable tray rack west of HRSG 1A PDC, missing section of cable tray after T on main pipe rack bottom layer. | A | E | Chris Colvin | McD | 2019-10-05 | Chris Colvin | Const | 2019-10-24 | Brad Stanford | 2019-12-14 | Mike Tabbert
FWS-01 | FWS-01 | PI09798 | Verified | Test Package FWS-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
FWS-01 | FWS-01 | PI09799 | Verified | Test Package FWS-T-02 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
FWS-01 | FWS-01 | PI09800 | Verified | Test PackageFWS-T-03 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
FWS-01 | FWS-01 | PI09801 | Verified | Test Package FWS-T-04 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
FWS-01 | FWS-01 | PI09802 | Verified | Test Package FWS-T-05 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
FWS-01 | FWS-01 | PI09803 | Verified | Test Package FWS-T-13 in service test | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const | 2019-11-04 | James Beech | 2019-12-04 | Kelvin Cook
FWS-01 | FWS-01 | PI09804 | Verified | Test Package FWS-T-13 need to be tested | B | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-26 | Kelvin Cook
FWS-01 | FWS-01 | PI12629 | Verified | Replace stem packing on valve 1A-FWS-V-1158A (LEAKED DURING HYDRO). | B | P | William Mitchell | McD | 2019-10-30 | William Mitchell | Const | 2019-12-23 | Michael Law | 2020-01-01 | Kelvin Cook
FWS-01 | FWS-01 | PI12630 | Verified | Replace stem packing on valve 1A-FWS-V-1158B (LEAKED DURING HYDRO). | B | P | William Mitchell | McD | 2019-10-30 | William Mitchell | Const | 2019-12-23 | Michael Law | 2020-01-01 | Kelvin Cook
FWS-01 | FWS-01 | PI12707 | Verified | BFP lube oil skid, temp. transmitter 1A-FWS-TT-1200A- signal wire is in the same conduit as the 120 vac control cable. Transmitter wire should be in a different conduit. | A | E | Dustin Futrell | McD | 2019-11-02 | Dustin Futrell | Const | 2019-11-13 | Dustin Futrell | 2019-11-19 | Albert Burge
FWS-01 | FWS-01 | PI12709 | Verified | BFP lube oil skid, temp. transmitter 1A-FWS-TT-1200B- signal wire is in the same conduit as the 120 vac control cable. Transmitter wire should be in a different conduit. | A | E | Dustin Futrell | McD | 2019-11-02 | Dustin Futrell | Const | 2019-11-13 | Dustin Futrell | 2019-11-19 | Albert Burge
FWS-01 | FWS-01 | PI12748 | Verified | Support 1A-FWS-PD-HGR-0798 not touching steel. | A | P | James Beech | McD | 2019-11-05 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-16 | Alex Isaac
FWS-01 | FWS-01 | PI13068 | Verified | Remove start-up trim and install final trim on valve 1A-FWS-PV-0513 (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-06 | Shane Copeland
FWS-01 | FWS-01 | PI13088 | Verified | Install final trim and actuator on valve 1A-FWS-FV-0235A (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-06 | Shane Copeland
FWS-01 | FWS-01 | PI13089 | Verified | Install final trim and actuator on valve 1A-FWS-FV-0235B (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-06 | Shane Copeland
FWS-01 | FWS-01 | PI13090 | Verified | Install final trim and actuator on valve 1A-FWS-FV-0269 (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-06 | Shane Copeland
FWS-01 | FWS-01 | PI13091 | Verified | Install final trim and actuator on valve 1A-FWS-FV-0537 (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-06 | Shane Copeland
FWS-01 | FWS-01 | PI13092 | Verified | Install final trim and actuator on valve 1A-FWS-FV-0570 (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-06 | Shane Copeland
FWS-01 | FWS-01 | PI13093 | Verified | Install final trim and actuator on valve 1A-FWS-PV-0551 (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2019-12-06 | Shane Copeland | 2019-12-08 | Shane Copeland
FWS-01 | FWS-01 | PI13108 | Verified | Re-locate 1A-FWS-FIT-0072B below tap. | B | I | Gonzalo Pena | McD | 2019-11-16 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-01 | FWS-01 | PI13395 | Verified | Complete restoration after degreasing completed | B | P | James Beech | McD | 2019-11-23 | James Beech | Const |  |  | 2019-12-07 | Michael Law
FWS-01 | FWS-01 | PI07020 | Verified | Restore valve 1A-FWS-TV-8119 (AFTER degrease) | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-12-02 | Bobby Williams | 2019-12-06 | Shane Copeland
FWS-01 | FWS-01 | PI14674 | Verified | Pipe Support LK-1A-FWS-PD-HGR-0634; ISO LK-1A-FWS-PD-P40-0200-01; Missing Cotter Pin in Strut Pin. Field Craft is working on this Pipe Support, Cotter may be pulled for adjustment. | B | P | James Beech | McD | 2019-12-10 | James Beech | Const | 2019-12-21 | James Beech | 2020-01-01 | Ethan Byrd
FWS-01 | FWS-01 | PI14675 | Verified | Pipe Support LK-1A-FWS-PD-HGR-0528; ISO LK-1A-FWS-PD-P40-0200-03; Loose Jam Nut | B | P | James Beech | McD | 2019-12-10 | James Beech | Const | 2020-01-06 | James Beech | 2020-01-09 | Kelvin Cook
FWS-01 | FWS-01 | PI14676 | Verified | Pipe Support LK-1A-FWS-PD-HGR-0524; ISO LK-1A-FWS-PD-P40-0236-01; Pipe Clamp (Item 1) does not appear to be tight. | B | P | James Beech | McD | 2019-12-10 | James Beech | Const | 2019-12-21 | James Beech | 2020-01-01 | Ethan Byrd
FWS-01 | FWS-01 | PI14677 | Verified | Pipe Support LK-1A-FWS-PD-HGR-0606; ISO LK-1A-FWS-PD-P40-0236-02; Pipe Support is MISSING. 6" C.S. Bolt-On Pipe Shoe (no welding required), No Slide Plate Required, Insulation has not been installed. | B | P | James Beech | McD | 2019-12-10 | James Beech | Const | 2019-12-21 | James Beech | 2020-01-01 | Ethan Byrd
FWS-01 | FWS-01 | PI14678 | Verified | Pipe Support LK-1A-FWS-PD-HGR-0643; ISO LK-1A-FWS-PD-P40-0237-02; Pipe Support is MISSING. 6" C.S. Bolt-On Pipe Shoe (no welding required), No Slide Plate Required, Insulation has not been installed. | B | P | James Beech | McD | 2019-12-10 | James Beech | Const | 2019-12-21 | James Beech | 2020-01-01 | Ethan Byrd
FWS-01 | FWS-01 | PI14679 | Verified | Pipe Support LK-1A-FWS-PD-HGR-0586; ISO LK-1A-FWS-PD-P40-0150-01; No Gap Exist on West side Trunion End Plate. 1/4" Gap is shown on the Support Sketch. The Computer Stress Analysis reveals that 1/16" Gap to the West is Required. Therefore, use grinder (Matabo) or Portaband to trim item 4 on Welded Pipe Attachment, see Dwg LK_1A-FWS-PD-HGR-0986 to create 1/16 Min-1/4" Max Gap on West side. | B | P | James Beech | McD | 2019-12-10 | James Beech | Const | 2020-02-10 | Tim Green | 2020-02-11 | Kelvin Cook
FWS-01 | FWS-01 | PI14680 | Verified | Set all spring cans to cold setting. | B | P | Bobby Williams | McD | 2019-12-10 | Bobby Williams | Const |  |  | 2019-12-20 | Bobby Williams
FWS-01 | FWS-01 | PI14727 | Verified | 1A-MSS-PD-P40-0040-01: 1A-MSS-HGR-0009 located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-18 | James Beech | 2019-12-19 | Kelvin Cook
FWS-01 | FWS-01 | PI14817 | Verified | 1A-HTS-CAB-0303-NEED TO CLEAN BOX INSIDE AND OUT. | C | I | James Tanner | McD | 2019-12-15 | James Tanner | Const | 2019-12-30 | Gonzalo Pena | 2020-01-13 | Michael Law
FWS-01 | FWS-01 | PI14818 | Verified | 1A-HTS-CAB-0201-NEED TO CLEAN BOX INSIDE AND OUT. | B | I | James Tanner | McD | 2019-12-15 | James Tanner | Const | 2019-12-17 | Gonzalo Pena | 2019-12-18 | John Sullivan
FWS-01 | FWS-01 | PI15364 | Verified | Install vent line 1A-FWS-0263-996X4 | B | I | Gonzalo Pena | McD | 2020-01-07 | Gonzalo Pena | Const | 2020-01-31 | Gonzalo Pena | 2020-01-31 | James Tanner
FWS-01 | FWS-01 | PI15903 | Verified | 1A-FWS-P-0100A - The pressure seal is leaking on the Alpha Alpha BFP check valve | B | P | Shane Crowe | McD | 2020-01-13 | Shane Crowe | Comm | 2020-02-10 | Shane Crowe | 2020-02-10 | Shannon Scott
FWS-01 | FWS-01 | PI15904 | Verified | 1A-FWS-P-0100B - Seals are going bad on the feedwater pump. | C | M | William Mitchell | McD | 2020-01-13 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2020-04-07 | Randy Carpenter
FWS-01 | FWS-01 | PI16673 | Verified | 1B-FWS-P-0100B - 1BB BFP Motor Junction box is not aligned and bolted correctly. | B | M | Shane Crowe | McD | 2020-02-07 | Shane Crowe | Comm | 2020-02-10 | Shane Crowe | 2020-02-10 | Shannon Scott
FWS-01 | FWS-01 | PI16674 | Verified | 1A-FWS-M-0100A - The temperature element fitting is leaking oil on the inboard bearing of Alpha Alpha motor. | B | I | Albert Burge | McD | 2020-02-07 | Albert Burge | Comm | 2020-03-10 | Albert Burge | 2020-03-10 | John Watts
FWS-01 | FWS-01 | PI16687 | Verified | 1A-FWS-P-0100B - Loose ground | B | E | Chris Colvin | McD | 2020-02-10 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-04-06 | Bernard Stasse
FWS-01 | FWS-01 | PI16688 | Verified | 1A-FWS-M-0100A - The temperature element fitting is leaking oil on the inboard bearing of Alpha Alpha motor. | B | I | Albert Burge | McD | 2020-02-10 | Albert Burge | Comm | 2020-02-28 | Albert Burge | 2020-02-28 | John Watts
FWS-01 | FWS-01 | PI16690 | Verified | 1A-FWS-V-0215A&B & 1A-FWS-V-219A&B - The temperature element fitting is leaking oil on the inboard bearing of Alpha Alpha motor. | B | I | Albert Burge | McD | 2020-02-10 | Albert Burge | Comm | 2020-03-10 | Albert Burge | 2020-03-10 | John Watts
FWS-01 | FWS-01 | PI17302 | Verified | Valve missing handwheel at 1A-FWS-V-0207A1; 1A HRSG HP Feedwater Drain Valve | B | P | James Beech | McD | 2020-02-28 | James Beech | Comm | 2020-03-07 | Tim Green | 2020-03-31 | Bernard Stasse
FWS-01 | FWS-01 | PI17303 | Verified | 1A-FWS-PIT-0513; HRSG 1A BFP Suction Header Feedwater Pressure Transmitter needs support at 1A Feedwater Suction Strainer platform | C | I | James Beech | McD | 2020-02-28 | James Beech | Comm | 2020-03-20 | Tim Green | 2020-03-31 | Bernard Stasse
FWS-01 | FWS-01 | PI17304 | Verified | Complete heat trace at HRSG 1A Boiler Feed Pump B | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
FWS-01 | FWS-01 | PI17305 | Verified | Outboard seal leaking at HRSG 1A Boiler Feed Pump B | B | M | Shane Crowe | McD | 2020-02-28 | Shane Crowe | Comm | 2020-03-10 | Shane Crowe | 2020-03-26 | Bernard Stasse
FWS-01 | FWS-01 | PI17306 | Verified | Open condolet at NE corner of HRSG 1A Boiler Feed Pump B enclosure | C | E | Chris Colvin | McD | 2020-02-28 | Chris Colvin | Comm | 2020-08-20 | Chris Colvin | 2021-01-15 | Dave Goldak
FWS-01 | FWS-01 | PI17307 | Verified | Seal all penetration at HRSG 1A Boiler Feed Pump B enclosure | C | M | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Comm | 2020-05-15 | Tim Gallegos | 2020-11-11 | Dave Goldak
FWS-01 | FWS-01 | PI17308 | Verified | Tighten handwheel at 1A-FWS-V-0051A; 1A HRSG BFP Suction Strainer A Vent Valve | B | P | James Beech | McD | 2020-02-28 | James Beech | Comm | 2020-03-07 | Tim Green | 2020-03-31 | Bernard Stasse
FWS-01 | FWS-01 | PI17309 | Verified | Clean up HRSG 1A Boiler Feed Suction Strainer platform | C | C | Johnny Campbell | McD | 2020-02-28 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-08 | Bernard Stasse
FWS-01 | FWS-01 | PI17310 | Verified | Tighten handwheel at 1A-FWS-V-1158B; 1A HRSG BFP IP Discharge Isolation Valve, Line no. 3-1A-FWS-0155 | B | P | James Beech | McD | 2020-02-28 | James Beech | Comm | 2020-03-07 | Tim Green | 2020-03-31 | Bernard Stasse
FWS-01 | FWS-01 | PI17358 | Verified | 1A-FWS-TV-8119 is leaking around packing box. | B | P | William Mitchell | McD | 2020-02-28 | William Mitchell | Comm | 2020-03-17 | William Mitchell | 2020-06-09 | Love Kayode
FWS-01 | FWS-01 | PI18025 | Verified | 1A-FWS-FV-0570 - FAC (Flow Accelerated Corrosion) inspection of piping downstream of the TCA valve. Due to known issues at SC, it would be a good QA/QC to check the piping downstream of the TCA valves. | C | P | William Mitchell | McD | 2020-03-17 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2021-05-07 | John Watts
FWS-01 | FWS-01 | PI18093 | Verified | 1A-FWS-FV-0537 - SCPS experienced a piping failure in the elbow just downstream of 1A-FWS-FV-0537. | C | I | Michael Law | McD | 2020-03-18 | Michael Law | Comm | 2020-04-02 | Michael Law | 2020-04-16 | Keith Pollock
FWS-01 | FWS-01 | PI18115 | Verified | All probe locations on the FWS need to be relocated to the lower horizontal section of piping. The probes require monthly calibrations. | D | I | Charles Worthington | McD | 2020-03-20 | Charles Worthington | Comm | 2020-06-24 | Donovan Anderson | 2020-06-24 | Donovan Anderson
FWS-01 | FWS-01 | PI18150 | Verified | 1A-FWS-P-0100A and 1A-FWS-P-0100B - Possibly overpressuring on the suction side during cold fill due to seal issues. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2021-05-07 | John Watts
FWS-01 | FWS-01 | PI18178 | Verified | 1A-FWS-PV-0513 - This valve has a packing leak. | C | P | William Mitchell | McD | 2020-03-24 | William Mitchell | Comm | 2020-04-20 | William Mitchell | 2021-01-15 | Dave Goldak
FWS-01 | FWS-01 | PI18185 | Verified | 1A-FWS-PSV-0549 relieves and will not reseat. Need solution for valve suitble for service. | D | P | Charles Worthington | McD | 2020-03-26 | Charles Worthington | Comm | 2020-07-22 | Bryan Sturgies | 2021-07-08 | John Watts
FWS-01 | FWS-01 | PI18187 | Verified | 1A-FWS-PSV-0540 relieves and will not reseat. Need solution for valve suitble for service. | D | P | Charles Worthington | McD | 2020-03-26 | Charles Worthington | Comm | 2020-07-22 | Bryan Sturgies | 2021-07-08 | John Watts
FWS-01 | FWS-01 | PI18259 | Verified | Provide motor run testing paperwork for new motors | C | M | Alan Joiner | McD | 2020-04-30 | Alan Joiner | Comm | 2020-05-29 | Jonathan Donham | 2020-05-29 | Michael Law
FWS-01 | FWS-01 | PI18261 | Verified | Provider motor/pump alignment record paperwork for the new motors | C | M | Shane Crowe | McD | 2020-04-30 | Shane Crowe | Comm | 2020-05-19 | Shane Crowe | 2020-06-16 | Mike Tabbert
FWS-02 | FWS-02 | PI08204 | Verified | ISO 1B-FWS-PD-P40-0150-01 missing material. | A | P | Kelvin Cook | McD | 2019-10-01 | Kelvin Cook | Const |  |  | 2019-10-25 | Kelvin Cook
FWS-02 | FWS-02 | PI08205 | Verified | ISO 1B-FWS-PD-P40-0155-01 missing material. | A | P | Kelvin Cook | McD | 2019-10-01 | Kelvin Cook | Const |  |  | 2019-10-25 | Kelvin Cook
FWS-02 | FWS-02 | PI08736 | Verified | Complete feedwater pump enclosures. Scaffolding interference. | B | M | Shane Crowe | McD | 2019-10-04 | Shane Crowe | Const | 2020-01-31 | Shane Crowe | 2020-02-02 | Kelvin Cook
FWS-02 | FWS-02 | PI08737 | Verified | Set termination box for 1B-FWS-M-0100B. | A | M | Shane Crowe | McD | 2019-10-04 | Shane Crowe | Const | 2019-10-29 | Shane Crowe | 2019-10-29 | Joshua Sturgeon
FWS-02 | FWS-02 | PI08738 | Verified | Tag all components at the feedwater pumps. | C | M | Shane Crowe | McD | 2019-10-04 | Shane Crowe | Const | 2020-04-03 | Shane Crowe | 2020-04-07 | Michael Law
FWS-02 | FWS-02 | PI08739 | Verified | Complete grouting in the feedwater enclosures. | C | C | Shane Crowe | McD | 2019-10-04 | Shane Crowe | Const |  |  | 2019-11-22 | Joshua Sturgeon
FWS-02 | FWS-02 | PI08740 | Verified | Grout all pipe, instrument & electrical supports. | C | C | Johnny Campbell | McD | 2019-10-04 | Johnny Campbell | Const |  |  | 2019-12-06 | Jack Fields
FWS-02 | FWS-02 | PI08741 | Verified | Motor B term box missing conduit fitting plate. | A | M | Shane Crowe | McD | 2019-10-04 | Shane Crowe | Const | 2019-10-29 | Shane Crowe | 2019-12-13 | Mike Tabbert
FWS-02 | FWS-02 | PI08742 | Verified | Complete coupling after pipe stress on FW pump A. | B | M | Shane Crowe | McD | 2019-10-04 | Shane Crowe | Const | 2019-12-17 | Joshua Sturgeon | 2019-12-17 | Joshua Sturgeon
FWS-02 | FWS-02 | PI08743 | Verified | Complete coupling after pipe stress on FW pump B. | B | M | Shane Crowe | McD | 2019-10-04 | Shane Crowe | Const | 2019-12-17 | Shane Crowe | 2019-12-17 | Joshua Sturgeon
FWS-02 | FWS-02 | PI08744 | Verified | Install 1B-FWS-SRV-0075B at FW pump B. | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-12-16 | Bobby Williams | 2019-12-18 | Shane Copeland
FWS-02 | FWS-02 | PI08745 | Verified | Install 1B-FWS-V-0202B1 & B2 at FW pump B. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08746 | Verified | Complete support on pressure relief line at FW pump B. | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2020-01-21 | Michael Law
FWS-02 | FWS-02 | PI08747 | Verified | Complete FW pump B casing drain. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2020-01-21 | Michael Law
FWS-02 | FWS-02 | PI08748 | Verified | Complete FW lube oil containment skid drain. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-31 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08749 | Verified | Install sight glass on FW pump B. | A | M | Shane Crowe | McD | 2019-10-04 | Shane Crowe | Const | 2020-02-05 | Shane Crowe | 2020-02-27 | Michael Law
FWS-02 | FWS-02 | PI08750 | Verified | Install sight glass on FW pump A. | B | M | Shane Crowe | McD | 2019-10-04 | Shane Crowe | Const | 2020-02-05 | Shane Crowe | 2020-02-27 | Michael Law
FWS-02 | FWS-02 | PI08751 | Verified | Install in-line flow meters on FW pump B. | A | M | Shane Crowe | McD | 2019-10-04 | Shane Crowe | Const | 2020-01-20 | Shane Crowe | 2020-02-27 | Michael Law
FWS-02 | FWS-02 | PI08752 | Verified | Re-drill for u-bolts on the CCW line at the FW pump B discharge. | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-31 | Bobby Williams | 2020-01-21 | Michael Law
FWS-02 | FWS-02 | PI08753 | Verified | Complete FW pump A casing drain. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2020-01-21 | Michael Law
FWS-02 | FWS-02 | PI08754 | Verified | Valves 1B-FWS-V-0070A&B, 0055A&B & 0054A&B missing stem protectors. | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-11-22 | Bobby Williams | 2020-01-21 | Michael Law
FWS-02 | FWS-02 | PI08755 | Verified | Install 1B-FWS-FE-0072B. After FW Flush | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-12-17 | Bobby Williams | 2019-12-18 | Shane Copeland
FWS-02 | FWS-02 | PI08756 | Verified | Remove temporary supports on line 1B-FWS-0070. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-19 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08757 | Verified | Loose flange bolts on strainer 1B-FWS-STN-0050A. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-19 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08758 | Verified | Line 1B-FWS-0278 not installed (strainer vent). | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-12-09 | Bobby Williams | 2019-12-12 | Shane Copeland
FWS-02 | FWS-02 | PI08759 | Verified | Tag all valves. | C | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2020-02-18 | Bobby Williams | 2020-03-03 | Michael Law
FWS-02 | FWS-02 | PI08760 | Verified | Line 1B-FWS-0363 not installed (strainer vent). | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-12-09 | Bobby Williams | 2019-12-12 | Shane Copeland
FWS-02 | FWS-02 | PI08761 | Verified | Valve 1B-FWS-V-0054B missing handwheel. | A | P | Alex Isaac | McD | 2019-10-04 | Alex Isaac | Const | 2019-10-24 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08762 | Verified | Loose u-bolts on strainer 1B-FWS-STN-0050B drain line flange. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-19 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08763 | Verified | Missing support at strainer 1B-FWS-STN-0050B. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08764 | Verified | Set all spring cans to cold setting & pull gags after hydro. | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-12-23 | Michael Law | 2020-01-13 | Michael Law
FWS-02 | FWS-02 | PI08765 | Verified | Scaffold interference with valve 1B-FWS-V-0552. | A | C | Jerry Smith | McD | 2019-10-04 | Jerry Smith | Const | 2019-11-12 | Jerry Smith | 2020-01-13 | Michael Law
FWS-02 | FWS-02 | PI08766 | Verified | Complete bolting on 1B-FWS-SRV-0548. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-19 | Bobby Williams | 2019-12-19 | J.L. Bickham
FWS-02 | FWS-02 | PI08767 | Verified | Loose flange bolts on 1B-FWS-SRV-0049. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-19 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08768 | Verified | Complete drain line on 1B-FWS-SRV-0548 and remove temporary support. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-19 | Bobby Williams | 2019-12-19 | J.L. Bickham
FWS-02 | FWS-02 | PI08769 | Verified | Repair stem indicator on valves 1B-FWS-V-1158A & B. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-16 | Alex Isaac
FWS-02 | FWS-02 | PI08770 | Verified | Line 1B-FWS-0150 not installed (vent line). | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const |  |  | 2019-11-05 | Alex Isaac
FWS-02 | FWS-02 | PI08771 | Verified | Rotate operator south on valves 1B-FWS-0054B, 0055B & 0070B. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2020-01-21 | Michael Law
FWS-02 | FWS-02 | PI08772 | Verified | Support nuts loose at 1B-FWS-CHK-0206B. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-19 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08773 | Verified | Rotate operator north on valve 1B-FWS-V-0209B. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-11-11 | Bobby Williams | 2019-11-16 | Alex Isaac
FWS-02 | FWS-02 | PI08774 | Verified | Complete support on line 1B-FWS-0202 & remove temporary support. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08775 | Verified | Complete support on line 1B-FWS-0200 & remove temporary support. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08776 | Verified | Install chain operator on valve 1B-FWS-V-0220. | B | S | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const |  |  | 2020-02-07 | Kelvin Cook
FWS-02 | FWS-02 | PI08777 | Verified | Install 1B-FWS-FE-8002. After degrease. | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const |  |  | 2019-12-09 | Bobby Williams
FWS-02 | FWS-02 | PI08778 | Verified | Valve 1B-FWS-V-0554 missing handwheel and repair stem indicator. | A | P | Alex Isaac | McD | 2019-10-04 | Alex Isaac | Const | 2019-10-23 | Bobby Williams | 2019-11-16 | Alex Isaac
FWS-02 | FWS-02 | PI08779 | Verified | Install 1B-FWS-FE-0520. After degrease. | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const |  |  | 2019-12-09 | Bobby Williams
FWS-02 | FWS-02 | PI08780 | Verified | Complete support on line 1B-FWS-0505. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-24 | Bobby Williams | 2019-11-16 | Alex Isaac
FWS-02 | FWS-02 | PI08781 | Verified | Valve 1B-FWS-V-0521 missing handwheel. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-19 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08782 | Verified | Complete support on relief valve drian line 1B-FWS-SRV-0549. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2020-01-21 | Michael Law
FWS-02 | FWS-02 | PI08783 | Verified | 1B-FWS-SRV-0540 missing bolts at flange connection. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-19 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08784 | Verified | Valve 1B-FWS-V-0528B missing handwheel. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-19 | Bobby Williams | 2019-11-16 | Alex Isaac
FWS-02 | FWS-02 | PI08785 | Verified | 1B-FWS-AOV-0530 - loose nuts on support. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-19 | Bobby Williams | 2020-01-21 | Michael Law
FWS-02 | FWS-02 | PI08786 | Verified | Install 1B-FWS-FE-0250. After degrease. | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const |  |  | 2019-12-09 | Bobby Williams
FWS-02 | FWS-02 | PI08787 | Verified | Rotate operator 180 deg. on 1B-FWS-V-0271. Install handwheel. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2019-11-16 | Alex Isaac
FWS-02 | FWS-02 | PI08788 | Verified | Line 1B-FWS-0250 - support not in per design. Needs adjustment. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-29 | Bobby Williams | 2020-01-21 | Michael Law
FWS-02 | FWS-02 | PI08789 | Verified | Line 1B-FWS-0236 - complete supports. Under condenser, east side. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-31 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08790 | Verified | Complete welds (2) on line 1B-FWS-0541. Under condenser, east side. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-19 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08791 | Verified | Valve 1B-FWS-V-0536 missing handwheel. Under condenser, east side. | A | P | Alex Isaac | McD | 2019-10-04 | Alex Isaac | Const | 2019-10-23 | Bobby Williams | 2019-11-16 | Alex Isaac
FWS-02 | FWS-02 | PI08792 | Verified | Complete support for 1B-FWS-PD-HGR-0132 at FG heater A. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08793 | Verified | Missing bolts at FG heaters A flange connection. | A | P | Alex Isaac | McD | 2019-10-04 | Alex Isaac | Const | 2019-10-29 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08794 | Verified | Missing bolts at FG heaters B flange connection. | A | P | Alex Isaac | McD | 2019-10-04 | Alex Isaac | Const | 2019-10-29 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08795 | Verified | Support incomplete - 1B-FWS-0260 at FG heater A. Ground level & above heater. | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-23 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08796 | Verified | 1B-FWS-0260 - adjust support clamp up (piping interference). | A | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-31 | Bobby Williams | 2019-11-02 | Alex Isaac
FWS-02 | FWS-02 | PI08797 | Verified | Install 1B-FWS-FE-0565 at TCA. After degrease. | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const |  |  | 2019-12-09 | Bobby Williams
FWS-02 | FWS-02 | PI08798 | Verified | Remove temporary support on line 1B-FW-0542 at TCA. | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const | 2019-10-31 | Bobby Williams | 2020-01-21 | Michael Law
FWS-02 | FWS-02 | PI08803 | Verified | M-0100A need ground on the duct bank | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-13 | Brad Stanford | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08804 | Verified | M-0100A no ground on motor | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-13 | Brad Stanford | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08805 | Verified | M-0100A finish flextron | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-21 | Michael Law | 2020-01-28 | Fred Michael
FWS-02 | FWS-02 | PI08806 | Verified | M-0100A finish ground on flex | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-21 | Michael Law | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08807 | Verified | P-0100A and B to finish lighting on the enclosure | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
FWS-02 | FWS-02 | PI08808 | Verified | P-0100A and B to install exhaust fans | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
FWS-02 | FWS-02 | PI08809 | Verified | BA and BB BFW pump TI-1224 is broken | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-02 | FWS-02 | PI08810 | Verified | BA and BB BFW pump TI-0130 and 31 missing | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const |  |  | 2019-11-12 | Michael Law
FWS-02 | FWS-02 | PI08811 | Verified | BA BFW pump skid, ground flex on JB-1205A going to LO heater | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-13 | Brad Stanford | 2020-01-27 | Michael Law
FWS-02 | FWS-02 | PI08812 | Verified | BA BFW pump skid TB-0101A ground flex | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08813 | Verified | BA BFW pump skid TB-0101A ground the ground bar inside the TB | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08814 | Verified | BA BFW pump skid TB-0101A clean out panel | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-23 | Richard Cruz | 2020-01-13 | Fred Michael
FWS-02 | FWS-02 | PI08815 | Verified | BA BFW pump skid tame the ground going to skid | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08816 | Verified | TB-0101A and B factory conduit is under size and no bushings | C | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-24 | Michael Law | 2019-11-24 | Michael Law
FWS-02 | FWS-02 | PI08817 | Verified | M-0100A ground motor terminal box and raceway for power cables | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-13 | Brad Stanford | 2020-01-27 | Michael Law
FWS-02 | FWS-02 | PI08818 | Verified | M-0100A plug and seal holes motor box | B | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-13 | Brad Stanford | 2020-01-27 | Michael Law
FWS-02 | FWS-02 | PI08819 | Verified | M-0100A ground flex to TB-0100A4 from motor box | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-13 | Brad Stanford | 2019-12-13 | Fred Michael
FWS-02 | FWS-02 | PI08820 | Verified | M-0100A grounding jumper needed on motor terminal box | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-13 | Brad Stanford | 2020-01-13 | Fred Michael
FWS-02 | FWS-02 | PI08821 | Verified | BA and BB BFW pump skids install freeze protection heaters on the building | B | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
FWS-02 | FWS-02 | PI08822 | Verified | BA and BB BFW pump skids unistruts around the pump skids need cold gal | C | E | Jorge Alexander | McD | 2019-10-04 | Jorge Alexander | Const |  |  | 2019-12-17 | Fred Michael
FWS-02 | FWS-02 | PI08823 | Verified | BB BFW skid grounding on raceway, need bushing, and ground on UG stub-up to complete | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08824 | Verified | BB BFW skid finish raceway to RTD and vib boxes | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08825 | Verified | BB BFW ground motor and ground ductbank to vib boxes | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08826 | Verified | BB BFW probe missing tag no. 135B2ZF | C | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const |  |  | 2019-12-17 | Fred Michael
FWS-02 | FWS-02 | PI08827 | Verified | Replace crack motor terminal box | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-19 | Dustin Futrell | 2019-12-18 | Randy Carpenter
FWS-02 | FWS-02 | PI08828 | Verified | BA and BB BFW skids, properly support all motor terminal boxes | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08829 | Verified | BB BFW skid all indicators are not nstalled | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-11-21 | Albert Burge
FWS-02 | FWS-02 | PI08830 | Verified | BB BFW skid finishflex and reterminate wire 1205B, motor and oil heater | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08831 | Verified | ZSO-0054A, 55A, 70A, 54B, 70B are missing | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-19 | James Tanner | 2019-11-21 | Albert Burge
FWS-02 | FWS-02 | PI08832 | Verified | ZSO-0054A, 55A, 70A, 54B, 70B conduits not installed | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Albert Burge
FWS-02 | FWS-02 | PI08833 | Verified | FIT-8002, PIT-8001 no raceway | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08834 | Verified | PIT-0160, 0210A and B no raceway | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-13 | Brad Stanford | 2019-12-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08835 | Verified | AOV-0530 conduit not tight | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-13 | Brad Stanford | 2019-12-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08836 | Verified | HTS-CAB-0307, 0202, 0304, 0200 with FWS instruments to reposition cabinets and complete raceway | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-11 | Gonzalo Pena | 2019-12-13 | Mike Tabbert
FWS-02 | FWS-02 | PI08837 | Verified | HTS-CAB-0307, 0202, 0304, 0200 with FWS instruments to reposition cabinets and complete tubing | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-12-13 | Mike Tabbert
FWS-02 | FWS-02 | PI08838 | Verified | PV-0513 conduit too close to pipe and flex is too short | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-11-24 | Fred Michael
FWS-02 | FWS-02 | PI08839 | Verified | AOV-0265 rework conduit to make room for insulation, and it's covering up the tee | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI08840 | Verified | LSL-0262 add a conduit | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI08841 | Verified | FV-0269 install conduit | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI08842 | Verified | AOV-0263 install conduit for solenoid | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI08843 | Verified | AOV-0256 install conduit for solenoid | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI08844 | Verified | TE-0251 no conduit | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI08845 | Verified | FIT-0072A, PDIT-0050, PIT-0530 no conduit | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI08846 | Verified | FIT-0072A, PDIT-0050, PIT-0530 no tubing | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-11 | Gonzalo Pena | 2019-12-01 | Albert Burge
FWS-02 | FWS-02 | PI08847 | Verified | PIT-0210A/B not installed. | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-15 | James Tanner | 2019-12-01 | Albert Burge
FWS-02 | FWS-02 | PI08848 | Verified | TE-0261 no conduit | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI08849 | Verified | PIT-0575 flex too short | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-11-24 | Fred Michael
FWS-02 | FWS-02 | PI08850 | Verified | PIT-0535A1, B!, FIT-0565 conduit fitting is loose | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-11-24 | Fred Michael
FWS-02 | FWS-02 | PI08851 | Verified | TE-0550 nipple too short | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-12-01 | Albert Burge
FWS-02 | FWS-02 | PI08852 | Verified | PIT-0555 seal tight fitting is loose, and flex is too short | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-11-24 | Fred Michael
FWS-02 | FWS-02 | PI08853 | Verified | East side HRsG need stands grounted | C | E | Johnny Campbell | McD | 2019-10-04 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2019-12-14 | Mike Tabbert
FWS-02 | FWS-02 | PI08854 | Verified | East side HRsG need unistrut cold gal | C | E | Jorge Alexander | McD | 2019-10-04 | Jorge Alexander | Const |  |  | 2019-12-17 | Fred Michael
FWS-02 | FWS-02 | PI08855 | Verified | FV-0537 no conduit | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-12-05 | Mark Ball | 2020-01-01 | Albert Burge
FWS-02 | FWS-02 | PI08856 | Verified | FV-0537 no tubing | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const |  |  | 2019-12-13 | Fred Michael
FWS-02 | FWS-02 | PI08857 | Verified | FV-0235A/B no conduit | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI08858 | Verified | FV-0235A/B no tubing | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const |  |  | 2019-12-03 | James Tanner
FWS-02 | FWS-02 | PI08859 | Verified | MOV-8200 finish up conduit | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI08860 | Verified | LV-8002A/B need conduit | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI08861 | Verified | LV-8002A/B need tubing | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-11 | Gonzalo Pena | 2019-12-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08862 | Verified | MOV-8003 no conduit | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-24 | Fred Michael
FWS-02 | FWS-02 | PI08863 | Verified | FIT-8413 no conduit | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-24 | Fred Michael
FWS-02 | FWS-02 | PI08864 | Verified | FIT-8413 no tubing | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-15 | James Tanner | 2019-12-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08865 | Verified | AOV-8415 no conduit | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI08866 | Verified | 1B-FWS-TV-8418 no conduit | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-12-05 | Mark Ball | 2019-12-13 | Fred Michael
FWS-02 | FWS-02 | PI08867 | Verified | FIT-8116 no conduit | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI08868 | Verified | FIT-8116 no tubing | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-15 | James Tanner | 2019-12-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08869 | Verified | AOV-8118 no conduit | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-11-24 | Fred Michael
FWS-02 | FWS-02 | PI08870 | Verified | AOV-8118 no tubing | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-11 | Gonzalo Pena | 2019-12-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08871 | Verified | TV-8119 actuator not installed | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const |  |  | 2019-12-20 | Bobby Williams
FWS-02 | FWS-02 | PI08872 | Verified | TV-8119 not installed | B | P | Bobby Williams | McD | 2019-10-04 | Bobby Williams | Const |  |  | 2019-12-09 | Bobby Williams
FWS-02 | FWS-02 | PI08873 | Verified | TV-8119 no tubing | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-25 | Gonzalo Pena | 2019-12-13 | Mike Tabbert
FWS-02 | FWS-02 | PI08874 | Verified | PI-0074A not installed | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-19 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-02 | FWS-02 | PI08875 | Verified | PI-0152A not insttaled | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-19 | Gonzalo Pena | 2020-01-01 | Al Canniff
FWS-02 | FWS-02 | PI08876 | Verified | PI-0202A not installed | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const |  |  | 2020-01-01 | Albert Burge
FWS-02 | FWS-02 | PI08877 | Verified | PIT-PIT-0210A and B not installed | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const |  |  | 2019-11-14 | Ed Gober
FWS-02 | FWS-02 | PI08878 | Verified | PI-007B not installed | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-02 | FWS-02 | PI08879 | Verified | PI-0202B not installed | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-02 | FWS-02 | PI08880 | Verified | PI-0152B not insttaled | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-02 | FWS-02 | PI08881 | Verified | PI-0202B not installed | B | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-02 | FWS-02 | PI08882 | Verified | FIT-0250A and B not installed | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-19 | Albert Burge
FWS-02 | FWS-02 | PI08883 | Verified | TE-251 not installed | A | I | Gonzalo Pena | McD | 2019-10-04 | Gonzalo Pena | Const | 2019-11-11 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-02 | FWS-02 | PI08885 | Verified | 1BFWSC0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI08886 | Verified | 1BFWSC0003, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08887 | Verified | 1BFWSC0018, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08888 | Verified | 1BFWSC0022, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08889 | Verified | 1BFWSC0036, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08890 | Verified | 1BFWSH0002A1, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-12-14 | Mike Tabbert | 2019-12-14 | Mike Tabbert
FWS-02 | FWS-02 | PI08891 | Verified | 1BFWSH0002A2, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08892 | Verified | 1BFWSH0002B1, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI08893 | Verified | 1BFWSH0002B2, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08894 | Verified | 1BFWSH0002C1, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-12-18 | Mike Tabbert | 2019-12-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08895 | Verified | 1BFWSH0002C2, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08896 | Verified | 1BFWSH0002G1, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI08897 | Verified | 1BFWSH0002G2, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08898 | Verified | 1BFWSK0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08899 | Verified | 1BFWSK0002, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08900 | Verified | 1BFWSK0018, Pull Cable | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI08901 | Verified | 1BFWSK0019, Pull Cable | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI08902 | Verified | 1BFWSK0020, Pull Cable | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI08903 | Verified | 1BFWSK0021, Pull Cable | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI08904 | Verified | 1BFWSK0022, Pull Cable | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI08905 | Verified | 1BFWSK0024, Pull Cable | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-03 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI08906 | Verified | 1BFWSK0025, Pull Cable | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI08907 | Verified | 1BFWSK0026, Pull Cable | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI08908 | Verified | 1BFWSK0027, Pull Cable | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI08909 | Verified | 1BFWSK0028, Pull Cable | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-03 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI08910 | Verified | 1BFWSK0029, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08911 | Verified | 1BFWSK0030, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08912 | Verified | 1BFWSX0026, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08913 | Verified | 1BFWSX0030, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08914 | Verified | 1BFWSX0031, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08915 | Verified | 1BFWSX0032, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08916 | Verified | 1BFWSX0034, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08917 | Verified | 1BFWSX0035, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08918 | Verified | 1BFWSX0036, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08919 | Verified | 1BFWSX0065, Pull Cable | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI08920 | Verified | 1BFWSX0066, Pull Cable | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI08921 | Verified | 10DCSX0159, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08922 | Verified | 1BCTSC0275, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08923 | Verified | 1BCTSC0276, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08924 | Verified | 1BCTSC0277, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08925 | Verified | 1BCTSC0278, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08926 | Verified | 1BCTSC0279, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08927 | Verified | 1BCTSC0280, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08928 | Verified | 1BCTSC0281, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
FWS-02 | FWS-02 | PI08953 | Verified | 1BCTSX0436, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-23 | Fred Michael
FWS-02 | FWS-02 | PI08954 | Verified | 1BCTSX0438, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08955 | Verified | 1BCTSX0439, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI08956 | Verified | 1BFWSC0001, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08957 | Verified | 1BFWSC0003, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08958 | Verified | 1BFWSC0018, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08959 | Verified | 1BFWSC0022, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08960 | Verified | 1BFWSC0023, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI08961 | Verified | 1BFWSC0036, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08962 | Verified | 1BFWSH0002A1, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
FWS-02 | FWS-02 | PI08963 | Verified | 1BFWSH0002A2, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08964 | Verified | 1BFWSH0002B1, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
FWS-02 | FWS-02 | PI08965 | Verified | 1BFWSH0002B2, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08966 | Verified | 1BFWSH0002C1, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
FWS-02 | FWS-02 | PI08967 | Verified | 1BFWSH0002C2, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08968 | Verified | 1BFWSH0002G1, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
FWS-02 | FWS-02 | PI08969 | Verified | 1BFWSH0002G2, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08970 | Verified | 1BFWSK0001, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08971 | Verified | 1BFWSK0002, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08972 | Verified | 1BFWSK0004, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08973 | Verified | 1BFWSK0007, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-02 | FWS-02 | PI08974 | Verified | 1BFWSK0010, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08975 | Verified | 1BFWSK0014, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08976 | Verified | 1BFWSK0016, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-02 | FWS-02 | PI08977 | Verified | 1BFWSK0017, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08978 | Verified | 1BFWSK0018, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI08979 | Verified | 1BFWSK0019, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI08980 | Verified | 1BFWSK0020, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI08981 | Verified | 1BFWSK0021, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI08982 | Verified | 1BFWSK0022, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI08983 | Verified | 1BFWSK0023, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
FWS-02 | FWS-02 | PI08984 | Verified | 1BFWSK0024, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-03 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI08985 | Verified | 1BFWSK0025, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-03 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI08952 | Verified | 1BCTSX0435, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08951 | Verified | 1BCTSX0434, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08950 | Verified | 1BCTSX0433, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-24 | Dustin Futrell | 2019-11-24 | Fred Michael
FWS-02 | FWS-02 | PI08949 | Verified | 1BCTSX0432, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08948 | Verified | 1BCTSX0401, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
FWS-02 | FWS-02 | PI08947 | Verified | 1BCTSX0400, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-02 | FWS-02 | PI08946 | Verified | 1BCTSX0399, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-02 | FWS-02 | PI08945 | Verified | 1BCTSX0398, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08944 | Verified | 1BCTSX0397, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-12-06 | Mike Tabbert | 2019-12-13 | Mike Tabbert
FWS-02 | FWS-02 | PI08943 | Verified | 1BCTSX0396, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-02 | FWS-02 | PI08942 | Verified | 1BCTSX0394, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08941 | Verified | 1BCTSX0393, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08940 | Verified | 1BCTSX0392, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI08939 | Verified | 1BCTSX0390, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08938 | Verified | 1BCTSX0389, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08937 | Verified | 1BCTSX0388, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08936 | Verified | 1BCTSX0387, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08935 | Verified | 1BCTSX0386, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI08934 | Verified | 1BCTSX0385, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08933 | Verified | 1BCTSX0384, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-22 | Dustin Futrell | 2019-12-06 | Mike Tabbert
FWS-02 | FWS-02 | PI08932 | Verified | 1BCTSX0383, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08931 | Verified | 1BCTSC0284, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08930 | Verified | 1BCTSC0283, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08929 | Verified | 1BCTSC0282, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08986 | Verified | 1BFWSK0026, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-03 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI08987 | Verified | 1BFWSK0027, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-03 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI08988 | Verified | 1BFWSK0028, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-03 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI08989 | Verified | 1BFWSK0029, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
FWS-02 | FWS-02 | PI08990 | Verified | 1BFWSK0030, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-20 | Mike Tabbert
FWS-02 | FWS-02 | PI08991 | Verified | 1BFWSX0003, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08992 | Verified | 1BFWSX0014, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI08993 | Verified | 1BFWSX0016, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-22 | Dustin Futrell | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI08994 | Verified | 1BFWSX0018, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-20 | Mike Tabbert
FWS-02 | FWS-02 | PI08995 | Verified | 1BFWSX0024, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI08996 | Verified | 1BFWSX0025, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI08997 | Verified | 1BFWSX0026, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI08998 | Verified | 1BFWSX0030, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI08999 | Verified | 1BFWSX0031, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09000 | Verified | 1BFWSX0032, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09001 | Verified | 1BFWSX0034, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09002 | Verified | 1BFWSX0035, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09003 | Verified | 1BFWSX0036, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-06 | Mike Tabbert
FWS-02 | FWS-02 | PI09004 | Verified | 1BFWSX0047, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
FWS-02 | FWS-02 | PI09005 | Verified | 1BFWSX0048, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
FWS-02 | FWS-02 | PI09006 | Verified | 1BFWSX0049, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09007 | Verified | 1BFWSX0050, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09008 | Verified | 1BFWSX0051, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09009 | Verified | 1BFWSX0053, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
FWS-02 | FWS-02 | PI09010 | Verified | 1BFWSX0054, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-02 | FWS-02 | PI09011 | Verified | 1BFWSX0055, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
FWS-02 | FWS-02 | PI09012 | Verified | 1BFWSX0056, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09013 | Verified | 1BFWSX0057, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
FWS-02 | FWS-02 | PI09014 | Verified | 1BFWSX0058, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09015 | Verified | 1BFWSX0059, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09016 | Verified | 1BFWSX0061, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
FWS-02 | FWS-02 | PI09041 | Verified | 1BFWSC0011, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09042 | Verified | 1BFWSC0012, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI09043 | Verified | 1BFWSC0018, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09044 | Verified | 1BFWSC0019, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09045 | Verified | 1BFWSC0020, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09046 | Verified | 1BFWSC0022, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09047 | Verified | 1BFWSC0023, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09048 | Verified | 1BFWSC0024, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09049 | Verified | 1BFWSC0025, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09050 | Verified | 1BFWSC0029, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI09051 | Verified | 1BFWSC0030, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09052 | Verified | 1BFWSC0032, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI09053 | Verified | 1BFWSC0033, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09054 | Verified | 1BFWSC0034, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09055 | Verified | 1BFWSC0035, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09056 | Verified | 1BFWSC0036, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-24 | Fred Michael
FWS-02 | FWS-02 | PI09057 | Verified | 1BFWSC0039, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI09058 | Verified | 1BFWSH0002A1, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09059 | Verified | 1BFWSH0002A2, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09060 | Verified | 1BFWSH0002B1, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09061 | Verified | 1BFWSH0002B2, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09062 | Verified | 1BFWSH0002C1, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09063 | Verified | 1BFWSH0002C2, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09064 | Verified | 1BFWSH0002G1, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09065 | Verified | 1BFWSH0002G2, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09066 | Verified | 1BFWSK0001, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09067 | Verified | 1BFWSK0002, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09068 | Verified | 1BFWSK0003, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI09069 | Verified | 1BFWSK0004, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI09070 | Verified | 1BFWSK0010, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI09071 | Verified | 1BFWSK0013, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-22 | Mike Tabbert
FWS-02 | FWS-02 | PI09072 | Verified | 1BFWSK0014, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09073 | Verified | 1BFWSK0017, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09040 | Verified | 1BFWSC0010, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-21 | Mike Tabbert
FWS-02 | FWS-02 | PI09039 | Verified | 1BFWSC0009, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI09038 | Verified | 1BFWSC0008, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI09037 | Verified | 1BFWSC0007, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI09036 | Verified | 1BFWSC0003, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09035 | Verified | 1BFWSC0001, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09034 | Verified | 1BCTSX0439, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI09033 | Verified | 1BCTSX0438, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09032 | Verified | 1BCTSX0436, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-24 | Fred Michael
FWS-02 | FWS-02 | PI09031 | Verified | 1BCTSX0433, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI09030 | Verified | 1BCTSX0432, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09029 | Verified | 1BCTSX0401, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09028 | Verified | 1BCTSX0400, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-02 | FWS-02 | PI09027 | Verified | 1BCTSX0397, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
FWS-02 | FWS-02 | PI09026 | Verified | 1BCTSX0396, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-02 | FWS-02 | PI09025 | Verified | 1BCTSX0395, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-02 | FWS-02 | PI09024 | Verified | 1BCTSX0394, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09023 | Verified | 1BCTSX0393, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09022 | Verified | 1BCTSX0392, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09021 | Verified | 1BCTSX0391, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09020 | Verified | 10DCSX0159, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09019 | Verified | 1BFWSX0066, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-03 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI09018 | Verified | 1BFWSX0065, From Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI09017 | Verified | 1BFWSX0062, From Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-02 | FWS-02 | PI09074 | Verified | 1BFWSK0018, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-03 | Jared Stimpson | 2020-01-13 | Mike Tabbert
FWS-02 | FWS-02 | PI09075 | Verified | 1BFWSK0019, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI09076 | Verified | 1BFWSK0020, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI09077 | Verified | 1BFWSK0021, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI09078 | Verified | 1BFWSK0022, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-03 | Jared Stimpson | 2020-01-13 | Mike Tabbert
FWS-02 | FWS-02 | PI09079 | Verified | 1BFWSK0023, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-14 | Mike Tabbert
FWS-02 | FWS-02 | PI09080 | Verified | 1BFWSK0024, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
FWS-02 | FWS-02 | PI09081 | Verified | 1BFWSK0025, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-24 | Fred Michael
FWS-02 | FWS-02 | PI09082 | Verified | 1BFWSK0026, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI09083 | Verified | 1BFWSK0027, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-02 | Mike Tabbert
FWS-02 | FWS-02 | PI09084 | Verified | 1BFWSK0028, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2020-01-09 | Mike Tabbert
FWS-02 | FWS-02 | PI09085 | Verified | 1BFWSK0029, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI09086 | Verified | 1BFWSK0030, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
FWS-02 | FWS-02 | PI09087 | Verified | 1BFWSX0001, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09088 | Verified | 1BFWSX0002, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09089 | Verified | 1BFWSX0003, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09090 | Verified | 1BFWSX0004, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09091 | Verified | 1BFWSX0007, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09092 | Verified | 1BFWSX0010, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09093 | Verified | 1BFWSX0011, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09094 | Verified | 1BFWSX0012, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09095 | Verified | 1BFWSX0013, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09096 | Verified | 1BFWSX0014, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09097 | Verified | 1BFWSX0015, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09098 | Verified | 1BFWSX0016, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09099 | Verified | 1BFWSX0017, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-02 | FWS-02 | PI09100 | Verified | 1BFWSX0018, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-02 | FWS-02 | PI09101 | Verified | 1BFWSX0019, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2020-01-06 | Mike Tabbert
FWS-02 | FWS-02 | PI09102 | Verified | 1BFWSX0020, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-22 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09103 | Verified | 1BFWSX0023, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09104 | Verified | 1BFWSX0024, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09105 | Verified | 1BFWSX0025, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09106 | Verified | 1BFWSX0026, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09107 | Verified | 1BFWSX0030, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-02 | FWS-02 | PI09108 | Verified | 1BFWSX0031, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09109 | Verified | 1BFWSX0032, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-24 | Fred Michael
FWS-02 | FWS-02 | PI09110 | Verified | 1BFWSX0034, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-02 | FWS-02 | PI09111 | Verified | 1BFWSX0035, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-02 | FWS-02 | PI09112 | Verified | 1BFWSX0036, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
FWS-02 | FWS-02 | PI09113 | Verified | 1BFWSX0047, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-02 | FWS-02 | PI09114 | Verified | 1BFWSX0048, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-02 | FWS-02 | PI09115 | Verified | 1BFWSX0049, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09116 | Verified | 1BFWSX0050, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const |  |  | 2019-11-08 | Mike Tabbert
FWS-02 | FWS-02 | PI09117 | Verified | 1BFWSX0051, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09118 | Verified | 1BFWSX0052, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-02 | FWS-02 | PI09119 | Verified | 1BFWSX0054, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-02 | FWS-02 | PI09120 | Verified | 1BFWSX0055, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
FWS-02 | FWS-02 | PI09121 | Verified | 1BFWSX0056, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
FWS-02 | FWS-02 | PI09122 | Verified | 1BFWSX0057, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09123 | Verified | 1BFWSX0058, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
FWS-02 | FWS-02 | PI09124 | Verified | 1BFWSX0059, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09125 | Verified | 1BFWSX0060, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09126 | Verified | 1BFWSX0061, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-02 | FWS-02 | PI09127 | Verified | 1BFWSX0062, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-10-09 | Mike Tabbert
FWS-02 | FWS-02 | PI09128 | Verified | 1BFWSX0063, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-18 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09129 | Verified | 1BFWSX0064, To Termination | A | E | Dustin Futrell | McD | 2019-10-04 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
FWS-02 | FWS-02 | PI09130 | Verified | 1BFWSX0065, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-02 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI09131 | Verified | 1BFWSX0066, To Termination | A | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Const | 2020-01-03 | Jared Stimpson | 2020-01-03 | Mike Tabbert
FWS-02 | FWS-02 | PI09137 | Verified | Cable tray rack west of HRSG 1B PDC, need hold down clamps as tray turns south towards riser all levels. | B | E | Chris Colvin | McD | 2019-10-05 | Chris Colvin | Const | 2019-12-08 | Brad Stanford | 2019-12-13 | Mike Tabbert
FWS-02 | FWS-02 | PI09138 | Verified | Cable tray rack west of HRSG 1B PDC, Cable tray needs two hole clamps bolted to angle iron suports on cable tray waterfall all levels. | A | E | Dustin Futrell | McD | 2019-10-05 | Dustin Futrell | Const |  |  | 2019-11-27 | Fred Michael
FWS-02 | FWS-02 | PI09140 | Verified | Cable tray rack west of HRSG 1B PDC, from HRSG PDC to pipe rack cable tray grounding needs to be completed, tie each level of tray to ground and take to grid every 100 feet. | A | E | Dustin Futrell | McD | 2019-10-05 | Dustin Futrell | Const |  |  | 2019-11-24 | Fred Michael
FWS-02 | FWS-02 | PI09689 | Verified | Install 1B-FWS-TI-0130A and B, and 1B-FWS-TI-0131A and B | B | I | Gonzalo Pena | McD | 2019-10-16 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2020-01-01 | Albert Burge
FWS-02 | FWS-02 | PI09805 | Verified | Test Package FWS-T-14 in service test | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const | 2019-11-21 | Michael Law | 2019-11-27 | Kelvin Cook
FWS-02 | FWS-02 | PI09806 | Verified | Test Package FWS-T-08 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const | 2019-11-11 | James Beech | 2019-11-23 | Kelvin Cook
FWS-02 | FWS-02 | PI09807 | Verified | Test Package FWS-T-09 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const | 2019-11-11 | James Beech | 2019-11-23 | Kelvin Cook
FWS-02 | FWS-02 | PI09808 | Verified | Test Package FWS-T-10 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const | 2019-11-11 | James Beech | 2019-11-23 | Kelvin Cook
FWS-02 | FWS-02 | PI09809 | Verified | Test Package FWS-T-11 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const | 2019-11-11 | James Beech | 2019-11-23 | Kelvin Cook
FWS-02 | FWS-02 | PI09810 | Verified | Test Package FWS-T-12 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-19 | Kelvin Cook
FWS-02 | FWS-02 | PI09811 | Verified | Test Package FWS-T-14 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-25 | Kelvin Cook
FWS-02 | FWS-02 | PI12595 | Verified | Pump BB missing cooling water tie-in to pump casing. | A | M | Shane Crowe | McD | 2019-10-29 | Shane Crowe | Const | 2019-11-11 | Shane Crowe | 2019-11-11 | Joshua Sturgeon
FWS-02 | FWS-02 | PI12596 | Verified | Pump BB motor - oil tubing flow visor missing. | A | M | Shane Crowe | McD | 2019-10-29 | Shane Crowe | Const |  |  | 2019-11-26 | Michael Law
FWS-02 | FWS-02 | PI12628 | Verified | Feedwater pump BB motor termination box not complete. | A | E | Chris Colvin | McD | 2019-10-29 | Chris Colvin | Const | 2019-11-21 | Michael Law | 2020-01-13 | Fred Michael
FWS-02 | FWS-02 | PI12708 | Verified | BFP lube oil skid, temp. transmitter 1B-FWS-TT-1200A- signal wire is in the same conduit as the 120 vac control cable. Transmitter wire should be in a different conduit. | A | E | Dustin Futrell | McD | 2019-11-02 | Dustin Futrell | Const |  |  | 2019-11-23 | Fred Michael
FWS-02 | FWS-02 | PI12710 | Verified | BFP lube oil skid, temp. transmitter 1B-FWS-TT-1200B- signal wire is in the same conduit as the 120 vac control cable. Transmitter wire should be in a different conduit. | A | E | Dustin Futrell | McD | 2019-11-02 | Dustin Futrell | Const |  |  | 2019-11-23 | Fred Michael
FWS-02 | FWS-02 | PI12749 | Verified | Handwheel not installed on valve 1B-FWS-V-0055B | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-21 | Michael Law | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12750 | Verified | Handwheel not installed on valve 1B-FWS-V-0070B | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-21 | Michael Law | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12751 | Verified | Install 1B-FWS-FE-0072B (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-12-16 | Bobby Williams | 2019-12-18 | Shane Copeland
FWS-02 | FWS-02 | PI12752 | Verified | Rotate handwheel 180° on valve 1B-FWS-V-0209A | B | P | William Mitchell | McD | 2019-11-05 | William Mitchell | Const | 2019-11-22 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12753 | Verified | Support 1B-FWS-PD-HGR-0558 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12754 | Verified | Install 1B-FWS-FE-8002 (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const |  |  | 2019-12-09 | Bobby Williams
FWS-02 | FWS-02 | PI12755 | Verified | Support 1B-FWS-PD-HGR-0001 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12756 | Verified | Loose bolts at flange connection to 1B-FWS-SRV-0548 | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-21 | Michael Law | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12757 | Verified | Remove rigging at support 1B-FWS-PD-HGR-0791 | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12758 | Verified | Support 1B-FWS-PD-HGR-0748 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-26 | Joseph Lamb | 2019-11-27 | Alex Isaac
FWS-02 | FWS-02 | PI12759 | Verified | Support 1B-FWS-PD-HGR-0527 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-26 | Joseph Lamb | 2019-11-27 | Alex Isaac
FWS-02 | FWS-02 | PI12760 | Verified | Support 1B-FWS-PD-HGR-0767 not on location | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12761 | Verified | Support 1B-FWS-PD-HGR-0836 not set per detail | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12762 | Verified | Support 1B-FWS-PD-HGR-0270 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12763 | Verified | Support 1B-FWS-PD-HGR-0271 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12764 | Verified | Support 1B-FWS-PD-HGR-0274 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-21 | Michael Law | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12765 | Verified | Install 1B-FWS-FE-0250 (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const |  |  | 2019-12-09 | Bobby Williams
FWS-02 | FWS-02 | PI12766 | Verified | Support 1B-FWS-PD-HGR-0279 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12767 | Verified | Support 1B-FWS-PD-HGR-0280 not installed (loose nuts on strut) | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-12-17 | Bobby Williams | 2019-12-18 | Shane Copeland
FWS-02 | FWS-02 | PI12768 | Verified | Support 1B-FWS-PD-HGR-0284 not installed (not complete) | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-12-17 | Bobby Williams | 2019-12-18 | Shane Copeland
FWS-02 | FWS-02 | PI12769 | Verified | Install 1B-FWS-FE-0520 (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-12-17 | Bobby Williams | 2019-12-17 | Shane Crowe
FWS-02 | FWS-02 | PI12770 | Verified | Install stem indicator on valve 1B-FWS-V-0524 (TAPED TO VALVE) | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-21 | Michael Law | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12771 | Verified | Install 1B-FWS-FE-0565 (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const |  |  | 2019-12-16 | Bobby Williams
FWS-02 | FWS-02 | PI12772 | Verified | Loose nuts on support 1B-FWS-PD-HGR-0067 | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12773 | Verified | Support 1B-FWS-PD-HGR-0074 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12774 | Verified | Support 1B-FWS-PD-HGR-0075 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12775 | Verified | Support 1B-FWS-PD-HGR-0076 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12776 | Verified | Support 1B-FWS-PD-HGR-0071 not complete | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12777 | Verified | Support 1B-FWS-PD-HGR-0073 not complete | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12778 | Verified | Support 1B-FWS-PD-HGR-0147 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12779 | Verified | Support 1B-FWS-PD-HGR-0106 not complete | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-24 | Alex Isaac
FWS-02 | FWS-02 | PI12780 | Verified | Remove temporary support (DUNNAGE) from support 1B-FWS-PD-HGR-0115 | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-23 | Alex Isaac
FWS-02 | FWS-02 | PI12781 | Verified | Support 1B-FWS-PD-HGR-0145 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-24 | Alex Isaac
FWS-02 | FWS-02 | PI12782 | Verified | Support 1B-FWS-PD-HGR-0200 not complete | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-21 | Michael Law | 2019-11-24 | Alex Isaac
FWS-02 | FWS-02 | PI12783 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-12-17 | Bobby Williams | 2019-12-19 | Shane Copeland
FWS-02 | FWS-02 | PI12784 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-12-17 | Bobby Williams | 2019-12-19 | Shane Copeland
FWS-02 | FWS-02 | PI12785 | Verified | Cap not installed at low point | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-22 | Bobby Williams | 2019-11-24 | Alex Isaac
FWS-02 | FWS-02 | PI12786 | Verified | Cap not installed at low point | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-22 | Bobby Williams | 2019-11-24 | Alex Isaac
FWS-02 | FWS-02 | PI12787 | Verified | Cap not installed at low point | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-22 | Bobby Williams | 2019-11-24 | Alex Isaac
FWS-02 | FWS-02 | PI12788 | Verified | TAG ALL VALVES | C | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const |  |  | 2020-01-10 | Michael Law
FWS-02 | FWS-02 | PI12789 | Verified | Support 1B-FWS-PD-HGR-0375 not installed | A | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-13 | Bobby Williams | 2019-11-24 | Alex Isaac
FWS-02 | FWS-02 | PI12790 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const |  |  | 2019-12-16 | Bobby Williams
FWS-02 | FWS-02 | PI12791 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const |  |  | 2019-12-16 | Bobby Williams
FWS-02 | FWS-02 | PI12792 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const |  |  | 2019-12-16 | Bobby Williams
FWS-02 | FWS-02 | PI12793 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const |  |  | 2019-12-16 | Bobby Williams
FWS-02 | FWS-02 | PI12794 | Verified | Cap not installed at high point | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-11-22 | Bobby Williams | 2019-11-24 | Alex Isaac
FWS-02 | FWS-02 | PI12795 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const |  |  | 2019-12-16 | Bobby Williams
FWS-02 | FWS-02 | PI12796 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const |  |  | 2019-12-16 | Bobby Williams
FWS-02 | FWS-02 | PI12797 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-12-16 | Bobby Williams | 2019-12-19 | Shane Copeland
FWS-02 | FWS-02 | PI12798 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-12-16 | Bobby Williams | 2019-12-19 | Shane Copeland
FWS-02 | FWS-02 | PI12799 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-12-16 | Bobby Williams | 2019-12-19 | Shane Copeland
FWS-02 | FWS-02 | PI12800 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-12-16 | Bobby Williams | 2019-12-19 | Shane Copeland
FWS-02 | FWS-02 | PI12801 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-12-16 | Bobby Williams | 2019-12-19 | Shane Copeland
FWS-02 | FWS-02 | PI12802 | Verified | Line not installed (AFTER DEGREASE) | B | P | Bobby Williams | McD | 2019-11-05 | Bobby Williams | Const | 2019-12-16 | Bobby Williams | 2019-12-19 | Shane Copeland
FWS-02 | FWS-02 | PI13069 | Verified | Remove start-up trim and install final trim on valve 1B-FWS-PV-0513 (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2019-12-09 | James Beech | 2019-12-09 | James Beech
FWS-02 | FWS-02 | PI13094 | Verified | Install final trim and actuator on valve 1B-FWS-FV-0235A (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2019-12-09 | James Beech | 2019-12-09 | James Beech
FWS-02 | FWS-02 | PI13095 | Verified | Install final trim and actuator on valve 1B-FWS-FV-0235B (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const |  |  | 2019-12-09 | Shane Copeland
FWS-02 | FWS-02 | PI13096 | Verified | Install final trim and actuator on valve 1B-FWS-FV-0269 (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const |  |  | 2019-12-09 | Albert Burge
FWS-02 | FWS-02 | PI13097 | Verified | Install final trim and actuator on valve 1B-FWS-FV-0537 (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const |  |  | 2019-12-09 | Shane Copeland
FWS-02 | FWS-02 | PI13098 | Verified | Install final trim and actuator on valve 1B-FWS-FV-0570 (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const |  |  | 2019-12-09 | Shane Copeland
FWS-02 | FWS-02 | PI13099 | Verified | Install final trim and actuator on valve 1B-FWS-PV-0551 (AFTER degrease) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const |  |  | 2019-12-09 | Shane Copeland
FWS-02 | FWS-02 | PI13109 | Verified | Re-locate 1B-FWS-FIT-0072B below tap. | B | I | Gonzalo Pena | McD | 2019-11-16 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2019-12-13 | Albert Burge
FWS-02 | FWS-02 | PI13179 | Verified | Install 1B-FWS-FIT-0250A. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-23 | Michael Law
FWS-02 | FWS-02 | PI13180 | Verified | Install 1B-FWS-FIT-0250B. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-23 | Michael Law
FWS-02 | FWS-02 | PI13181 | Verified | Install 1B-FWS-FIT-0520A. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-23 | Michael Law
FWS-02 | FWS-02 | PI13182 | Verified | Install 1B-FWS-FIT-0520B. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-23 | Michael Law
FWS-02 | FWS-02 | PI13183 | Verified | Install 1B-FWS-FIT-0520C. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-23 | Michael Law
FWS-02 | FWS-02 | PI13184 | Verified | Install 1B-FWS-FIT-0565. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-23 | Michael Law
FWS-02 | FWS-02 | PI13185 | Verified | Install 1B-FWS-PIT-0260. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-23 | Michael Law
FWS-02 | FWS-02 | PI13186 | Verified | Install 1B-FWS-FV-0269. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-12-03 | James Tanner | 2019-12-12 | James Tanner
FWS-02 | FWS-02 | PI13187 | Verified | Install 1B-FWS-FV-0537. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-12-03 | James Tanner | 2019-12-12 | James Tanner
FWS-02 | FWS-02 | PI13188 | Verified | Install 1B-FWS-FV-0570. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2019-12-03 | James Tanner | 2019-12-12 | James Tanner
FWS-02 | FWS-02 | PI13396 | Verified | Complete restoration after degreasing completed | B | P | James Beech | McD | 2019-11-23 | James Beech | Const |  |  | 2019-12-07 | Michael Law
FWS-02 | FWS-02 | PI13397 | Verified | Support 1b-fws-pd-hgr-0279 not touching steel (restore after degrease) | A | P | Bobby Williams | McD | 2019-11-23 | Bobby Williams | Comm | 2019-12-20 | Bobby Williams | 2020-01-08 | Ethan Byrd
FWS-02 | FWS-02 | PI08166 | Verified | Restore valve 1B-FWS-TV-8119 (AFTER Chemical Clean) | A | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-12-05 | Bobby Williams | 2019-12-08 | Shane Copeland
FWS-02 | FWS-02 | PI13966 | Verified | Restore internals 1B-FWS-CHK-0156A. | B | P | Shane Copeland | McD | 2019-12-05 | Shane Copeland | Const | 2019-12-23 | Michael Law | 2020-01-01 | Kelvin Cook
FWS-02 | FWS-02 | PI13967 | Verified | Restore internals 1B-FWS-CHK-0156B. | B | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-21 | James Beech | 2020-01-01 | Kelvin Cook
FWS-02 | FWS-02 | PI13968 | Verified | Restore internals 1B-FWS-CHK-0206A. | B | P | James Beech | McD | 2019-12-05 | James Beech | Const |  |  | 2019-12-09 | Shane Copeland
FWS-02 | FWS-02 | PI13969 | Verified | Restore internals 1B-FWS-CHK-0206B. | B | P | James Beech | McD | 2019-12-05 | James Beech | Const |  |  | 2019-12-09 | Shane Copeland
FWS-02 | FWS-02 | PI13353 | Verified | 1BFWSX0033, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
FWS-02 | FWS-02 | PI14848 | Verified | Install new graphite gasket on valve 1B-FWS-CHK-206A Isometric 1B-FWS-PD-P40-0200-02 | A | P | James Beech | McD | 2019-12-18 | James Beech |  | 2019-12-19 | James Beech | 2019-12-20 | Shane Copeland
FWS-02 | FWS-02 | PI16044 | Verified | Pipe Support 1B-FWS-PD-HGR-0527 (Ref Iso LK-1B-FWS-PD-P40-0237-01) is installed approximately 3 ft. East of the Design Location. This minor relocation of the Spring Support is deemed acceptable by Engineering Judgement for Pipe Stress and Pipe Support Design . G.Pickeral 1-14-2020 | C | P | James Beech | McD | 2020-01-15 | James Beech | Comm |  |  | 2020-01-15 | Gary Pickeral
FWS-02 | FWS-02 | PI16045 | Verified | Pipe Support 1B-FWS-PD-HGR-0709 (Ref Iso LK-1B-FWS-PD-P40-0010-01) is missing the "Guide Clips" (Item 2 of sketch). | B | P | James Beech | McD | 2020-01-15 | James Beech | Comm | 2020-02-10 | Tim Green | 2020-02-11 | Kelvin Cook
FWS-02 | FWS-02 | PI16046 | Verified | Pipe Support 1B-FWS-PD-HGR-0703 (Ref Iso LK-1B-FWS_PD-P40-0070-02) is missing the "Load Platter" (on Item 1 of sketch). | C | P | James Beech | McD | 2020-01-15 | James Beech | Comm |  |  | 2020-02-12 | Kelvin Cook
FWS-02 | FWS-02 | PI16047 | Verified | Pipe Support 1B-FWS-PD-HGR-0704 (Ref Iso LK-1B-FWS_PD-P40-0070-02) is missing the "Load Platter" (on Item 1 of sketch). | C | P | James Beech | McD | 2020-01-15 | James Beech | Comm |  |  | 2020-02-12 | Kelvin Cook
FWS-02 | FWS-02 | PI16048 | Verified | Pipe Support 1B-FWS-PD-HGR-0705 (Ref Iso LK-1B-FWS_PD-P40-0070-02) is missing the "Load Platter" (on Item 1 of sketch). | C | P | James Beech | McD | 2020-01-15 | James Beech | Comm |  |  | 2020-02-12 | Kelvin Cook
FWS-02 | FWS-02 | PI16049 | Verified | Pipe Support 1B-FWS-PD-HGR-0706 (Ref Iso LK-1B-FWS-PD-P40-0070-04) is missing a Jam Nut. | B | P | James Beech | McD | 2020-01-15 | James Beech | Comm | 2020-02-10 | Tim Green | 2020-02-11 | Kelvin Cook
FWS-02 | FWS-02 | PI16050 | Verified | Pipe Support 1B-FWS-PD-HGR-0776 (Ref Iso LK-1B-FWS-PD-P40-0505-05) is missing the Guide Clips (Item 1 on Support Sketch). | B | P | James Beech | McD | 2020-01-15 | James Beech | Comm | 2020-02-10 | Tim Green | 2020-02-11 | Kelvin Cook
FWS-02 | FWS-02 | PI16051 | Verified | Pipe Support 1B-FWS-PD-HGR-0778 (Ref Iso LK-1B-FWS-PD-P40-0505-05) is missing the Axial Stops (Item 1 on Support Sketch). | B | P | James Beech | McD | 2020-01-15 | James Beech | Comm | 2020-02-10 | Tim Green | 2020-02-11 | Kelvin Cook
FWS-02 | FWS-02 | PI16052 | Verified | Pipe Support 1B-FWS-PD-HGR-0780 (Ref Iso LK-1B-FWS-PD-P40-0505-05) is missing the Guide Clips (Item 1 on Support Sketch). | B | P | James Beech | McD | 2020-01-15 | James Beech | Comm | 2020-02-10 | Tim Green | 2020-02-11 | Kelvin Cook
FWS-02 | FWS-02 | PI16053 | Verified | There are several Safety Relief Valves (SRV) scattered throughout the FWS system. Many of them are "Gagged" via a large plastic Wire Tie; these must be removed prior to full pressurization and commercial operation of the system. This note applies to all SRV's throughout the plant. | A | P | James Beech | McD | 2020-01-15 | James Beech | Comm | 2020-02-07 | Bobby Williams | 2020-02-12 | Kelvin Cook
FWS-02 | FWS-02 | PI16689 | Verified | 1B-FWS-PIT-0523 - The cabinet is full of moisture due to water leaking out of the pressure transmitter sensing line. | B | I | Gonzalo Pena | McD | 2020-02-10 | Gonzalo Pena | Comm | 2020-03-04 | Tim Green | 2020-04-06 | Bernard Stasse
FWS-02 | FWS-02 | PI16691 | Verified | 1B-FWS-PIT-0523 - The cabinet is full of moisture due to water leaking out of the pressure transmitter sensing line. | B | I | Gonzalo Pena | McD | 2020-02-10 | Gonzalo Pena | Comm | 2020-03-04 | Tim Green | 2020-04-06 | Bernard Stasse
FWS-02 | FWS-02 | PI17277 | Verified | 1B-FWS-FIT-0072B; HRSG 1B Feedwater Pump B Suction Flow Transmitter was relocated, remove wiring and flex conduit from old location at 1B Feedwater Pump suction, 1B Feedwater Suction Strainer platform | C | E | Chris Colvin | McD | 2020-02-28 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2021-01-05 | Keith Pollock
FWS-02 | FWS-02 | PI17278 | Verified | 1B-FWS-PIT-0523; HRSG 1B TCAC Inlet Header Pressure Tansmitter was relocated, remove wiring and flex conduit from old location at 1B Feedwater Pump discharge, 1B Feedwater Suction Strainer platform | C | E | Chris Colvin | McD | 2020-02-28 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2021-01-05 | Keith Pollock
FWS-02 | FWS-02 | PI17279 | Verified | Clean up HRSG 1B Feedwater Suction Strainer platform | C | C | Johnny Campbell | McD | 2020-02-28 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-08 | Bernard Stasse
FWS-02 | FWS-02 | PI17280 | Verified | Rod hanger clamp disconnected on 1" Vent Line No. 1-1A-FWS-0282, vent off 6" return from 1A and 1B Fuel Gas Heater, 1B HRSG Feedwater Suction Strainer platform | B | P | James Beech | McD | 2020-02-28 | James Beech | Comm | 2020-03-09 | Tim Green | 2020-03-31 | Bernard Stasse
FWS-02 | FWS-02 | PI17281 | Verified | 1B-FWS-TE-0525; 1B TCAC Pumps Feedwater Discharge Header Temp Element connection is loose | C | I | Albert Burge | McD | 2020-02-28 | Albert Burge | Comm | 2020-04-01 | Albert Burge | 2020-04-01 | Randy Carpenter
FWS-02 | FWS-02 | PI17282 | Verified | Condolet cover to soldenoid open at 1B-FWS-AOV-0530; 1B TCAC Pumps Feedwater Discharge Header Air Operated Valve | C | E | Chris Colvin | McD | 2020-02-28 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2021-01-15 | Dave Goldak
FWS-02 | FWS-02 | PI17283 | Verified | Condolet cover to soldenoid open at 1B-FWS-AOV-0525; 1B Feedwater 1B Fuel Gas Heater A & B Supply Air Operated Valve | C | E | Chris Colvin | McD | 2020-02-28 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2021-03-03 | John Watts
FWS-02 | FWS-02 | PI17284 | Verified | Complete insulation throughout system | C | Q | Sheri Fritz | PCI | 2020-02-28 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
FWS-02 | FWS-02 | PI17285 | Verified | Clean up inside 1B Feedwater Pump B enclosure | C | C | Alan Huntsman | McD | 2020-02-28 | Alan Huntsman | Comm | 2020-03-18 | Johnny Campbell | 2020-03-26 | Bernard Stasse
FWS-02 | FWS-02 | PI17287 | Verified | Seal all penetrations at 1B Feedwater Pump B enclosure | C | M | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Comm | 2020-05-15 | Tim Gallegos | 2020-11-11 | Dave Goldak
FWS-02 | FWS-02 | PI17288 | Verified | Temperature Indicator is loose at 1B Feedwater Pump B Lube Oil Cooler - 3/27 on order waiting for parts AB | C | I | Mike Tabbert | McD | 2020-02-28 | Mike Tabbert | Comm | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
FWS-02 | FWS-02 | PI17289 | Verified | Tags missing from Pressure Indicator rack at North side of 1B Feedwater Pump B | C | P | Tim Green | McD | 2020-02-28 | Tim Green | Comm | 2020-06-01 | Tim Green | 2021-01-05 | Keith Pollock
FWS-02 | FWS-02 | PI17290 | Verified | Empty conduit at East side of 1B Feedwater Pump B | C | E | Chris Colvin | McD | 2020-02-28 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2021-01-05 | Keith Pollock
FWS-02 | FWS-02 | PI17291 | Verified | Conduit strap missing at NE corner of 1B Feedwater Pump B enclosure | C | E | Chris Colvin | McD | 2020-02-28 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2021-01-05 | Keith Pollock
FWS-02 | FWS-02 | PI17292 | Verified | Plug hole through wall at NE corner of 1B Feedwater Pump B enclosure | C | M | Tim Gallegos | McD | 2020-02-28 | Tim Gallegos | Comm | 2020-06-02 | Tim Gallegos | 2020-11-11 | Dave Goldak
FWS-02 | FWS-02 | PI17293 | Verified | Pressure Indicator broken on IA Regulator at 1B-FWS-PV-0551; 1B TCAC Pumps Feedwater Discharge Header Pressure Control Valve | B | I | James Beech | McD | 2020-02-28 | James Beech | Comm | 2020-03-09 | Tim Green | 2021-01-05 | Keith Pollock
FWS-02 | FWS-02 | PI17294 | Verified | Flex ground disconnected on lighting conduit at NE corner of 1B Feedwater Pump B enclosure | C | E | Chris Colvin | McD | 2020-02-28 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2021-01-15 | Dave Goldak
FWS-02 | FWS-02 | PI17295 | Verified | Tube bundle needs support above 1B-HTS-CAB-0204, 1B Feedwater Pump Suction Strainer platform | C | I | James Beech | McD | 2020-02-28 | James Beech | Comm | 2020-03-27 | James Beech | 2021-01-05 | Keith Pollock
FWS-02 | FWS-02 | PI17296 | Verified | Heat shrink tube bundle boots at 1B-HTS-CAB-0204, 1B Feedwater Pump Suction Strainer platform | C | I | James Beech | McD | 2020-02-28 | James Beech | Comm | 2020-03-27 | James Beech | 2021-01-05 | Keith Pollock
FWS-02 | FWS-02 | PI17690 | Verified | 1B BFWP motor Top Hat, internal panels have fallen near the outlet louvers on both ends. | C | M | Shane Crowe | McD | 2020-03-04 | Shane Crowe | Comm | 2020-03-27 | Shane Crowe | 2021-04-21 | John Watts
FWS-02 | FWS-02 | PI18067 | Verified | 1B-FWS-AOV-8118 - This valve needs more support. Also, the cross sectional support above this valve only had 1 bolt per mounting hole (there should be 2), and the middle section that ties the cross sections together is also missing a bolt. | C | P | Tim Green | McD | 2020-03-18 | Tim Green | Comm | 2020-06-04 | Tim Green | 2021-01-15 | Dave Goldak
FWS-02 | FWS-02 | PI18094 | Verified | 1B-FWS-FV-0537 - SCPS experienced a piping failure in the elbow just downstream of 1B-FWS-FV-0537. | C | I | Michael Law | McD | 2020-03-18 | Michael Law | Comm | 2020-04-02 | Michael Law | 2020-04-16 | Keith Pollock
FWS-02 | FWS-02 | PI18116 | Verified | All probe locations on the FWS need to be relocated to the lower horizontal section of piping. The probes require monthly calibrations. | D | I | Charles Worthington | McD | 2020-03-20 | Charles Worthington | Comm | 2020-09-15 | Jason Ezell | 2021-01-05 | Keith Pollock
FWS-02 | FWS-02 | PI18151 | Verified | 1B-FWS-P-0100A and 1B-FWS-P-0100B - Possibly overpressuring on the suction side during cold fill due to seal issues. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2021-04-21 | John Watts
FWS-02 | FWS-02 | PI18179 | Verified | 1B-FWS-CHK-0272 - 1B-FWS-CHK-0272 is leaking at the top flange of the check valve. | C | P | William Mitchell | McD | 2020-03-24 | William Mitchell | Comm | 2020-04-20 | William Mitchell | 2021-01-05 | Keith Pollock
FWS-02 | FWS-02 | PI18186 | Verified | 1B-FWS-PSV-0549 relieves and will not reseat. Need solution for valve suitble for service - Transferred to Warranty List 15-Jul | C | P | Charles Worthington | McD | 2020-03-26 | Charles Worthington | Comm | 2020-07-16 | Jason Ezell | 2020-07-16 | Jason Ezell
FWS-02 | FWS-02 | PI18188 | Verified | 1B-FWS-PSV-0540 relieves and will not reseat. Need solution for valve suitble for service. - Transferred to Warranty List 15-Jul | C | P | Charles Worthington | McD | 2020-03-26 | Charles Worthington | Comm | 2020-07-16 | Jason Ezell | 2020-07-16 | Jason Ezell
FWS-02 | FWS-02 | PI18260 | Verified | Provide motor run testing paperwork for new motors | C | M | Alan Joiner | McD | 2020-04-30 | Alan Joiner | Comm | 2020-05-29 | Jonathan Donham | 2020-05-29 | Michael Law
FWS-02 | FWS-02 | PI18262 | Verified | Provider motor/pump alignment record paperwork for the new motors | C | M | Shane Crowe | McD | 2020-04-30 | Shane Crowe | Comm | 2020-05-19 | Shane Crowe | 2020-06-16 | Mike Tabbert
GCH-01 | GCH-01 | PI02465 | Verified | LK-10-GCH-P41-0100-02 Need welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-26 | Tom Noble | 2019-07-26 | Tom Noble
GCH-01 | GCH-01 | PI02466 | Verified | LK-10-GCH-P41-0101-01 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
GCH-01 | GCH-01 | PI02575 | Verified | ISO 10-GCH-PD-P41-0104-02 Install restraints as per detail for 10-GCH-PD-HGR-0073. | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GCH-01 | GCH-01 | PI02576 | Verified | ISO 10-GCH-PD-P41-0104-01 install isolation kit at UG connection. | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GCH-01 | GCH-01 | PI02620 | Verified | LK-10-GCH-PD-P41-0101-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-07-25 | Tom Noble | 2019-07-25 | Tom Noble
GCH-01 | GCH-01 | PI02621 | Verified | LK-10-GCH-PD-P41-0104-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-07-25 | Tom Noble | 2019-07-25 | Tom Noble
GCH-01 | GCH-01 | PI02622 | Verified | LK-10-GCH-PD-P41-0104-03 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-07-25 | Tom Noble | 2019-07-25 | Tom Noble
GCH-01 | GCH-01 | PI02623 | Verified | LK-10-GCH-PD-P41-0104-04 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-07-25 | Tom Noble | 2019-07-25 | Tom Noble
GCH-01 | GCH-01 | PI02624 | Verified | LK-10-GCH-PD-P42-0103-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-07-24 | Damon Turner | 2019-07-24 | Tom Noble
GCH-01 | GCH-01 | PI02628 | Verified | LK-10-GCH-PD-P41-0101-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-07-26 | Tom Noble | 2019-07-26 | Tom Noble
GCH-01 | GCH-01 | PI02730 | Verified | 10-GCH-PD-P41-0100-01 install HGR-0059. | B | P | Damon Turner | McD | 2019-07-24 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GCH-01 | GCH-01 | PI02731 | Verified | 10-GCH-PD-P41-0100-02 install vendor supplied instrument 10-GCH-V-0100. | A | P | Damon Turner | McD | 2019-07-24 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GCH-01 | GCH-01 | PI02732 | Verified | 10-GCH-PD-P41-0102-01 install HGR-0065. | B | P | Damon Turner | McD | 2019-07-24 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GCH-01 | GCH-01 | PI02734 | Verified | Tie duct bank 51 grounds into ground grid in the Sw of the hydrogen pad. | A | E | Luis Cantu | McD | 2019-07-24 | Luis Cantu | Const | 2019-07-25 | Ken Mundy | 2019-07-29 | Mike Tabbert
GCH-01 | GCH-01 | PI02735 | Verified | Complete all completion paperwork. | A | E | Luis Cantu | McD | 2019-07-24 | Luis Cantu | Const | 2019-08-03 | Mike Tabbert | 2019-08-03 | Mike Tabbert
GCH-01 | GCH-01 | PI02736 | Verified | Housekeeping in hydrogen pad. | A | E | Luis Cantu | McD | 2019-07-24 | Luis Cantu | Const | 2019-07-25 | Ken Mundy | 2019-07-29 | Mike Tabbert
GCH-01 | GCH-01 | PI02737 | Verified | LB covers and T covers missing at 1C-GCH-CP-9000 and 1C-GCH-RAK-9000. | B | E | Luis Cantu | McD | 2019-07-24 | Luis Cantu | Const | 2019-07-25 | Ken Mundy | 2019-07-29 | Mike Tabbert
GCH-01 | GCH-01 | PI02738 | Verified | Clean Panel 1C-GCH-CP-9000. | A | E | Luis Cantu | McD | 2019-07-24 | Luis Cantu | Const | 2019-07-25 | Ken Mundy | 2019-08-03 | Mike Tabbert
GCH-01 | GCH-01 | PI02739 | Verified | Ground outside door of panel 1C-GCH-CP-9000. | A | E | Luis Cantu | McD | 2019-07-24 | Luis Cantu | Const | 2019-07-31 | Ken Mundy | 2019-08-03 | Mike Tabbert
GCH-01 | GCH-01 | PI02740 | Verified | Ground shields of cables 1CGCHX0003 and 1CGCHX0001 in panel 1C-GCH-CP-9000. | A | E | Luis Cantu | McD | 2019-07-24 | Luis Cantu | Const | 2019-07-25 | Ken Mundy | 2019-07-29 | Mike Tabbert
GCH-01 | GCH-01 | PI02742 | Verified | Erect hydrogen area fencing. | B | C | Sheri Fritz | McD | 2019-07-24 | Sheri Fritz | Const | 2019-09-13 | Michael Law | 2019-11-23 | Michael Law
GCH-01 | GCH-01 | PI02743 | Verified | Install hydrogen area bollards. | B | C | Jerry Smith | McD | 2019-07-24 | Jerry Smith | Const | 2019-09-06 | Jerry Smith | 2019-11-23 | Michael Law
GCH-01 | GCH-01 | PI02744 | Verified | Caulk grounds at stub-ups. | B | E | Luis Cantu | McD | 2019-07-24 | Luis Cantu | Const | 2019-07-26 | Ken Mundy | 2019-07-29 | Mike Tabbert
GCH-01 | GCH-01 | PI02745 | Verified | Need sign identifying emergency shut off at panel at the CO2 skid. | B | E | Mike Tabbert | McD | 2019-07-24 | Mike Tabbert | Const | 2019-08-01 | Mike Tabbert | 2019-08-29 | Richard Rothwell
GCH-01 | GCH-01 | PI02746 | Verified | Weld repair required at valve 10-GCH-V-0102 at skid. | A | P | Terry Deaton | McD | 2019-07-24 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-08-01 | Kelvin Cook
GCH-01 | GCH-01 | PI02747 | Verified | Install retractable ground for truck unloading. | A | E | Luis Cantu | McD | 2019-07-24 | Luis Cantu | Const | 2019-08-03 | Ken Mundy | 2019-08-03 | Mike Tabbert
GCH-01 | GCH-01 | PI02748 | Verified | On ISO 10-GCH-PD-P41-0100-01 pipe support 10-GCH-PD-HGR-0059 is not installed. | B | P | Terry Deaton | McD | 2019-07-24 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Kelvin Cook
GCH-01 | GCH-01 | PI02749 | Verified | On ISO 10-GCH-PD-P41-0101-01 pipe support 10-GCH-V-0106 missing lock for lever. | B | P | Damon Turner | McD | 2019-07-24 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
GCH-01 | GCH-01 | PI02750 | Verified | On ISO 10-GCH-PD-P41-0102-01 pipe support 10-GCH-PD-HGR-0065 is not installed. | A | P | Terry Deaton | McD | 2019-07-24 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-08-01 | Kelvin Cook
GCH-01 | GCH-01 | PI02751 | Verified | On ISO 10-GCH-PD-P41-0102-01 specialty item 10-GCH-RC-0101 is not installed. | B | P | Terry Deaton | McD | 2019-07-24 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-20 | Kelvin Cook
GCH-01 | GCH-01 | PI02758 | Verified | See new revision On ISO 10-GCH-PD-P41-0100-02 after the 90 heading to valve 10-GCH-V-0101 is not installed. | A | P | Terry Deaton | McD | 2019-07-24 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-08-01 | Kelvin Cook
GCH-01 | GCH-01 | PI02759 | Verified | On ISO 10-GCH-PD-P41-0101-01 connection to underground needs added support. | B | P | Terry Deaton | McD | 2019-07-24 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-08-01 | Kelvin Cook
GCH-01 | GCH-01 | PI02760 | Verified | On ISO 10-GCH-PD-P41-0104-05 pipe support 10-GCH-PD-HGR-0004 loose ubolt. | B | P | Damon Turner | McD | 2019-07-24 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GCH-01 | GCH-01 | PI02761 | Verified | On ISO 10-GCH-PD-P41-0104-05 pipe support 10-GCH-PD-HGR-0005 loose ubolt. | B | P | Damon Turner | McD | 2019-07-24 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GCH-01 | GCH-01 | PI02762 | Verified | On ISO 10-GCH-PD-P41-0104-05 pipe support 10-GCH-PD-HGR-0008 missing guide. | A | P | Damon Turner | McD | 2019-07-24 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GCH-01 | GCH-01 | PI02763 | Verified | On ISO 10-GCH-PD-P41-0104-06 pipe support 10-GCH-PD-HGR-0009 loose ubolt. | B | P | Damon Turner | McD | 2019-07-24 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GCH-01 | GCH-01 | PI02764 | Verified | On ISO 10-GCH-PD-P41-0104-06 pipe support 10-GCH-PD-HGR-0010 loose ubolt. | B | P | Damon Turner | McD | 2019-07-24 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GCH-01 | GCH-01 | PI02765 | Verified | On ISO 10-GCH-PD-P41-0104-06 pipe support 10-GCH-PD-HGR-0011 loose ubolt. | B | P | Damon Turner | McD | 2019-07-24 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GCH-01 | GCH-01 | PI02766 | Verified | On ISO 10-GCH-PD-P41-0104-06 pipe support 10-GCH-PD-HGR-0012 incorrectly welded. | A | P | Damon Turner | McD | 2019-07-24 | Damon Turner | Const | 2019-07-24 | Kelvin Cook | 2019-07-24 | Kelvin Cook
GCH-01 | GCH-01 | PI02803 | Verified | Ground piping in hydrogen system. | A | E | Luis Cantu | McD | 2019-07-26 | Luis Cantu | Const | 2019-07-31 | Ken Mundy | 2019-08-03 | Mike Tabbert
GCH-01 | GCH-01 | PI13007 | Verified | Downstream union installed backwards at 10-GCH-V-0100; Excess Flow Valve, Line No. 2-10-GCH-0100 | A | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm |  |  | 2019-11-20 | Blake Boudreaux
GCH-01 | GCH-01 | PI13008 | Verified | Replace unions with flanges at 10-GCH-V-0100, Line No. 2-10-GCH-0100, engineering to evaluate | D | P | Kevin Leppert | McD | 2019-11-14 | Kevin Leppert | Comm | 2020-02-07 | Michael Law | 2020-04-08 | Bernard Stasse
GCH-01 | GCH-01 | PI13009 | Verified | U-Bolts loose at Line No.'s 2-10-GCH-0100 and 2-10-GCH-0110 | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-15 | Bobby Williams | 2020-02-11 | Blake Boudreaux
GCH-01 | GCH-01 | PI13010 | Verified | Hanger 10-GCH-PD-HGR-0012 has incorrect clamps, STG Bldg. Mezzanine NE side | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-15 | Bobby Williams | 2020-01-23 | Blake Boudreaux
GCH-01 | GCH-01 | PI13011 | Verified | Angle iron support for U-Bolt 1B-GCH-PD-HGR-0040 is inadequate at Line No. 1.5-10-GCH-0105, W side of GT B | D | P | Michael Law | McD | 2019-11-14 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-05-28 | Dave Goldak
GCH-01 | GCH-01 | PI13012 | Verified | Tag all subsystem components | C | P | James Beech | McD | 2019-11-14 | James Beech | Comm | 2020-05-20 | James Beech | 2020-05-28 | Dave Goldak
GCH-01 | GCH-01 | PI13013 | Verified | Remove rust and cold gal supports where needed | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-15 | Bobby Williams | 2020-02-12 | Shannon Scott
GCH-01 | GCH-01 | PI13014 | Verified | Remove unused ground lugs from last above ground flange at Line No. 2-10-GCH-0103 | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-02-19 | Bobby Williams | 2020-03-04 | Dave Goldak
GCH-01 | GCH-01 | PI13015 | Verified | Touch up paint throughout system | C | X | Johnny Campbell | McD | 2019-11-14 | Johnny Campbell | Comm | 2020-04-08 | Johnny Campbell | 2020-04-24 | Mark Williamson
GCH-01 | GCH-01 | PI13016 | Verified | Remove unused ground lugs from first flange above ground at STG Building, Line No. 2-10-GCH-0104 | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-02-19 | Bobby Williams | 2020-03-05 | Dave Goldak
GCH-01 | GCH-01 | PI13017 | Verified | Remove rope, tape, and wire from all system piping | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-15 | Bobby Williams | 2020-02-12 | Shannon Scott
GCH-01 | GCH-01 | PI13965 | Verified | LK-10-GCH-PD-P41-0100-02 FW3,4,5,6 VT rejected due to more filler material required to cover threads. "Outage" | B | P | Bobby Williams | McD | 2019-12-04 | Bobby Williams | Const | 2020-01-31 | Charlie English | 2020-02-05 | Tom Noble
GCH-01 | GCH-01 | PI15234 | Verified | Replace Hydrogen Emergency Shutoff sign screws with bolts and nuts on outside of 10-NJS-PNL-0005; CO2 & Hydrogen Area Power Panel | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2020-08-14 | Dave Goldak
GCH-01 | GCH-01 | PI15839 | Verified | 1A-CTS-PD-P40-0315-03 Modify piping Vent per REV FR-01 | B | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Const | 2020-02-02 | Charlie English | 2020-02-03 | Kelvin Cook
GCH-01 | GCH-01 | PI15841 | Verified | 1A-CTS-HGR-0310 Modify support per Revision | B | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Const | 2020-02-02 | Charlie English | 2020-02-03 | Kelvin Cook
GCH-01 | GCH-01 | PI15842 | Verified | 1B-CTS-PD-P40-0315-03 Modify piping Vent per REV FR-01 | B | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Const | 2020-02-02 | Bobby Williams | 2020-02-03 | Kelvin Cook
GCH-01 | GCH-01 | PI15843 | Verified | 1B-CTS-PD-P41-0320-03 Modify piping Vent per REV FR-01 | B | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Const | 2020-02-02 | Bobby Williams | 2020-02-03 | Kelvin Cook
GCH-01 | GCH-01 | PI15844 | Verified | 1B-CTS-HGR-0336 Modify support per Revision | B | P | Bobby Williams | McD | 2020-01-09 | Bobby Williams | Const | 2020-02-02 | Bobby Williams | 2020-02-03 | Kelvin Cook
GCH-01 | GCH-01 | PI17475 | Verified | Red line drawing 1B-GCH-PD-P41-0105-03. Valve 1B-GCH-V-0114 installed stem south. | D | P | Michael Law | McD | 2020-03-03 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
GCH-01 | GCH-01 | PI17476 | Verified | Red line drawing 1B-GCH-PD-P41-0105-03. Support 1B-GCH-HGR-0056 installed in different location | D | P | Michael Law | McD | 2020-03-03 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-06-04 | Dave Goldak
GCH-01 | GCH-01 | PI17477 | Verified | Remove stray snow fence from piping northwest of 1B GT. Hanging from a valve | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-08 | James Beech | 2020-05-26 | Dave Goldak
GCH-01 | GCH-01 | PI17478 | Verified | Support 1B-GCH-HGR-0038 is missing/not installed | B | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-09 | Tim Green | 2020-05-26 | Dave Goldak
GCH-01 | GCH-01 | PI17479 | Verified | Support 1B-GCH-HGR-0051 is missing one nut above plate per drawing. | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-27 | James Beech | 2020-06-24 | Dave Goldak
GCH-01 | GCH-01 | PI17480 | Verified | Support 1B-GCH-HGR-0051; upper plate not welded to angle iron per drawing. | B | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-09 | Tim Green | 2020-05-26 | Dave Goldak
GCH-01 | GCH-01 | PI17481 | Verified | Support 1A-GCH-HGR-0035; three nuts loose at anchor bolt baseplate | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-26 | Dave Goldak
GCH-01 | GCH-01 | PI17482 | Verified | Support 1A-GCH-HGR-0030; upper plate not welded to angle iron per drawing. | B | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-03-07 | Tim Green | 2020-03-09 | Dave Goldak
GCH-01 | GCH-01 | PI17483 | Verified | Red line drawing 10-GCH-PD-P41-0100-02. Valve 10-GCH-V-0105 installed stem EAST. | D | P | Michael Law | McD | 2020-03-03 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
GCH-01 | GCH-01 | PI17484 | Verified | Patch paint (yellow) weld. Line 10-GCH-0100-02 | C | C | Johnny Campbell | McD | 2020-03-03 | Johnny Campbell | Comm | 2020-04-08 | Johnny Campbell | 2020-04-24 | Mark Williamson
GCH-01 | GCH-01 | PI17485 | Verified | Support 10-GCH-HGR-0062; one loose nut at anchor bolt baseplate | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-26 | Dave Goldak
GCH-01 | GCH-01 | PI17486 | Verified | Valve 10-GCH-V-0102; incorrect ID tag installed | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-08 | James Beech | 2020-05-26 | Dave Goldak
GCH-01 | GCH-01 | PI17487 | Verified | Safety Relief Valve 10-GCH-SRV-0101; painted over valve nameplate | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-05 | James Beech | 2020-05-26 | Dave Goldak
GCH-01 | GCH-01 | PI17488 | Verified | Remove/relocate Heat trace piping/tubing supports from Hydrogen piping. Two locations north side of condenser. Line 10-GSH-0104-02. | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm | 2020-05-29 | James Beech | 2020-06-24 | Dave Goldak
GCH-01 | GCH-01 | PI17489 | Verified | Support 10-GCH-HGR-0080; one bolt is too short on the bottom side of hanger | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-26 | Dave Goldak
GCH-01 | GCH-01 | PI17490 | Verified | Line 10-GCH-P41-0104-03 piping installed out of level, slopes down toward the south. | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm | 2020-06-04 | Dave Goldak | 2020-06-04 | Dave Goldak
GCH-01 | GCH-01 | PI17491 | Verified | Support 10-GCH-HGR-0081; missing nuts on threaded rod | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-26 | Dave Goldak
GCH-01 | GCH-01 | PI17492 | Verified | Line 1C-GCH-P41-0110-01 piping installed sloping backwards. Should slope down to the south. | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm | 2020-06-04 | Dave Goldak | 2020-06-04 | Dave Goldak
GCH-01 | GCH-01 | PI17493 | Verified | Valve 1C-GCH-V-0131; Missing Equipment ID tag | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-27 | James Beech | 2020-06-18 | Dave Goldak
GCH-01 | GCH-01 | PI17494 | Verified | Red line drawing 10-GCH-PD-P42-0103. Additional (un-numbered pipe support added at Hydrogen storage are (elevation 500) | D | P | Michael Law | McD | 2020-03-03 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-06-04 | Dave Goldak
GCH-02 | GCH-02 | PI01008 | Verified | Paint all piping. | C | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-08 | Michael Law | 2019-05-08 | Michael Law
GCH-02 | GCH-02 | PI01012 | Verified | Install proper gasket after pressure test is completed and prior to turnover to commissioning. | A | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-16 | Terry Deaton | 2019-05-16 | Kelvin Cook
GCH-02 | GCH-02 | PI01016 | Verified | Tag valve 1A-GCH-V-0123. | C | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-22 | Terry Deaton | 2019-06-03 | Kelvin Cook
GCH-02 | GCH-02 | PI13018 | Verified | Install correct bolts at Hydrogen flange connection to Mitsubishi CO2/Hydrogen manifold | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2019-11-21 | Kelvin Cook | 2019-12-13 | Blake Boudreaux
GCH-02 | GCH-02 | PI13019 | Verified | Angle iron support for hanger 1A-GCH-PD-HGR-0019 is inadequate, Line No. 1.5-GCH-0105, W side of GT A | D | P | Michael Law | McD | 2019-11-14 | Michael Law | Comm |  |  | 2020-02-12 | Shannon Scott
GCH-02 | GCH-02 | PI13020 | Verified | Remove tape, wire, rope, and unsused tags throughout subsytem | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-16 | Bobby Williams | 2020-02-12 | Shannon Scott
GCH-02 | GCH-02 | PI13021 | Verified | Remove rust and touch up paint throughout subsystem | C | X | Jerry Smith | McD | 2019-11-14 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
GCH-02 | GCH-02 | PI13022 | Verified | Remove rust and cold gal supports throughout subsystem | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-16 | Bobby Williams | 2020-02-12 | Shannon Scott
GCH-02 | GCH-02 | PI13023 | Verified | Tag all subsystem components | C | P | James Beech | McD | 2019-11-14 | James Beech | Comm | 2020-04-22 | James Beech | 2020-05-26 | Dave Goldak
GCH-02 | GCH-02 | PI17473 | Verified | Support 1A-GCH-HGR-0036: 3 Loose nuts at anchor bolts. | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-26 | Dave Goldak
GCH-02 | GCH-02 | PI17474 | Verified | Support 1A-GCH-HGR-0037: All 4 nuts at anchor bolts are loose. | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-26 | Dave Goldak
GCH-03 | GCH-03 | PI01009 | Verified | Paint all piping. | C | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-08 | Michael Law | 2019-05-08 | Michael Law
GCH-03 | GCH-03 | PI01013 | Verified | Install proper gasket after pressure test is completed and prior to turnover to commissioning. | A | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-14 | Terry Deaton | 2019-05-14 | Kelvin Cook
GCH-03 | GCH-03 | PI01017 | Verified | Tag valve 1B-GCH-V-0113. | C | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-22 | Terry Deaton | 2019-06-03 | Kelvin Cook
GCH-03 | GCH-03 | PI13024 | Verified | Bolts too long and nuts on backwards at tie in flange to 1B-CTS-MKQ01; 1B Gas Control Unit, Line No. 1.5-1B-GCH-105, S side of GT B | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2019-11-21 | Kelvin Cook | 2019-12-13 | Blake Boudreaux
GCH-03 | GCH-03 | PI13025 | Verified | Bent hangar rod at 1B-GCH-PD-HGR-0048, Line No, 1.5-1B-GCH-0105, SW side of GT B | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-15 | Billy Williams | 2020-02-11 | Shannon Scott
GCH-03 | GCH-03 | PI13026 | Verified | Incorrect hangar clamps at 1B-GCH-PD-HGR-0048, Line No, 1.5-1B-GCH-0105, SW side of GT B | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2019-11-21 | Kelvin Cook | 2019-12-13 | Blake Boudreaux
GCH-03 | GCH-03 | PI13027 | Verified | Loose clamp bolts at 1B-GCH-PD-HGR-0048, Line No, 1.5-1B-GCH-0105, SW side of GT B | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2019-11-21 | Kelvin Cook | 2019-12-13 | Blake Boudreaux
GCH-03 | GCH-03 | PI13028 | Verified | Remove rust and paint hydrogen throughout subsystem | C | C | Jorge Alexander | McD | 2019-11-14 | Jorge Alexander | Comm |  |  | 2020-02-11 | Shannon Scott
GCH-03 | GCH-03 | PI13029 | Verified | Remove rust and cold gal all supports throughout subsystem | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-16 | Bobby Williams | 2020-02-11 | Shannon Scott
GCH-03 | GCH-03 | PI13030 | Verified | Remove tape, wire, rope, and old unused tag throughout subsystem piping | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-16 | Bobby Williams | 2020-02-11 | Shannon Scott
GCH-03 | GCH-03 | PI13031 | Verified | Tag all subsystem components | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm |  |  | 2020-02-11 | Shannon Scott
GCH-04 | GCH-04 | PI02626 | Verified | LK-1C-GCH-PD-P41-0108-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-14 | Damon Turner | 2019-08-14 | Tom Noble
GCH-04 | GCH-04 | PI02627 | Verified | LK-1C-GCH-PD-P41-0108-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-14 | Damon Turner | 2019-08-14 | Tom Noble
GCH-04 | GCH-04 | PI02733 | Verified | Pour seals with chico after commissioning activities in the hydrogen pad. | C | E | Chris Colvin | McD | 2019-07-24 | Chris Colvin | Const | 2020-01-14 | Mike Tabbert | 2020-01-20 | Mike Tabbert
GCH-04 | GCH-04 | PI02625 | Verified | LK-1C-GCH-PD-P40-0115-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-14 | Damon Turner | 2019-08-14 | Tom Noble
GCH-04 | GCH-04 | PI03807 | Verified | Install 1C-GCH-V-90003A & B and 1C-GCH-V-9011A & B. | A | P | Alex Isaac | McD | 2019-08-12 | Alex Isaac | Const | 2019-09-13 | Damon Turner | 2019-09-13 | Kelvin Cook
GCH-04 | GCH-04 | PI03808 | Verified | Clean out the Hydrogen Gas Measuring Rack. | B | P | Damon Turner | McD | 2019-08-12 | Damon Turner | Const | 2019-08-14 | Damon Turner | 2019-08-20 | Joshua Sturgeon
GCH-04 | GCH-04 | PI03809 | Verified | The key is broken off in panel 1C-GCH-CP-9000. | B | E | Christie Harris | McD | 2019-08-12 | Christie Harris | Const | 2019-08-21 | Christie Harris | 2019-08-21 | Mike Tabbert
GCH-04 | GCH-04 | PI03810 | Verified | Cable conductors in 1C-GCH-PSL-9021 are labeled "X" instead of "C". | A | E | Dustin Futrell | McD | 2019-08-12 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-15 | Albert Burge
GCH-04 | GCH-04 | PI03811 | Verified | Valve tags for 1C-STO-V-9362, 9363 & 9364 need to be swapped with valve tags 1C-GCH-V-9016, 9017 & 9018. | B | P | Damon Turner | McD | 2019-08-12 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-09-26 | Albert Burge
GCH-04 | GCH-04 | PI03812 | Verified | Remove teflon tap on liquid detector vent & drain. | B | P | Damon Turner | McD | 2019-08-12 | Damon Turner | Const | 2019-08-14 | Damon Turner | 2019-08-20 | Kelvin Cook
GCH-04 | GCH-04 | PI03813 | Verified | Provide adequate support for Float Switch 1C-GCH-LSH-9018. | B | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-08-21 | Gonzalo Pena | 2019-08-21 | Alex Isaac
GCH-04 | GCH-04 | PI03814 | Verified | Complete grounding on all pipe flanges. | A | E | Dustin Futrell | McD | 2019-08-12 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-20 | Kelvin Cook
GCH-04 | GCH-04 | PI03815 | Verified | Bolts are too short on 1C-GCH-SRV-0107. | A | P | Damon Turner | McD | 2019-08-12 | Damon Turner | Const | 2019-08-14 | Damon Turner | 2019-08-15 | Albert Burge
GCH-04 | GCH-04 | PI03816 | Verified | Complete vent line piping. | A | P | Damon Turner | McD | 2019-08-12 | Damon Turner | Const | 2019-08-15 | Damon Turner | 2019-08-15 | Justin Houdeshell
GCH-04 | GCH-04 | PI03857 | Verified | ISO DDKW27136-b sheet 3 coupling connecting to Leak test SW is missing | A | P | Damon Turner | McD | 2019-08-13 | Damon Turner | Const | 2019-08-15 | Damon Turner | 2019-08-15 | Justin Houdeshell
GCH-04 | GCH-04 | PI03858 | Verified | Drawing SPC-GIH-XULC1-00005 SH28 (GFP-1 line) is incomplete | A | P | Damon Turner | McD | 2019-08-13 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-21 | Alex Isaac
GCH-04 | GCH-04 | PI03859 | Verified | Drawing SPC-GIH-XULC1-00005 SH28 (GFS-1 line) is incomplete | A | P | Damon Turner | McD | 2019-08-13 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-21 | Alex Isaac
GCH-04 | GCH-04 | PI03860 | Verified | Drawing SPC-GIH-XULC1-00005 SH30 (H2 Gas Filter Inlet GST) is not installed ; ISO DDKW27136-b sheet 3 on Nozzle table item C | A | P | Damon Turner | McD | 2019-08-13 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-21 | Alex Isaac
GCH-04 | GCH-04 | PI03861 | Verified | Drawing SPC-GIH-XULC1-00005 SH30 (H2 Gas Filter Inlet GSC) is not installed ; ISO DDKW27136-b sheet 3 on Nozzle table item B | A | P | Damon Turner | McD | 2019-08-13 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-21 | Alex Isaac
GCH-04 | GCH-04 | PI03862 | Verified | 1C-GCH-PD-P40-0108-01 and -02 is incomplete | A | P | Damon Turner | McD | 2019-08-13 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
GCH-04 | GCH-04 | PI03863 | Verified | 1C-GCH-PD-P40-0115-01 and -02 connecting to Toshiba Gas Control System/ DDKW27136-b TP-EA-06 is incomplete | A | P | Damon Turner | McD | 2019-08-13 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
GCH-04 | GCH-04 | PI03864 | Verified | DDKW27142 page 6/10 (GLD) needs support underneath the generator, suggest using a shim pad on the W-Beam with a ubolt | A | P | Damon Turner | McD | 2019-08-13 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
GCH-04 | GCH-04 | PI03865 | Verified | DDKW27142 page 7/10 (GHD) is run level and needs more slope | A | P | Damon Turner | McD | 2019-08-13 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
GCH-04 | GCH-04 | PI03866 | Verified | DDKW27142 page 5/10 (GHF) needs support under generators suggest using 3x3 angle to catch adjacent 2" and 1" piping. | A | P | Damon Turner | McD | 2019-08-13 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
GCH-04 | GCH-04 | PI04244 | Verified | Complete Test GCH-T-06 (pneumatic) and turn documents. | A | P | Damon Turner | McD | 2019-08-14 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-16 | Kelvin Cook
GCH-04 | GCH-04 | PI04245 | Verified | Complete Installation and turn in documents on GCH-T-07 (in-service) vents and drains. | A | P | Damon Turner | McD | 2019-08-14 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-16 | Kelvin Cook
GCH-04 | GCH-04 | PI13032 | Verified | Complete walkdown of GCH-04 after hydrogen manifold piping air blows are complete | B | P | J.L. Bickham | McD | 2019-11-14 | J.L. Bickham | Comm | 2020-02-21 | J.L. Bickham | 2020-02-22 | J.L. Bickham
GCH-04 | GCH-04 | PI13033 | Verified | Loose U-Bolts downstream of 1-GCH-SRV-0107; Hydrogen Safety Relief Valve | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-17 | Charlie English | 2020-02-12 | Shannon Scott
GCH-04 | GCH-04 | PI13034 | Verified | Panel door ground disconnected at 1C-GCH-CP-9000; Hydrogen/CO2 Gas Purity Indicator Panel | B | E | Chris Colvin | McD | 2019-11-14 | Chris Colvin | Comm | 2019-11-21 | Richard Cruz | 2019-12-13 | Blake Boudreaux
GCH-04 | GCH-04 | PI13035 | Verified | Remove tape, wire, rope and unused tags from subsytem components | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-16 | Bobby Williams | 2020-02-12 | Shannon Scott
GCH-04 | GCH-04 | PI13036 | Verified | Remove rust and paint subsystem piping | C | X | Jerry Smith | McD | 2019-11-14 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
GCH-04 | GCH-04 | PI13037 | Verified | Remove rust and cold gal subsystem supports | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-16 | Bobby Williams | 2020-02-12 | Shannon Scott
GCH-04 | GCH-04 | PI13038 | Verified | Tag all subsystem components | C | P | James Beech | McD | 2019-11-14 | James Beech | Comm | 2020-04-22 | James Beech | 2020-05-26 | Dave Goldak
GCH-04 | GCH-04 | PI17638 | Verified | 1C-GCH-SRV-0107: Valve nameplate has been painted over. | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-20 | James Beech | 2020-05-26 | Dave Goldak
GCH-04 | GCH-04 | PI17639 | Verified | Missing ground jumper on removable spool flange. Downstream from SRV. | C | E | Chris Colvin | McD | 2020-03-03 | Chris Colvin | Comm | 2020-04-28 | Michael Law | 2020-05-26 | Dave Goldak
GCH-04 | GCH-04 | PI17640 | Verified | Support 10-GCH-HGR-0099: Top plate not welded per drawing. | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-26 | James Beech | 2020-05-26 | Dave Goldak
GCH-04 | GCH-04 | PI17641 | Verified | Support 10-GCH-HGR-0099: Missing one jamb nut on top of plate/threaded rod per drawing. | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-26 | Dave Goldak
GCH-04 | GCH-04 | PI17642 | Verified | Support 10-GCH-HGR-0100: Missing two nuts at u-bolt (top side of angle leg) per drawing. | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-26 | Dave Goldak
GCH-04 | GCH-04 | PI17643 | Verified | Line 1C-GCH-0108-01 not installed per isometric. Red line drawing. | D | P | Michael Law | McD | 2020-03-03 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-06-04 | Dave Goldak
GCH-04 | GCH-04 | PI17644 | Verified | Support 10-GCH-HGR-0103: Support missing/ not installed. | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm |  |  | 2020-05-26 | Dave Goldak
GCH-04 | GCH-04 | PI17645 | Verified | Line 1C-GCH-0108-02 not installed per isometric. Red line drawing. | D | P | Michael Law | McD | 2020-03-03 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-06-04 | Dave Goldak
GCH-04 | GCH-04 | PI17646 | Verified | Support 10-GCH-HGR-0107: Loose nuts at u-bolt. | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-26 | Dave Goldak
GCH-04 | GCH-04 | PI17647 | Verified | Support 10-GCH-HGR-0113: one leg missing grout at baseplate. One leg broken/damaged grout. | C | C | Johnny Campbell | McD | 2020-03-03 | Johnny Campbell | Comm | 2020-04-14 | Johnny Campbell | 2020-04-28 | Mark Williamson
GCH-04 | GCH-04 | PI17648 | Verified | Support 10-GCH-HGR-0111: Not enough weld to column . | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-27 | James Beech | 2020-07-07 | Dave Goldak
GCH-04 | GCH-04 | PI17649 | Verified | Support 10-GCH-HGR-0110: Not installed. Refer to 1C-GCH-HGR-0125 and red line isometric . | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-26 | James Beech | 2020-06-04 | Dave Goldak
GCH-04 | GCH-04 | PI17650 | Verified | Support 1C-GCH-HGR-0121: 3/8" plate missing/not installed (hanger drawing Part #3). | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-27 | James Beech | 2020-08-14 | Dave Goldak
GCH-04 | GCH-04 | PI17651 | Verified | Support 10-GCH-HGR-0806: Not installed. Refer to 10-GCH-HGR-0105 and red line isometric | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm | 2020-06-04 | Dave Goldak | 2020-06-04 | Dave Goldak
GCH-04 | GCH-04 | PI17652 | Verified | Support 1C-GCH-HGR-0122: plate steel restraints missing/not installed (hanger drawing Part #4). | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-27 | James Beech | 2020-08-14 | Dave Goldak
GCH-04 | GCH-04 | PI17653 | Verified | Support 1C-GCH-HGR-0125: plate steel restraints missing/not installed (hanger drawing Part #4). | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-27 | James Beech | 2020-08-14 | Dave Goldak
GMC-01 | GMC-01 | PI01986 | Verified | Thread test port on Stator Cooling | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-08 | Stuart Herring
GMC-01 | GMC-01 | PI01987 | Verified | Hardware missing on flanges, tighten nuts on flanges of pipe | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-08-08 | Stuart Herring
GMC-01 | GMC-01 | PI01988 | Verified | Loose flanges around Stator Cooling | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-08-08 | Stuart Herring
GMC-01 | GMC-01 | PI01989 | Verified | Valve 1C-GMC-V-944B need to be finish connected | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-08-08 | Stuart Herring
GMC-01 | GMC-01 | PI01990 | Verified | Jacking bolt missing on flow trap tank | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-08-08 | Stuart Herring
GMC-01 | GMC-01 | PI01991 | Verified | Line HFC-1 and HFG-1 is missing and not complete | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-08 | Stuart Herring
GMC-01 | GMC-01 | PI01992 | Verified | High pressure pipe is not tied into system | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-08 | Stuart Herring
GMC-01 | GMC-01 | PI01994 | Verified | Missing valve 1C-GMC-V-9492, need to change direction when installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-08 | Stuart Herring
GMC-01 | GMC-01 | PI02104 | Verified | Carbon contamination must be removed | B | X | James Beech | McD | 2019-07-02 | James Beech | Const | 2019-08-01 | Damon Turner | 2019-12-01 | Stuart Herring
GMC-01 | GMC-01 | PI02105 | Verified | Clean all skids/areas | B | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-30 | Damon Turner | 2019-08-16 | Shannon Scott
GMC-01 | GMC-01 | PI02106 | Verified | Grout skids | A | C | Johnny Campbell | McD | 2019-07-02 | Johnny Campbell | Const | 2019-07-16 | Johnny Campbell | 2019-07-31 | Shannon Scott
GMC-01 | GMC-01 | PI02107 | Verified | Fix poison pads on all supports | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-02 | Shannon Scott
GMC-01 | GMC-01 | PI02108 | Verified | Tag all valves and equipment | C | P | Tim Green | McD | 2019-07-02 | Tim Green | Const | 2021-01-22 | Eric Policarpio | 2021-01-22 | Eric Policarpio
GMC-01 | GMC-01 | PI02109 | Verified | Fix incomplete bolt-ups | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-02 | Shannon Scott
GMC-01 | GMC-01 | PI02110 | Verified | Pump seal water lines and drains not on P&ID | C | P | Charles Worthington | McD | 2019-07-02 | Charles Worthington | Const | 2020-04-28 | Charles Worthington | 2020-07-24 | Nelson Eichelberger
GMC-01 | GMC-01 | PI02111 | Verified | Stator Cooling Water skid platform has no top rung for ladder. | C | C | Charles Worthington | McD | 2019-07-02 | Charles Worthington | Const | 2020-06-26 | Tim Gallegos | 2020-07-14 | Nelson Eichelberger
GMC-01 | GMC-01 | PI02112 | Verified | Stator Cooling Water skid platform has no slip resistance on rungs for ladder. | C | C | Charles Worthington | McD | 2019-07-02 | Charles Worthington | Const | 2020-06-26 | Tim Gallegos | 2020-07-14 | Nelson Eichelberger
GMC-01 | GMC-01 | PI02113 | Verified | Stator Cooling Water skid platform has no safety gate. | C | C | Charles Worthington | McD | 2019-07-02 | Charles Worthington | Const | 2020-06-26 | Tim Gallegos | 2021-04-21 | John Watts
GMC-01 | GMC-01 | PI02114 | Verified | Stator Cooling Water skid platform has no mid rail. | C | C | Charles Worthington | McD | 2019-07-02 | Charles Worthington | Const | 2020-06-26 | Tim Gallegos | 2020-07-14 | Nelson Eichelberger
GMC-01 | GMC-01 | PI02115 | Verified | RAK-9400 not installed | A | I | Gonzalo Pena | McD | 2019-07-02 | Gonzalo Pena | Const | 2019-07-24 | Gonzalo Pena | 2019-07-31 | Shannon Scott
GMC-01 | GMC-01 | PI02116 | Verified | Cold galv. all supports. | C | P | James Beech | McD | 2019-07-02 | James Beech | Const | 2020-04-22 | James Beech | 2020-07-14 | Nelson Eichelberger
GMC-01 | GMC-01 | PI02117 | Verified | Grout all supports | B | C | Johnny Campbell | McD | 2019-07-02 | Johnny Campbell | Const | 2019-07-16 | Johnny Campbell | 2019-08-29 | Nelson Eichelberger
GMC-01 | GMC-01 | PI02118 | Verified | No mesh screen on vent to atmosphere | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-15 | Dave Goldak
GMC-01 | GMC-01 | PI02119 | Verified | Lines from FE-9445 to RAK-9400 not installed | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-31 | Shannon Scott
GMC-01 | GMC-01 | PI02120 | Verified | STN-9449 is rolled on a 45 degree | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-02 | Shannon Scott
GMC-01 | GMC-01 | PI02121 | Verified | CP-9400 piping inside cabinet does not match P&ID | C | P | Charles Worthington | McD | 2019-07-02 | Charles Worthington | Const | 2020-06-10 | Charles Worthington | 2020-07-24 | Nelson Eichelberger
GMC-01 | GMC-01 | PI02122 | Verified | TI and TE 9443 need to be swapped | A | I | Gonzalo Pena | McD | 2019-07-02 | Gonzalo Pena | Const | 2019-08-01 | Gonzalo Pena | 2019-08-02 | Shannon Scott
GMC-01 | GMC-01 | PI02123 | Verified | V-9441 is missing cap | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-02 | Shannon Scott
GMC-01 | GMC-01 | PI02124 | Verified | V-9468 is missing ubolt | B | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-30 | Damon Turner | 2019-08-29 | Nelson Eichelberger
GMC-01 | GMC-01 | PI02125 | Verified | V-9466 is not lockable. 1C-GMC-V-9466 | D | P | Michael Law | McD | 2019-07-02 | Michael Law | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
GMC-01 | GMC-01 | PI02126 | Verified | P-9400A/B suction lines do not match P&ID | C | P | Charles Worthington | McD | 2019-07-02 | Charles Worthington | Const | 2020-04-28 | Charles Worthington | 2020-07-24 | Nelson Eichelberger
GMC-01 | GMC-01 | PI02127 | Verified | P&ID is missing a cap upstream of V-9471 (red line). | C | P | Charles Worthington | McD | 2019-07-02 | Charles Worthington | Const | 2020-04-28 | Charles Worthington | 2020-07-24 | Nelson Eichelberger
GMC-01 | GMC-01 | PI02128 | Verified | (2) 1/2" lines from SKD-9400 to RAK-9400 not installed | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-31 | Shannon Scott
GMC-01 | GMC-01 | PI02467 | Verified | LK-1C-GMC-P41-0010-01 Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-22 | Damon Turner | Const | 2019-07-24 | Damon Turner | 2019-07-24 | Tom Noble
GMC-01 | GMC-01 | PI02468 | Verified | LK-1C-GMC-P41-0012-02 Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-22 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-01 | Tom Noble
GMC-01 | GMC-01 | PI02772 | Verified | Housekeeping around Water Stator Skid | B | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-26 | Ken Mundy | 2019-07-26 | Fred Michael
GMC-01 | GMC-01 | PI02773 | Verified | Seal counduits going to GMC-CP-9400 | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-26 | Ken Mundy | 2019-08-02 | Shannon Scott
GMC-01 | GMC-01 | PI02774 | Verified | Clean inside GMC-CP-9400 | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-26 | Ken Mundy | 2019-08-02 | Shannon Scott
GMC-01 | GMC-01 | PI02775 | Verified | Label GMC-CP-9400 | B | E | Dustin Futrell | McD | 2019-07-25 | Dustin Futrell | Const | 2019-07-27 | Luis Cantu | 2019-08-06 | Albert Burge
GMC-01 | GMC-01 | PI02776 | Verified | Pull 1CGMAX0010 out of conduit | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-27 | Luis Cantu | 2019-07-29 | Mike Tabbert
GMC-01 | GMC-01 | PI02777 | Verified | 1/2" plug on thermowell above 1C-GMC-TE-9475, 9476 | B | I | Gonzalo Pena | McD | 2019-07-25 | Gonzalo Pena | Const | 2019-07-26 | Gonzalo Pena | 2019-08-02 | Fred Michael
GMC-01 | GMC-01 | PI02778 | Verified | Pull &Terminate cable 1CGMCC0005 | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-30 | Luis Cantu | 2019-08-01 | Mike Tabbert
GMC-01 | GMC-01 | PI02779 | Verified | Pull &Terminate cable 1CGMCX0010 | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-30 | Luis Cantu | 2019-08-01 | Mike Tabbert
GMC-01 | GMC-01 | PI02780 | Verified | 1CGMCC0004, Terminate cable | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-26 | Ken Mundy | 2019-07-29 | Mike Tabbert
GMC-01 | GMC-01 | PI02781 | Verified | Ground sealtight to control panel 1C-GMC-CP-9400 | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-26 | Ken Mundy | 2019-07-29 | Mike Tabbert
GMC-01 | GMC-01 | PI02782 | Verified | Temprature Element J-Box has a bent cover, need to repair. | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-26 | Ken Mundy | 2019-07-29 | Mike Tabbert
GMC-01 | GMC-01 | PI02783 | Verified | 1C-GMC-RAK-9400, Install instrument rack. | A | I | Gonzalo Pena | McD | 2019-07-25 | Gonzalo Pena | Const | 2019-07-26 | Gonzalo Pena | 2019-07-26 | Mike Tabbert
GMC-01 | GMC-01 | PI02784 | Verified | 1C-GMC-RAK-9400, Install conduit to instrument rack. | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-26 | Ken Mundy | 2019-07-29 | Mike Tabbert
GMC-01 | GMC-01 | PI02785 | Verified | Existing T condulet covers need to be installed. | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-26 | Ken Mundy | 2019-07-29 | Mike Tabbert
GMC-01 | GMC-01 | PI02786 | Verified | All completion paper work to be turned in. | A | E | Luis Cantu | McD | 2019-07-25 | Luis Cantu | Const | 2019-07-26 | Ken Mundy | 2019-08-01 | Mike Tabbert
GMC-01 | GMC-01 | PI02948 | Verified | Tubing is not tied to GMC Box 1C-GMC-V-9409 | A | I | Gonzalo Pena | McD | 2019-07-30 | Gonzalo Pena | Const | 2019-08-01 | Gonzalo Pena | 2019-08-02 | Fred Michael
GMC-01 | GMC-01 | PI02949 | Verified | Tubing is not tied to GMC Box 1C-GMC-V-9417 | A | I | Gonzalo Pena | McD | 2019-07-30 | Gonzalo Pena | Const | 2019-08-01 | Gonzalo Pena | 2019-08-02 | Fred Michael
GMC-01 | GMC-01 | PI02950 | Verified | 1C-GMC-FI-9460 need tag | B | I | Gonzalo Pena | McD | 2019-07-30 | Gonzalo Pena | Const | 2019-08-01 | Gonzalo Pena | 2019-08-02 | Fred Michael
GMC-01 | GMC-01 | PI02951 | Verified | 1C-GMC-LSLH-9400 need tag | B | I | Gonzalo Pena | McD | 2019-07-30 | Gonzalo Pena | Const | 2019-08-01 | Gonzalo Pena | 2019-08-02 | Fred Michael
GMC-01 | GMC-01 | PI02952 | Verified | 1C-GMC-TE-9443 need tag | B | I | Gonzalo Pena | McD | 2019-07-30 | Gonzalo Pena | Const | 2019-08-01 | Gonzalo Pena | 2019-08-02 | Fred Michael
GMC-01 | GMC-01 | PI02953 | Verified | 1C-GMC-TE-9474, 9475. 9476 need tag | B | I | Gonzalo Pena | McD | 2019-07-30 | Gonzalo Pena | Const | 2019-08-01 | Gonzalo Pena | 2019-08-02 | Fred Michael
GMC-01 | GMC-01 | PI03040 | Verified | Torque all connections, unbolt and use neversieze on threads | B | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-20 | Damon Turner | 2019-09-18 | Kelvin Cook
GMC-01 | GMC-01 | PI03041 | Verified | On 1C-GMC-SKD-9400, missing 3/4" instrument air supply (on skid, on top of auxilliary panel) | A | I | Gonzalo Pena | McD | 2019-08-02 | Gonzalo Pena | Const | 2019-08-03 | Gonzalo Pena | 2019-08-03 | Justin Houdeshell
GMC-01 | GMC-01 | PI03042 | Verified | On 1C-GMC-SKD-9400, missing 1/2" instrument air supply (on skid, on top of auxilliary panel) | B | I | Gonzalo Pena | McD | 2019-08-02 | Gonzalo Pena | Const | 2019-08-07 | Gonzalo Pena | 2019-08-08 | Justin Houdeshell
GMC-01 | GMC-01 | PI03043 | Verified | On DDKW27137 (3/7) the bolting is loose, remove plastic insert | A | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-02 | Damon Turner | 2019-08-03 | Justin Houdeshell
GMC-01 | GMC-01 | PI03044 | Verified | On DDKW27143 (3/5) the piping does not have adequate support on the turbine top | B | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-06 | Damon Turner | 2019-08-08 | Justin Houdeshell
GMC-01 | GMC-01 | PI03045 | Verified | On DDKW27143 (4/5) the piping does not have correct slope | A | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-02 | Damon Turner | 2019-08-03 | Justin Houdeshell
GMC-01 | GMC-01 | PI03046 | Verified | On DDKW27137 (3/7) fix flow arrows marked on pipe | C | P | James Beech | McD | 2019-08-02 | James Beech | Const | 2019-08-26 | Damon Turner | 2019-11-23 | Kelvin Cook
GMC-01 | GMC-01 | PI03047 | Verified | On DDKW27137 (4/7) fix flow arrows marked on pipe | C | P | James Beech | McD | 2019-08-02 | James Beech | Const | 2019-08-26 | Damon Turner | 2019-11-23 | Kelvin Cook
GMC-01 | GMC-01 | PI03048 | Verified | On DDKW27137 (4/7) / SPC-GIH-XULC1-00005 (43/45) Instrument connetion PP needs a plug | B | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-03 | Damon Turner | 2019-08-03 | Justin Houdeshell
GMC-01 | GMC-01 | PI03049 | Verified | On SPC-GIH-XULC1-00005 (41/45) needs adequate support above skid | B | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-26 | Damon Turner | 2019-10-03 | Kelvin Cook
GMC-01 | GMC-01 | PI03050 | Verified | On DDKW27137 (6/7) / SPC-GIH-XULC1-00005 (44/45) Connection G not installed (tee and plugs) | B | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-20 | Damon Turner | 2019-10-03 | Kelvin Cook
GMC-01 | GMC-01 | PI03051 | Verified | On DDKW27137 (5/7) / SPC-GIH-XULC1-00005 (44/45) Connection F not installed (tee and plugs) | B | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-20 | Damon Turner | 2019-10-03 | Kelvin Cook
GMC-01 | GMC-01 | PI03052 | Verified | On DDKW27137 (5/7) support issues | B | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-06 | Damon Turner | 2019-09-18 | Kelvin Cook
GMC-01 | GMC-01 | PI03053 | Verified | On DDKW27137 (6/7) support issues | B | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-06 | Damon Turner | 2019-09-18 | Kelvin Cook
GMC-01 | GMC-01 | PI03054 | Verified | 1C-GMC-PD-P40-0024-01 has incorrect hardware | B | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-20 | Damon Turner | 2019-10-03 | Kelvin Cook
GMC-01 | GMC-01 | PI03055 | Verified | 1C-GMC-PD-P40-0022-01 has incorrect hardware | B | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-20 | Damon Turner | 2019-10-03 | Kelvin Cook
GMC-01 | GMC-01 | PI03056 | Verified | 1C-GMC-PD-P40-0022-01 trim pipe in drain hub | B | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-03 | Damon Turner | 2019-08-03 | Justin Houdeshell
GMC-01 | GMC-01 | PI03057 | Verified | 1C-GMC-PD-P40-0012-02 is missing 1C-GMC-HGR-0007 | B | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-06 | Damon Turner | 2019-08-09 | Justin Houdeshell
GMC-01 | GMC-01 | PI03058 | Verified | 1C-GMC-PD-P40-0012-02 cannot tie into another line, cope the drain hub per the drawing | B | P | Damon Turner | McD | 2019-08-02 | Damon Turner | Const | 2019-08-06 | Damon Turner | 2019-08-08 | Justin Houdeshell
GMC-01 | GMC-01 | PI03059 | Verified | Blank Plate needed, 2-1/2" 150# bolt pattern | B | P | Kelvin Cook | McD | 2019-08-02 | Kelvin Cook | Const | 2019-09-06 | Damon Turner | 2019-09-18 | Kelvin Cook
GMC-01 | GMC-01 | PI14875 | Verified | Conduit broken to 1C-GMC-TE-9433; Stator Cooling Inlet Temperature Element | B | E | Chris Colvin | McD | 2019-12-24 | Chris Colvin | Comm | 2020-02-27 | Chris Colvin | 2020-07-28 | Keith Pollock
GMC-01 | GMC-01 | PI14876 | Verified | 1C-GMC-PDI-9430; Stator Cooling Inlet Filter Pressure Differential Indicator not installed - on order | C | I | Albert Burge | McD | 2019-12-24 | Albert Burge | Comm | 2020-05-27 | Albert Burge | 2020-07-28 | Keith Pollock
GMC-01 | GMC-01 | PI14877 | Verified | Need additional support for YG6; Feeler Line, Pump Discharge to Rack and YG7; Test Line piping, between Stator Cooling Skid and STG Bldg. mezzanine | B | P | James Beech | McD | 2019-12-24 | James Beech | Comm | 2020-03-10 | James Beech | 2020-04-06 | Bernard Stasse
GMC-01 | GMC-01 | PI14878 | Verified | 1C-GMC-TE-9476; Generator Outlet Conductivity Cell Temperature Element is not installed | B | I | Albert Burge | McD | 2019-12-24 | Albert Burge | Comm |  |  | 2020-01-22 | Albert Burge
GMC-01 | GMC-01 | PI14879 | Verified | 1C-GMC-CP-9400; Stator Cooling Water Aux Panel not grounded | B | E | Chris Colvin | McD | 2019-12-24 | Chris Colvin | Comm | 2020-02-27 | Chris Colvin | 2020-03-05 | Nelson Eichelberger
GMC-01 | GMC-01 | PI14881 | Verified | Clean up the 1C-GMC-SKD-9400; Stator Cooling Water Skid | C | C | Johnny Campbell | McD | 2019-12-24 | Johnny Campbell | Comm | 2020-04-09 | Johnny Campbell | 2020-11-11 | Dave Goldak
GMC-01 | GMC-01 | PI14882 | Verified | Missing U-Bolt at 1C-GMC-V-9468; 1/2" Globe Valve downstream of Deonizer Filter; FLT-9460 | C | P | James Beech | McD | 2019-12-24 | James Beech | Comm | 2020-01-25 | James Beech | 2020-02-02 | Shannon Scott
GMC-01 | GMC-01 | PI14883 | Verified | 1C-GMC-PIC-9440; Instrument Air Pressure Indicator is currently tagged as 1C-GMC-PIC-9440, inside Stator Cooling Water Aux Panel | C | I | Gonzalo Pena | McD | 2019-12-24 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
GMC-01 | GMC-01 | PI14884 | Verified | 1C-GMC-PIC-V-9422, 9421, 9424, 9425, 9426, 9427 have incorrect tags, inside Stator Cooling Water Aux Panel | C | I | Gonzalo Pena | McD | 2019-12-24 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
GMC-01 | GMC-01 | PI14885 | Verified | Trim hose clamps at 1C-GMC-V-V9445A; 1" Instrument Line to 1C-GMC-FE-9445 | C | P | James Beech | McD | 2019-12-24 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-07 | Randy Carpenter
GMC-01 | GMC-01 | PI14886 | Verified | Instrument Air Pressure Regulator to 1C-FI-9497; Flow Meter is not shown on Mitsubishi Drawing 1KC004735; Diagram Stator Cooling Water System | C | P | Kelvin Cook | McD | 2019-12-24 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-07-28 | Keith Pollock
GMC-01 | GMC-01 | PI14887 | Verified | Clean out 1C-GMC-CP-9400; Stator Cooling Water Aux Panel | C | C | Jonathan Donham | McD | 2019-12-24 | Jonathan Donham | Comm | 2020-02-27 | Fred Michael | 2020-04-06 | Bernard Stasse
GMC-01 | GMC-01 | PI14888 | Verified | YIV1 Storage Tank Vent orrifice is not shown on Mitsubishi Drawing 1KC004735; Diagram Stator Cooling Water System | C | P | Kelvin Cook | McD | 2019-12-24 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-06 | Bernard Stasse
GMC-01 | GMC-01 | PI14889 | Verified | 1C-GMC-CP-9400; Stator Cooling Water Aux Panel cable termination box needs phenolic label | C | E | Chris Colvin | McD | 2019-12-24 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-06 | Bernard Stasse
GMC-01 | GMC-01 | PI14890 | Verified | Tubing boots on top of 1C-GMC-RAK-9400; Generator Stator Cooling Water Measuring Rak are open, need to be sealed | C | I | Gonzalo Pena | McD | 2019-12-24 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
GMC-01 | GMC-01 | PI14891 | Open | Does 1/2" instrument lines to 1C-GMC-RAK-9400; Generator Stator Cooling Water Measuring Rak require insulation; YFLA, YFLB,YG6, YG7, YG8A/ | C | C | Richard McSpadden | PCI | 2019-12-24 | Richard McSpadden | Comm
GMC-01 | GMC-01 | PI14892 | Verified | Ladder at East side of 1C-GMC-SKD-9400; Stator Cooling Water Skid rusted, needs cold gal | C | S | Tim Gallegos | McD | 2019-12-24 | Tim Gallegos | Comm | 2020-04-29 | Tim Gallegos | 2020-07-10 | Dave Goldak
GMC-01 | GMC-01 | PI14893 | Verified | Replace twisted metal wire used for tagging inside 1C-GMC-RAK-9400; Generator Stator Cooling Water Measuring Rak with wire rope | C | I | Gonzalo Pena | McD | 2019-12-24 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
GMC-01 | GMC-01 | PI14894 | Verified | 1C-GMC-V-9497 valve inside 1C-GMC-RAK-9400 Stator Cooling Water Aux Panel is not on Toshiba Drawing 1KC004735; Diagram Stator Cooling Water System, also missing knob | C | P | Charles Worthington | McD | 2019-12-24 | Charles Worthington | Comm | 2020-06-10 | Charles Worthington | 2020-07-28 | Keith Pollock
GMC-01 | GMC-01 | PI14895 | Verified | Seal crack in concrete between 1C-GMC-RAK-9400; Generator Stator Cooling Water Measuring RAK foundation and STG pedestal | C | C | Alan Huntsman | McD | 2019-12-24 | Alan Huntsman | Comm | 2020-02-20 | Alan Huntsman | 2020-04-06 | Bernard Stasse
GMC-01 | GMC-01 | PI14896 | Verified | Seal conduit penetrations at 1C-GMC-RAK-9400; Generator Stator Cooling Water Measuring RAK | C | E | Tim Gallegos | McD | 2019-12-24 | Tim Gallegos | Comm | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
GMC-01 | GMC-01 | PI14897 | Verified | Cold gal all Stator Cooling piping supports on STG Bldg mezzaine as necessary | C | C | Johnny Campbell | McD | 2019-12-24 | Johnny Campbell | Comm | 2020-04-08 | Johnny Campbell | 2020-07-10 | Dave Goldak
GMC-01 | GMC-01 | PI14898 | Verified | Missing hose clamp on SS flashing, at YFLA 1/2" High Pressure Flow Orrifice Feeder line, at penetration through grating, STG Bldg mezzanine | C | P | James Beech | McD | 2019-12-24 | James Beech | Comm | 2020-01-25 | James Beech | 2020-02-02 | Shannon Scott
GMC-01 | GMC-01 | PI16201 | Verified | 1C-GMC-M-9400A & 1C-GMC-M-9400B - Need guard around the packing gland for rotating equipment | B | M | Shane Crowe | McD | 2020-01-20 | Shane Crowe | Comm | 2020-01-31 | Shane Crowe | 2020-02-10 | Shannon Scott
GMC-01 | GMC-01 | PI17843 | Verified | There's a broken condulet on the 1C Stator Cooling Water System. | C | E | Chris Colvin | McD | 2020-03-16 | Chris Colvin | Const | 2020-04-06 | Michael Law | 2020-07-28 | Keith Pollock
GMS-01 | GMS-01 | PI13229 | Verified | Thyristor building - HVAC to complete and louvers missing | A | E | Mike Tabbert | McD | 2019-11-20 | Mike Tabbert | Const |  |  | 2020-01-08 | Mike Tabbert
GMS-01 | GMS-01 | PI13228 | Verified | Thyristor building - to address leaking issues | B | C | Alan Huntsman | McD | 2019-11-20 | Alan Huntsman | Const | 2020-02-27 | Michael Law | 2020-02-27 | Michael Law
GMS-01 | GMS-01 | PI13230 | Verified | Thyristor building - Power up the building | B | E | Mike Tabbert | McD | 2019-11-20 | Mike Tabbert | Const |  |  | 2020-01-20 | Mike Tabbert
GMS-01 | GMS-01 | PI13231 | Verified | Thyristor building - Need general housekeeping | A | E | Chris Colvin | McD | 2019-11-20 | Chris Colvin | Const | 2019-12-18 | Fred Michael | 2019-12-18 | Fred Michael
GMS-01 | GMS-01 | PI13377 | Verified | Cable tray from thyristor building | B | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-12-07 | Michael Law
GMS-01 | GMS-01 | PI14765 | Verified | 1C-EXS-XFM-9000 to torque after Hi-pot | B | E | Jonathan Donham | McD | 2019-12-14 | Jonathan Donham | Const |  |  | 2020-01-29 | Fred Michael
GMS-01 | GMS-01 | PI14766 | Verified | 1C-EXS-XFM-9000 remove all shipping protection | A | P | Kelvin Cook | McD | 2019-12-14 | Kelvin Cook | Const | 2020-01-07 | Tim Gallegos | 2020-01-21 | Mike Tabbert
GMS-01 | GMS-01 | PI14767 | Verified | Weld the XFM to the base plates | A | P | Kelvin Cook | McD | 2019-12-14 | Kelvin Cook | Const | 2020-01-06 | Tim Gallegos | 2020-01-08 | Mike Tabbert
GMS-01 | GMS-01 | PI14768 | Verified | 1C-GMS-TB-9000 clean the panel | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2019-12-18 | Fred Michael | 2019-12-20 | Mike Tabbert
GMS-01 | GMS-01 | PI14770 | Verified | Backside panel of EXS XFM install correct hardware on the terminations | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const |  |  | 2020-01-22 | Mike Tabbert
GMS-01 | GMS-01 | PI14771 | Verified | Backside panel of EXS XFM shields need to get made up | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2020-02-10 | Mike Tabbert | 2020-02-10 | Mike Tabbert
GMS-01 | GMS-01 | PI14772 | Verified | Clean the area of EXS XFM | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const |  |  | 2019-12-17 | Fred Michael
GMS-01 | GMS-01 | PI14773 | Verified | Seal all penetrations on all cable entry points | C | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2020-04-08 | Chris Colvin | 2020-04-21 | Michael Law
GMS-01 | GMS-01 | PI14774 | Verified | Adaptor for the sample drain line to handover to Entergy | C | E | Mike Tabbert | McD | 2019-12-14 | Mike Tabbert | Const | 2020-02-21 | Mike Tabbert | 2020-03-09 | Michael Law
GMS-01 | GMS-01 | PI14775 | Verified | Need to put braid between isophase bus and XFM - scaff req'd | B | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const |  |  | 2020-01-21 | Mike Tabbert
GMS-01 | GMS-01 | PI14776 | Verified | Braids to be installed at generator end | B | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2020-02-10 | Fred Michael | 2020-02-17 | Mike Tabbert
GMS-01 | GMS-01 | PI14777 | Verified | Complete the heaters on the isophase bus | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2019-12-18 | Fred Michael | 2020-01-16 | Michael Law
GMS-01 | GMS-01 | PI14778 | Verified | Downspout and evesdrop to install at THY building | C | C | Tim Gallegos | McD | 2019-12-14 | Tim Gallegos | Const | 2020-05-26 | Tim Gallegos | 2020-06-01 | Mike Tabbert
GMS-01 | GMS-01 | PI14779 | Verified | Missing permanent cable tray support to install between EXS XFM and THY building | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2019-12-18 | Fred Michael | 2019-12-18 | Fred Michael
GMS-01 | GMS-01 | PI14780 | Verified | Seal off cable penetration to EXS-XFM | C | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const |  |  | 2020-02-02 | Fred Michael
GMS-01 | GMS-01 | PI14781 | Verified | Complete HVAC on THY building | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const |  |  | 2020-01-02 | Mike Tabbert
GMS-01 | GMS-01 | PI14782 | Verified | Seal all cable entry points at THY building | C | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const |  |  | 2020-02-02 | Fred Michael
GMS-01 | GMS-01 | PI14783 | Verified | Finish grounding on all cabinets at THY building | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2019-12-18 | Fred Michael | 2019-12-18 | Fred Michael
GMS-01 | GMS-01 | PI14784 | Verified | Install all the fans inside the cabinets at THY building | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2019-12-18 | Fred Michael | 2019-12-18 | Fred Michael
GMS-01 | GMS-01 | PI14785 | Verified | Heat detector device to install, need wire and conduit | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const |  |  | 2020-01-03 | Mike Tabbert
GMS-01 | GMS-01 | PI14786 | Verified | Cable scoping to check with Randy Carpenter. In GSN is 78. As per scope drawing is 67. | B | E | Mike Tabbert | McD | 2019-12-14 | Mike Tabbert | Const |  |  | 2020-02-19 | Michael Law
GMS-01 | GMS-01 | PI14787 | Verified | THY power panel to remove temporary power and install permanent power, with panel schedule | B | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2020-01-15 | Michael Law | 2020-01-15 | Mike Tabbert
GMS-01 | GMS-01 | PI14788 | Verified | Verify all braids and install as per comm advise | B | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2020-01-15 | Michael Law | 2020-01-15 | Mike Tabbert
GMS-01 | GMS-01 | PI14789 | Verified | 1C-GMS-CUB-9020 © tighten all hold down bolts | B | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-04-21 | Michael Law
GMS-01 | GMS-01 | PI14790 | Verified | Finish the connection of NGR to the generator | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const |  |  | 2020-02-07 | Mike Tabbert
GMS-01 | GMS-01 | PI14791 | Verified | Install flex grounds on excitation building | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const |  |  | 2019-12-20 | Mike Tabbert
GMS-01 | GMS-01 | PI14792 | Verified | Monitor VTSA cubicle for water penetration | C | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2020-02-24 | Mike Tabbert | 2020-02-24 | Mike Tabbert
GMS-01 | GMS-01 | PI14793 | Verified | Finish grounding on NGR and generator side isophase | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2020-01-15 | Chris Colvin | 2020-01-21 | Michael Law
GMS-01 | GMS-01 | PI14794 | Verified | Install proper grounding on the generator | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2020-01-15 | Chris Colvin | 2020-01-28 | Fred Michael
GMS-01 | GMS-01 | PI14795 | Verified | Install proper grounding on the collector cabinet | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const | 2020-02-21 | Chris Colvin | 2020-02-21 | Mike Tabbert
GMS-01 | GMS-01 | PI14796 | Verified | Need housekeeping at the collector cabinet | A | E | Chris Colvin | McD | 2019-12-14 | Chris Colvin | Const |  |  | 2019-12-18 | Fred Michael
GMS-01 | GMS-01 | PI14825 | Verified | 1CGMSK0005, Pull Cable | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2020-01-02 | Mike Tabbert
GMS-01 | GMS-01 | PI14826 | Verified | 1CGMSK0011, Pull Cable | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2020-01-02 | Mike Tabbert
GMS-01 | GMS-01 | PI14827 | Verified | 1CSTSJ0001, Pull Cable | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
GMS-01 | GMS-01 | PI14828 | Verified | 1CEXSC0003, From Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
GMS-01 | GMS-01 | PI14829 | Verified | 1CEXSC0005, From Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2020-01-04 | Mike Tabbert
GMS-01 | GMS-01 | PI14830 | Verified | 1CEXSC0007, From Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2020-01-04 | Mike Tabbert
GMS-01 | GMS-01 | PI14831 | Verified | 1CGMSK0001, From Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
GMS-01 | GMS-01 | PI14832 | Verified | 1CGMSK0005, From Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2020-01-02 | Mike Tabbert
GMS-01 | GMS-01 | PI14833 | Verified | 1CGMSK0007, From Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
GMS-01 | GMS-01 | PI14834 | Verified | 1CGMSK0011, From Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
GMS-01 | GMS-01 | PI14835 | Verified | 1CGMSK0014, From Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
GMS-01 | GMS-01 | PI14836 | Verified | 1CSTSJ0001, From Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
GMS-01 | GMS-01 | PI14837 | Verified | 1CSTSK0022, From Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
GMS-01 | GMS-01 | PI14838 | Verified | 1CSTSK0023, From Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2020-01-04 | Mike Tabbert
GMS-01 | GMS-01 | PI14839 | Verified | 1CGMSK0001, To Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
GMS-01 | GMS-01 | PI14840 | Verified | 1CGMSK0005, To Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
GMS-01 | GMS-01 | PI14841 | Verified | 1CGMSK0007, To Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
GMS-01 | GMS-01 | PI14842 | Verified | 1CGMSK0011, To Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
GMS-01 | GMS-01 | PI14843 | Verified | 1CGMSK0014, To Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
GMS-01 | GMS-01 | PI14844 | Verified | 1CSTSC0014, To Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2020-01-04 | Mike Tabbert
GMS-01 | GMS-01 | PI14845 | Verified | 1CSTSJ0001, To Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
GMS-01 | GMS-01 | PI14846 | Verified | 1CSTSK0010, To Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2020-01-02 | Mike Tabbert
GMS-01 | GMS-01 | PI14847 | Verified | 1CSTSK0023, To Termination | A | E | Chris Colvin | McD | 2019-12-16 | Chris Colvin | Const |  |  | 2020-01-04 | Mike Tabbert
GMS-01 | GMS-01 | PI15009 | Verified | Clean up inside 1C-GMS-CP-9010, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-06 | Bernard Stasse
GMS-01 | GMS-01 | PI15010 | Verified | Seal cable floor penetrations inside 1C-GMS-CP-9010, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-03-05 | Nelson Eichelberger
GMS-01 | GMS-01 | PI15011 | Verified | 50 OHM BNC Terminator missing at 1C-GMS-CP-9010, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
GMS-01 | GMS-01 | PI15012 | Verified | Replace wiring duct covers inside 1C-GMS-CP-9010, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-06 | Bernard Stasse
GMS-01 | GMS-01 | PI18018 | Verified | 1C-NQS-IPB-0001 - At St. Charles, there was a condensation issue in the generator isophase buses. It would be helpful if there was a common header connecting all three isophases with a drain valve in case condensation were to build up. At SCPS, they connected instrument air to the drains with a low pressure regulator to keep dry air in and to prevent condensation buildup. | D | E | Charles Worthington | McD | 2020-03-17 | Charles Worthington | Comm | 2020-04-28 | Michael Law | 2021-01-05 | Keith Pollock
GND-01 | GND-01 | PI12492 | Verified | Drawing: 10-322-PL-EE-GND-0002, 4/0 coil of cable above grade southeast of 1A control package along south road, cable to be buried at correct depth and connected to grid. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-05 | Scott Davis | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12493 | Verified | Drawing: 10-322-PL-EE-GND-0002, 4/0 ground tail stubbed-up on south end of 1A control package not attached. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brandy Roy | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12494 | Verified | Drawing: 10-322-PL-EE-GND-0002, At 1A control package, northeast corner there is a ground tail as per drawing, but there is no platform column, remove ground tail and seal stub-up location. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12495 | Verified | Drawing: 10-322-PL-EE-GND-0002, Ground bus installed at north end of 1A control package needs to be reworked, insulated and uninsulated ground tails are landed on bus. There is no call for the bus, utilize the grounds per drawing and spare the rest. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12496 | Verified | Drawing: 10-322-PL-EE-GND-0002, Any grounds that have been run on the surface of the concrete that create a tripping hazard need to reworked as per engineering direction. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2020-02-11 | Mike Tabbert
GND-01 | GND-01 | PI12497 | Verified | Drawing: 10-322-PL-EE-GND-0002, Seal all ground cable penetrations (1" PVC Conduit in Fondation) | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12498 | Verified | Drawing: 10-322-PL-EE-GND-0001, 4/0 coil of cable above grade on west side of manhole 10, cable to buried at correct depth and tied to grid. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12499 | Verified | Drawing: 10-322-PL-EE-GND-0001, Ground insert not installed east of manhole 10. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12500 | Verified | Drawing: 10-322-PL-EE-GND-0001, Any grounds that have been run on the surface of the concrete that create a tripping hazard need to reworked as per engineering direction. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2020-02-11 | Mike Tabbert
GND-01 | GND-01 | PI12501 | Verified | Drawing: 10-322-PL-EE-GND-0001, Seal all ground cable penetrations (1" PVC Conduit in Fondation) | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12502 | Verified | Drawing: 1A-411-PL-EE-GND-0002, 12 ground tails on this drawing not attached, see marked-up drawing. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-20 | Mike Tabbert
GND-01 | GND-01 | PI12503 | Verified | Drawing: 1A-411-PL-EE-GND-0002, 4/0 coil of cable above grade east of GT Lube Oil Enclosure, cable to buried at correct depth and tied into grid. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-18 | Fred Michael
GND-01 | GND-01 | PI12504 | Verified | Drawing: 1A-411-PL-EE-GND-0002, Ground tail on north east of lube oil enclosure grounded to stairway, should be to lube oil enclosure. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12505 | Verified | Drawing: 1A-411-PL-EE-GND-0002, 4/0 ground stub-up east of GT enclosure, no structure or equipment near, spare or remove. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-18 | Fred Michael
GND-01 | GND-01 | PI12506 | Verified | Drawing: 1A-411-PL-EE-GND-0002, Complete generator 1A grounding. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12507 | Verified | Drawing: 1A-411-PL-EE-GND-0002, Unable to locate ground tails in turbine pedestals inside enclosure. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-18 | Fred Michael
GND-01 | GND-01 | PI12508 | Verified | Drawing: 1A-411-PL-EE-GND-0002, Vent fan grounds not installed. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-18 | Fred Michael
GND-01 | GND-01 | PI12509 | Verified | Drawing: 1A-411-PL-EE-GND-0002, Any grounds that have been run on the surface of the concrete that create a tripping hazard need to reworked as per engineering direction. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-18 | Fred Michael
GND-01 | GND-01 | PI12510 | Verified | Drawing: 1A-411-PL-EE-GND-0002, Seal all ground cable penetrations (1" PVC Conduit in Fondation) | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12511 | Verified | Drawing: 1A-411-PL-EE-GND-0001,Complete Generator grounding. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12512 | Verified | Drawing: 1A-411-PL-EE-GND-0001, Ground not attached northeast corner of oily waste sump | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12513 | Verified | Drawing: 1A-411-PL-EE-GND-0001, Ground inserts and tails not installed on west and east side of oily water sump, see marked-up drawing. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12514 | Verified | Drawing: 1A-411-PL-EE-GND-0001, Six tails stubbed up for IPB connection, IPB is single point ground and these tails will not be used, spare them in place. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12515 | Verified | Drawing: 1A-411-PL-EE-GND-0001, Ground cable between 1A GT Purge Air and Turbine enclosure needs to be protected and supported. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Albert Burge | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12516 | Verified | Drawing: 1A-411-PL-EE-GND-0001, Unable to locate ground tails in Gas Turbine pedestals, loacte and confirm installation. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-22 | Mike Tabbert
GND-01 | GND-01 | PI12517 | Verified | Drawing: 1A-411-PL-EE-GND-0001, Rework all ground cables that have been bent out of shape, had the supports removed due to grout installation. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-19 | Fred Michael | 2019-12-19 | Fred Michael
GND-01 | GND-01 | PI12518 | Verified | Drawing: 1A-411-PL-EE-GND-0001, Any grounds that have been run on the surface of the concrete that create a tripping hazard need to reworked as per engineering direction. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-17 | Fred Michael
GND-01 | GND-01 | PI12519 | Verified | Drawing: 1A-411-PL-EE-GND-0001, Seal all ground cable penetrations (1" PVC Conduit in Fondation) | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12520 | Verified | Drawing: 1A-111-PL-EE-GND-0002, Five ground tails are not attached, see marked-up drawing. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-18 | Fred Michael
GND-01 | GND-01 | PI12521 | Verified | Drawing: 1A-111-PL-EE-GND-0002, Ground inserts not installed at HRSG blowdown sump, tails will need to be tied to grid to ground sump cover. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12522 | Verified | Drawing: 1A-111-PL-EE-GND-0002, Ground insert not installed on east side of unit A stack. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12523 | Verified | Drawing: 1A-111-PL-EE-GND-0002, 4/0 ground grid cable is above grade on north side of blowdown sump, bury cable to correct depth. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12524 | Verified | Drawing: 1A-111-PL-EE-GND-0002, Cable tails stubbed-up at duct burner skid need to be routed up to duct burner skid and attached. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12525 | Verified | Drawing: 1A-111-PL-EE-GND-0002, Any grounds that have been run on the surface of the concrete that create a tripping hazard need to reworked as per engineering direction. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2020-01-15 | Mike Tabbert
GND-01 | GND-01 | PI12526 | Verified | Drawing: 1A-111-PL-EE-GND-0002, Seal all ground cable penetrations (1" PVC Conduit in Fondation) | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12527 | Verified | Drawing: 1A-111-PL-EE-GND-0001, Five ground tails not attached to equipment. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-17 | Fred Michael
GND-01 | GND-01 | PI12528 | Verified | Drawing: 1A-111-PL-EE-GND-0001, Ground tail on west side of Unit A stack meant to be for ladder ground, rerout this cable to ladder and attach. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12529 | Verified | Drawing: 1A-111-PL-EE-GND-0001, Ground tail at fuel gas scrubber not attached to tank. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12530 | Verified | Drawing: 1A-111-PL-EE-GND-0001, Three 4/0 cable coils laying above grade on west side of stack, cables to be buried to correct depth and connected to grid. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12531 | Verified | Drawing: 1A-111-PL-EE-GND-0001, Rework all ground tails that have been bent out of shape, had the supports removed due to equipment grouting. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-20 | Mike Tabbert
GND-01 | GND-01 | PI12532 | Verified | Drawing: 1A-111-PL-EE-GND-0001, Any grounds that have been run on the surface of the concrete that create a tripping hazard need to reworked as per engineering direction. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-17 | Fred Michael
GND-01 | GND-01 | PI12533 | Verified | Drawing: 1A-111-PL-EE-GND-0001, Seal all ground cable penetrations (1" PVC Conduit in Fondation) | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12534 | Verified | Drawing: 10-323-PL-EE-GND-0002, Coils of 4/0 cable above grade, south and southwest of 1B control Building, 500 MCM cable above grade east of switchyard 1A, bury cable to correct depth and reconnect to grid. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12535 | Verified | Drawing: 10-323-PL-EE-GND-0002, Lightning protection ground cable is connected to ground insert on concrete columns (4 corners), remove and tie into lightning protection down comer when installed. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12536 | Verified | Drwaing: 10-323-PL-EE-GND-0002, Lightining protection down comers not installed. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2020-02-11 | Mike Tabbert
GND-01 | GND-01 | PI12537 | Verified | Drawing: 10-323-PL-EE-GND-0002, On north end of 1B Control Building a bus bar has been installed and insulated and uninsulated ground grid cables have been landed, this needs to be removed and grounds seperated. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12538 | Verified | Drawing: 10-323-PL-EE-GND-0002, Column grounds not attached to columns north of 1B control Building. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12539 | Verified | Drawing: 10-323-PL-EE-GND-0002, Any grounds that have been run on the surface of the concrete that create a tripping hazard need to reworked as per engineering direction. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2020-02-11 | Mike Tabbert
GND-01 | GND-01 | PI12540 | Verified | Drawing: 10-323-PL-EE-GND-0002, Seal all ground cable penetrations (1" PVC Conduit in Fondation) | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12541 | Verified | Drawing: 10-323-PL-EE-GND-0001, Tie ground insert to excitation transformer northeast corner. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12542 | Verified | Drawing: 10-323-PL-EE-GND-0001, Any grounds that have been run on the surface of the concrete that create a tripping hazard need to reworked as per engineering direction. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2020-01-15 | Mike Tabbert
GND-01 | GND-01 | PI12543 | Verified | Drawing: 10-323-PL-EE-GND-0001, Seal all ground cable penetrations (1" PVC Conduit in Fondation) | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12544 | Verified | Drawing: 1B-421-PL-EE-GND-0002, grounds not attached refer to marked-up drawing. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2020-01-15 | Mike Tabbert
GND-01 | GND-01 | PI12545 | Verified | Drawing: 1B-421-PL-EE-GND-0002, Seven 4/0 cable coils above grade on east side of 1B lube oil and gas turbine, refer to marked-up drawing. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12546 | Verified | Drawing: 1B-421-PL-EE-GND-0002, Ground tail on northeast corner of aux building tied to stairway, needs to tie to aux building. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12547 | Verified | Drawing: 1B-421-PL-EE-GND-0002, Complete Unit 1B Generator Grounding. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12548 | Verified | Drawing: 1B-421-PL-EE-GND-0002, grounding has been completed in several areas but civil has removed supports and deformed cable in order to place grout, replace supports and reform cable. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2020-01-15 | Mike Tabbert
GND-01 | GND-01 | PI12549 | Verified | Drawing: 1B-421-PL-EE-GND-0002, Unable to locate grounds in turbine enclosure at support pedestals. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-17 | Fred Michael
GND-01 | GND-01 | PI12550 | Verified | Drawing: 1B-421-PL-EE-GND-0002, Any grounds that have been run on the surface of the concrete that create a tripping hazard need to reworked as per engineering direction. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2020-02-11 | Mike Tabbert
GND-01 | GND-01 | PI12551 | Verified | Drawing: 1B-421-PL-EE-GND-0002, Seal all ground cable penetrations (1" PVC Conduit in Fondation) | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12552 | Verified | Drawing: 1B-421-PL-EE-GND-0001, Complete Unit 1B Generator Grounding. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12553 | Verified | Drawing: 1B-421-PL-EE-GND-0001, 4/0 ground tail above grade north of 1B oily waste sump. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12554 | Verified | Drawing: 1B-421-PL-EE-GND-0001, Grounds not attached at oil water sump, tails and inserts not installed on west side. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12555 | Verified | Drawing: 1B-421-PL-EE-GND-0001, Unable to locate grounds in turbine enclosure at support pedestals. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12556 | Verified | Drawing: 1B-421-PL-EE-GND-0001, Six grounds for IPB will not be used as we have single point grounding, dress up ground tails at grade elevation. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12557 | Verified | Drawing: 1B-421-PL-EE-GND-0001, Refer to marked-up drawing for grounds not installed. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2020-02-12 | Mike Tabbert
GND-01 | GND-01 | PI12558 | Verified | Drawing: 1B-421-PL-EE-GND-0001, Grounding has been completed in several areas but civil has removed supports and deformed cable in order to place grout, replace supports and reform cable. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12559 | Verified | Drawing: 1B-421-PL-EE-GND-0001, Any grounds that have been run on the surface of the concrete that create a tripping hazard need to reworked as per engineering direction. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-17 | Fred Michael
GND-01 | GND-01 | PI12560 | Verified | Drawing: 1B-421-PL-EE-GND-0001, Seal all ground cable penetrations (1" PVC Conduit in Fondation) | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12561 | Verified | Drawing: 1B-121-PL-EE-GND-0002, Ground tail for ladder just northwest of blowdown tank in wrong spot may need to cut trench in concrete. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-18 | Fred Michael
GND-01 | GND-01 | PI12562 | Verified | Drawing: 1B-121-PL-EE-GND-0002, Ground tails for duct burner skid to be run up support steel and tied into duct burner skid. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12563 | Verified | Drawing: 1B-121-PL-EE-GND-0002, Ground tails not attached refer to marked-up drawing. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2020-01-15 | Mike Tabbert
GND-01 | GND-01 | PI12564 | Verified | Drawing: 1B-121-PL-EE-GND-0002, 4/0 cable coil above ground east of duct burner skid. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12565 | Verified | Drawing: 1B-121-PL-EE-GND-0002, Ground grid above grade north side of blowdown sump, three inserts not installed (see marked-up drawing for referance). | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-18 | Fred Michael
GND-01 | GND-01 | PI12566 | Verified | Drawing: 1B-121-PL-EE-GND-0002, Ground tail missing for stair well east end of HRSG PDC. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12567 | Verified | Drawing: 1B-121-PL-EE-GND-0002, Any grounds that have been run on the surface of the concrete that create a tripping hazard need to reworked as per engineering direction. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2020-02-11 | Mike Tabbert
GND-01 | GND-01 | PI12568 | Verified | Drawing: 1B-121-PL-EE-GND-0002, Seal all ground cable penetrations (1" PVC Conduit in Fondation) | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-11-23 | Brad Stanford | 2019-12-05 | Scott Davis
GND-01 | GND-01 | PI12569 | Verified | Drawing: 1B-121-PL-EE-GND-0001, 4/0 ground cable above grade west of 1B Fuel Scrubber, cable to be buried to correct depth. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12570 | Verified | Drawing: 1B-121-PL-EE-GND-0001, 4/0 ground tail above grade south of 1B-NJS-XFM-0005, cable to be exposed, bureid and tied into grid at correct depth. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12571 | Verified | Drawing: 1B-121-PL-EE-GND-0001, The ladder ground on west side of stack has been taken to the stack, this needs to be reworked and the ladder grounded. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12572 | Verified | Drawing: 1B-121-PL-EE-GND-0001, Ground tails not installed at boiler feed water stairs and HRSG 1B PDC, (see marled up drawing. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12573 | Verified | Drawing: 1B-121-PL-EE-GND-0001, ground cable support and protection has been removed for grouting, this needs to be replaced in mutiple locations. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2020-02-11 | Mike Tabbert
GND-01 | GND-01 | PI12574 | Verified | Drawing: 1B-121-PL-EE-GND-0001, Any grounds that have been run on the surface of the concrete that create a tripping hazard need to reworked as per engineering direction. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2020-02-11 | Mike Tabbert
GND-01 | GND-01 | PI12575 | Verified | Drawing: 1B-121-PL-EE-GND-0001, Seal all ground cable penetrations (1" PVC Conduit in Fondation) | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12576 | Verified | Add conduit strap at south end of 1A GT control package under grating. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-20 | Mike Tabbert
GND-01 | GND-01 | PI12577 | Verified | Move isolated ground (touching I-beam) at south end of 1A GT control package. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-18 | Fred Michael | 2019-12-18 | Fred Michael
GND-01 | GND-01 | PI12578 | Verified | Move cable tray ground at south end of 1A GT control package. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-18 | Fred Michael | 2019-12-18 | Fred Michael
GND-01 | GND-01 | PI12579 | Verified | Add conduit support & re-fasten existing ground at the east side of 1A GT control package. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
GND-01 | GND-01 | PI12580 | Verified | Put bolts in all unused embeds. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2020-01-08 | Fred Michael
GND-01 | GND-01 | PI12581 | Verified | Move stairway ground to bottom side - east side of 1A GT. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const | 2019-12-07 | Scott Davis | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12582 | Verified | Re-work all grounds at columns that aren't formed up. Clean & grind existing cad welds & cold galv. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-18 | Fred Michael
GND-01 | GND-01 | PI12583 | Verified | Cut rebar at ground stub-up on the west side of 1A HRSG at Aux. platform (next to GT casing cooling fan). | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12584 | Verified | Unit A FGPA unit - ground embed at southwest corner. Form ground to bldg. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12585 | Verified | Tighten & torque ground bus bar at colum south of 1A seal oil skid. Reverse the bolting so nut is on the outside. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-18 | Fred Michael
GND-01 | GND-01 | PI12586 | Verified | Ground the Unit A bus duct supports (every other support). | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-18 | Fred Michael
GND-01 | GND-01 | PI12587 | Verified | Add conduit strap under the Unit ASFC package & cut down protruding rebar. | B | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12588 | Verified | Add ground for heat trace panel & the stairs at the southeast corner of the 1A BFW bldg. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12589 | Verified | Remove ground on west side of the 1A stack & use for nearby ladder. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12590 | Verified | Ground the 1A stack Aux. platform on the east side. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-07 | Scott Davis
GND-01 | GND-01 | PI12591 | Verified | Ground stairwells on Unit B PDC. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12592 | Verified | Missing embed to grid ground on unit B lube oil enclosure, southwest to southeast. | A | E | Chris Colvin | McD | 2019-10-28 | Chris Colvin | Const |  |  | 2019-12-08 | Scott Davis
GND-01 | GND-01 | PI12703 | Verified | Filter Press stairs - ground cable and PVC conduit is causing trip hazard. | C | E | Chris Colvin | McD | 2019-11-01 | Chris Colvin | Const |  |  | 2019-12-17 | Fred Michael
GND-01 | GND-01 | PI14899 | Verified | Strap down PVC sleeve to concrete on backside of UAT 1B Transformer. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14900 | Verified | Remove ground tail from backside of UAT 1A transformer, unbolt at embed under grading. | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-12 | Mike Tabbert
GND-01 | GND-01 | PI14901 | Verified | Cut and remove 1 hole ground straps & studs in concrete directly beneath buss duct between transformers & cable tray, east side of main PDC. Cold -Gal oxidized cadwelds on columns, clean and torque grounds. | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-12 | Mike Tabbert
GND-01 | GND-01 | PI14902 | Verified | Attach ground tail (existing) beneath grating at northwest corner of main PDC to stair way, 12 foot elevation. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14903 | Verified | Dress up all insulated grounds in a neat and workmanship like manner, at 3 center concrete columns on north end of main PDC. | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-12 | Mike Tabbert
GND-01 | GND-01 | PI14904 | Verified | All duct bank stub-ups at main PDC need sveral of the grounds reattached, clean all pulling lubricant and dirt and forein matter from duct banks and ground cables. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14905 | Verified | Ground stairs and entrance platform at west side Thyristor Building. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
GND-01 | GND-01 | PI14906 | Verified | Ground ISO-Phase support columns on west side of Thyristor Building. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
GND-01 | GND-01 | PI14907 | Verified | 10-CCW-M-0100 A & B Motors, remove existing grounds and split bolts, utilize C-Taps and reinstall ground cables. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14908 | Verified | North stairs at STG ground level, rework grounds to column and hydrogen stub-up, reduce excess cable. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
GND-01 | GND-01 | PI14909 | Verified | Remove and reroute 5 existing column grounds by civil design that are tripping hazards, see electrical engineering or electrical QC for details, STG ground floor. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-04-02 | Mike Tabbert
GND-01 | GND-01 | PI14910 | Verified | In thyristor building, take 4/0 ground from ground bus in AC incoming cub. To ground bar in 1C-STS-CUB-0001. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
GND-01 | GND-01 | PI14911 | Verified | 1C-OMC-RAK-9400, need to remove paint off cabinet were grounds are attached, then Cold Gal area. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-09 | Mike Tabbert
GND-01 | GND-01 | PI14912 | Verified | STG Seal-Oil Skid, Need to remove paint were grounds are attached, coat the area with cold gal. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-09 | Mike Tabbert
GND-01 | GND-01 | PI14913 | Verified | Complete 6-500 MCM ground cables to ground steam turbine and generator. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-10 | Fred Michael
GND-01 | GND-01 | PI14914 | Verified | STG Seal-Oil Skid, need to torque ground connections on skid. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
GND-01 | GND-01 | PI14915 | Verified | Complete six lightning protection going to operator deck. (if requried) | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-11 | Mike Tabbert
GND-01 | GND-01 | PI14916 | Verified | All ground connections on condenser need to be torqued. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-10 | Fred Michael
GND-01 | GND-01 | PI14917 | Verified | Column, L-7, need to strap down PVC conduit. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-09 | Mike Tabbert
GND-01 | GND-01 | PI14918 | Verified | Air Compressors, torque all ground connections. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
GND-01 | GND-01 | PI14919 | Verified | Hydrulic unit, strap ground cable down. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-09 | Mike Tabbert
GND-01 | GND-01 | PI14920 | Verified | Hydralic unit, caulk PVC conduit. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-09 | Mike Tabbert
GND-01 | GND-01 | PI14921 | Verified | Column C-6 cadweld needs to be re-shot. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-10 | Fred Michael
GND-01 | GND-01 | PI14922 | Verified | Column F-7, PVC sleeve is damaged needs to be replaced. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-03-26 | Chris Colvin | 2020-04-03 | Mike Tabbert
GND-01 | GND-01 | PI14923 | Verified | Gland steam exhausters A & B, move ground connections to web of beam. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-11 | Mike Tabbert
GND-01 | GND-01 | PI14924 | Verified | 10-NJS-XFM-0003B, Re-Strap PVC on north end. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14925 | Verified | Ground cable at cooling tower PDC, south side needs to be buried to dorrect depth. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-21 | Mike Tabbert
GND-01 | GND-01 | PI14926 | Verified | Cooling tower PDC, dress up spare insulated grounds on north side. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14927 | Verified | Cooling Tower PDC, tie insulated grounds to ground grid, north side. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14928 | Verified | Cooling Tower PDC, Ne corner, dress up stub up at cable tray ground. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14929 | Verified | Cooling tower PDC, 10-NJS-XFM-0003B, south of transformer need to bury ground cable at correct depth. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-21 | Mike Tabbert
GND-01 | GND-01 | PI14930 | Verified | Cooling tower chemical feed, ground sodium hypochlorite tank hold down clamps. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
GND-01 | GND-01 | PI14931 | Verified | 10-NJS-PNL-0007, need to support PVC ground sleeve. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14932 | Verified | Column NE of sodium hypochlrite tank, ground column to embed. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
GND-01 | GND-01 | PI14933 | Verified | Column NW of sulfuric Acid Tank needs to be grounded. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
GND-01 | GND-01 | PI14934 | Verified | Install retractable truck grounding cable to north side of chemical feed, tie to embed. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-12 | Mike Tabbert
GND-01 | GND-01 | PI14935 | Verified | Cooling tower circulation motors, need to ground motors to the grid ground and tie duct bank grounds to the grid ground. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14936 | Verified | North of HRSG PDC 1B and north of road, ground cable needs to be tied back to grid and buried to correct depth. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14937 | Verified | Top of cooling tower, need to disconnect control panel ground from lightining protection cable and reconnect to ground grid, fans J, H and D. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14938 | Verified | Top of cooling tower , Motor E needs connected to lighting protection cable. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14939 | Verified | South west of hydrogen storage tank, ground cable needs to be buried to correct depth. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-13 | Fred Michael
GND-01 | GND-01 | PI14940 | Verified | Hydrogen storage area, seal ground cable penetrations. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-12 | Mike Tabbert
GND-01 | GND-01 | PI14941 | Verified | South of demineralized water tank, bury ground cable to correct depth. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
GND-01 | GND-01 | PI14942 | Verified | Drawing 10-900-PL-EE-GND-0001, Clean up ground connection northwest corner of storage tank and cold gal | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-13 | Fred Michael
GND-01 | GND-01 | PI14943 | Verified | Drawing 10-900-PL-EE-GND-0001, Ground tail stubed-up at light pole, complete this installation. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-02-27 | Chris Colvin | 2020-03-02 | Mike Tabbert
GND-01 | GND-01 | PI14944 | Verified | Drawing 10-530-PL-EE-GND-0004, Need ground connection to stairs east side of Clarifier. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-16 | Mike Tabbert
GND-01 | GND-01 | PI14945 | Verified | Drawing 10-530-PL-EE-GND-0004, Need two hole lugs on sludge pump transfer pump and skid. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-12 | Mike Tabbert
GND-01 | GND-01 | PI14946 | Verified | Drawing 10-530-PL-EE-GND-0004, Tails to be connected to hold downs on sludge tank. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-16 | Mike Tabbert
GND-01 | GND-01 | PI14947 | Verified | Drawing 10-530-PL-EE-GND-0004, Connect ground to east sump motor. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-16 | Mike Tabbert
GND-01 | GND-01 | PI14948 | Verified | Drawing 10-530-PL-EE-GND-0004, Sodium Hydroxide Storage Tank, seal ground penetrations. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
GND-01 | GND-01 | PI14949 | Verified | Drawing 10-530-PL-EE-GND-0004, Sodium Hydroxide Storage Tank, Support PVC conduit used as ground raceway at northeast corner. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-16 | Mike Tabbert
GND-01 | GND-01 | PI14950 | Verified | Drawing 10-530-PL-EE-GND-0004, Sodium Hydroxide Storage Tank, ground ladder at northeast corner. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
GND-01 | GND-01 | PI14951 | Verified | Drawing 10-530-PL-EE-GND-0004, Ground caustic feed pump skid. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
GND-01 | GND-01 | PI14952 | Verified | Drawing 10-530-PL-EE-GND-0004, Sodium Hydroxide Storage Tank, Ground hold down clamps. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
GND-01 | GND-01 | PI14953 | Verified | Drawing: 10-600-PL-EE-GND-0002, Grounding to be completed in manhole northwest corner of control building. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-02-18 | Chris Caywood | 2020-02-19 | Mike Tabbert
GND-01 | GND-01 | PI14954 | Verified | Drawing: 10-003-PL-EE-GND-0001, One ground attached only to motor, motor base requires ground grid connection. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14955 | Verified | Drawing: 10-003-PL-EE-GND-0001, Rework grounds to attach to skid not anchor bolts, 10-RWS-M-0200A and 10-RWS-M-200B. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14956 | Verified | Drawing: 10-003-PL-EE-GND-0001, Tank ladder not grounded, tank hold downs not grounded. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14957 | Verified | Drawing: 10-003-PL-EE-GND-0001, Ground cable is creating a tripping hazard inside building at west door, cable should be trenched into concrete. | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-04-14 | Chris Colvin | 2020-04-21 | Mike Tabbert
GND-01 | GND-01 | PI14958 | Verified | Drawing: 10-004-PL-EE-GND-0003, Ground tail above grade, north of waste water system. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-12 | Mike Tabbert
GND-01 | GND-01 | PI14959 | Verified | Drawing: 10-004-PL-EE-GND-0003, Marked-up drawing has been highlighted to show ground grid that has not been installed, complete ground grid installation and highlight drawing. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-02-20 | Chris Colvin | 2020-02-20 | Mike Tabbert
GND-01 | GND-01 | PI14960 | Verified | Drawing: 10-004-PL-EE-GND-0002, Ground rod above grade west of west road, complete installation in this area. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-12 | Mike Tabbert
GND-01 | GND-01 | PI14961 | Verified | Drawing: 10-004-PL-EE-GND-0002, Marked-up drawing has been highlighted to show ground grid that has not been installed, complete grid installation and highlight drawing. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-12 | Mike Tabbert
GND-01 | GND-01 | PI14962 | Verified | Drawing: 10-004-PL-EE-GND-0001, Marked-up drawing has been highlighted to show ground grid that has not been installed, complete grid installation and highlight drawing. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-12 | Mike Tabbert
GND-01 | GND-01 | PI14963 | Verified | Drawing: 10-600-PL-EE-GND-0003, Marked-up drawing has been highlighted to show ground grid that has not been installed, complete grid installation and highlight drawing. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-12 | Mike Tabbert
GND-01 | GND-01 | PI14964 | Verified | Drawing: 10-600-PL-EE-GND-0001, Marked-up drawing has been highlighted to show ground grid that is not installed, complete grid installation and highlight drawing. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-12 | Mike Tabbert
GND-01 | GND-01 | PI14965 | Verified | Drawing: LK-10-900-PL-EE-GND-0002, Marked-up drawing has been highlighted to show ground grid that has not been installed, grid to be installed and drawing highlighted. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-09 | Mike Tabbert
GND-01 | GND-01 | PI14966 | Verified | Drawing: 10-530-PL-EE-GND-0004, Seal all PVC conduit penetrations thru concrete floor of polymer metering enclosure. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14967 | Verified | Drawing: 10-530-PL-EE-GND-0004, Repair ground tail PVC conduit at panel 10-MWS-CP-0310, south side exterior of polymer metering enclosure building. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-16 | Mike Tabbert
GND-01 | GND-01 | PI14968 | Verified | Drawing: 10-530-PL-EE-GND-0004, All grounding to hypochlorite coagulant vessel containment area south of polymer enclosure building needs to be properly reworked and formed to steel columns. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
GND-01 | GND-01 | PI14969 | Verified | Drawing: 10-530-PL-EE-GND-0004, Ground hold down clamps for vessels on interior of containment area for hypochlorite and coagulant tanks. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14970 | Verified | Drawing: 10-530-PL-EE-GND-0004, Repiar ground on top of divder wall between hypochlorite and coagulant containment. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14971 | Verified | Drawing: 10-530-PL-EE-GND-0004, Support columns for grating and 2 each ladders need grounded to embeds below elevated platforms. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14972 | Verified | Drawing: 10-530-PL-EE-GND-0004, Ground all grating support steel on top of claifier to embeds. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-02-20 | Chris Colvin | 2020-02-20 | Mike Tabbert
GND-01 | GND-01 | PI14973 | Verified | Drawing: 10-530-PL-EE-GND-0003, Strighten/Rework ground and PVC stub-up on south side of transformer pad (fire pump house XFM) | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14974 | Verified | Drawing: 10-530-PL-EE-GND-0003, Seal all PVC ground tail stub-ups at fire pump transformer pad. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14975 | Verified | Drawing: 10-530-PL-EE-GND-0003, Seal all conduit stub-ups thru interior floor of both north and south entrance doors on fire water pump house. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14976 | Verified | Drawing: 10-530-PL-EE-GND-0003, Locate at grid and install ground tail on ext south east side of fire-water pump house. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-16 | Mike Tabbert
GND-01 | GND-01 | PI14977 | Verified | Drawing: 10-530-PL-EE-GND-0003, Ground fuel control panel box mounted on exterior wall, west side of fire water pump house. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14978 | Verified | Drawing: 10-530-PL-EE-GND-0001, Install Ground to ladder that access's grading plateform to oil-water separator horizontal tank 10-OWS-CP-0010. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
GND-01 | GND-01 | PI14979 | Verified | Drawing: 10-530-PL-EE-GND-0001, Install 4/0 ground to ladder going over containment wall, north central, bury 4/0 beneath gravel to ladder. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
GND-01 | GND-01 | PI14980 | Verified | Drawing: 10-530-PL-EE-GND-0001, Ground WWT Collection Sump lid support steel, utilize 4/0 ground tail at northeast corner of sump. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-02-13 | Fred Michael
GND-01 | GND-01 | PI14981 | Verified | Drawing: 10-530-PL-EE-GND-0001, Seal all PVC conduits penetrating concretefloor of water treatment building, cut grind and caulk unused ground tails that are in walkways. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-04 | Mike Tabbert
GND-01 | GND-01 | PI14982 | Verified | Drawing: 10-530-PL-EE-GND-0001, Additional grounding required for chemical feed skids on west end of water treatment building, two grounds per skid. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-04 | Mike Tabbert
GND-01 | GND-01 | PI14983 | Verified | Drawing: 10-530-PL-EE-GND-0001, Seal grounding tail PVC conduit thru concrete floor of southwest corner of water treatment building. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-04 | Mike Tabbert
GND-01 | GND-01 | PI14984 | Verified | Drawing: 10-530-PL-EE-GND-0001, Rework poor workmanship on ground lug to embed, southeast corner of CIP skid, water treatment building. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14985 | Verified | Drawing: 10-530-PL-EE-GND-0001, Install and complete grounding on south side of CIP Vertical tank | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14986 | Verified | Drawing: 10-530-PL-EE-GND-0001, Rework grounding to 10-WTD-R-0900 Aeration Blower XFMR, poor quality | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14987 | Verified | Drawing: 10-530-PL-EE-GND-0001, Ground two uninsulated showers in rear of water treatment building. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-04 | Mike Tabbert
GND-01 | GND-01 | PI14988 | Verified | Drawing: 10-530-PL-EE-GND-0001, Ground west side of permeate vertical tank, north wall of water treatment building. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-04 | Mike Tabbert
GND-01 | GND-01 | PI14989 | Verified | Drawing: 10-530-PL-EE-GND-0001, Transformers on north wall of water treatment building 10-WTD-XFM-0001 & 0006 not grounded properly. Ground cabinet enclosures not not anchor bolts. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-04 | Mike Tabbert
GND-01 | GND-01 | PI14990 | Verified | Drawing: 10-530-PL-EE-GND-0001, Missing 2 corner grounds on RO skid. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14991 | Verified | Drawing: 10-530-PL-EE-GND-0001, Attach ground to sealtight connector at panel 10-WTD-R-0510 | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-07 | Fred Michael
GND-01 | GND-01 | PI14992 | Verified | Drawing: 10-530-PL-EE-GND-0002, Install ground bushings and ground all stub-ups before cables are terminated. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-16 | Mike Tabbert
GND-01 | GND-01 | PI14993 | Verified | Drawing: 10-530-PL-EE-GND-0002, Complete all grounding at filter press. | A | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
GND-01 | GND-01 | PI14994 | Verified | Drawing: 10-003-PL-EE-GND-0001, Dress up ground cables at 10-ESL-PNL-0007 | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-21 | Mike Tabbert
GND-01 | GND-01 | PI14995 | Verified | Drawing: 10-003-PL-EE-GND-0001, Dress up ground cables at 10-ESH-PNL-0007 | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-21 | Mike Tabbert
GND-01 | GND-01 | PI14996 | Verified | Drawing: 10-003-PL-EE-GND-0001, Tighten clamps on PVC ground chase on top of containment wall north west corner. | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-21 | Mike Tabbert
GND-01 | GND-01 | PI14997 | Verified | Drawing: 10-003-PL-EE-GND-0001, Dress up ground and support at 10-RWS-CP-0200 | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-01-16 | Jared Stimpson | 2020-01-20 | Mike Tabbert
GND-01 | GND-01 | PI14999 | Verified | Restore N. Perimeter fence grounding after turnstiles removed | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2021-01-05 | Keith Pollock
GND-01 | GND-01 | PI15000 | Verified | Complete grounding install behind lunch tent E perimeter | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-06-23 | Chris Colvin | 2020-08-07 | Dave Goldak
GND-01 | GND-01 | PI15613 | Verified | 10MBY91GZ003; Pressure Reduction Panel ground cable needs to buried, currently above ground | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2021-05-27 | John Watts
GND-01 | GND-01 | PI16421 | Verified | Isolation Panel Insulators Have Weld Spatter | A | E | Sheri Fritz | McD | 2020-01-28 | Sheri Fritz | Const |  |  | 2020-01-28 | Mike Tabbert
GND-01 | GND-01 | PI16422 | Verified | Several Isolation Panel Insulators are chipped | A | E | Sheri Fritz | McD | 2020-01-28 | Sheri Fritz | Const |  |  | 2020-01-28 | Mike Tabbert
GND-01 | GND-01 | PI16423 | Verified | Isolation Panel Touching Earth | A | E | Sheri Fritz | McD | 2020-01-28 | Sheri Fritz | Const |  |  | 2020-01-28 | Mike Tabbert
GND-01 | GND-01 | PI16424 | Verified | Insulator Bolts not Seated in Several Panels | A | E | Sheri Fritz | McD | 2020-01-28 | Sheri Fritz | Const |  |  | 2020-01-28 | Mike Tabbert
GND-01 | GND-01 | PI16425 | Verified | Brackets for one Isolation Panel May need to be reworked, Unable to Remove Bolts. | A | E | Sheri Fritz | McD | 2020-01-28 | Sheri Fritz | Const |  |  | 2020-01-28 | Mike Tabbert
GND-01 | GND-01 | PI16426 | Verified | Isolation Panel Welds Not Cleaned Before Touch-Up Paint, needs to be repainted. | A | E | Sheri Fritz | McD | 2020-01-28 | Sheri Fritz | Const |  |  | 2020-01-28 | Mike Tabbert
GND-01 | GND-01 | PI16427 | Verified | Isolation Panel Bracetts Welded over Fence Straps. | A | E | Sheri Fritz | McD | 2020-01-28 | Sheri Fritz | Const |  |  | 2020-01-28 | Mike Tabbert
GND-01 | GND-01 | PI16428 | Verified | Ground Cable not Buried Northwest corner. | A | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Const |  |  | 2020-01-31 | Mike Tabbert
GND-01 | GND-01 | PI16429 | Verified | Ground Tails to Fence Not Buried, West End of Site | A | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Const |  |  | 2020-01-31 | Mike Tabbert
GND-01 | GND-01 | PI16430 | Verified | Cable at Overflow Area Not Buried West End of Site. | A | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Const |  |  | 2020-01-31 | Mike Tabbert
GND-01 | GND-01 | PI16431 | Verified | North Gate Grounding Not Complete. | A | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Const |  |  | 2020-01-31 | Mike Tabbert
GND-01 | GND-01 | PI16432 | Verified | Grounding Cable Not Buried Northeast Section at Craft Parking. | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Const | 2020-05-15 | Chris Colvin | 2020-05-19 | Mike Tabbert
GND-01 | GND-01 | PI16433 | Verified | Cable not Buried from Northeast Corner to Main Road Corner. | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Const | 2020-05-15 | Chris Colvin | 2020-05-19 | Mike Tabbert
GND-01 | GND-01 | PI16434 | Verified | Fence Ground needs to be tied into Main Ground Grid, Mutiple Locations. | A | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Const |  |  | 2020-02-13 | Mike Tabbert
GND-01 | GND-01 | PI16435 | Verified | Gate to laydown, grounding not complete. | A | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Const |  |  | 2020-01-31 | Mike Tabbert
GND-01 | GND-01 | PI16436 | Verified | Warehouse Area not complete from gates at Warehouse to and including gates at main entrance. | C | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Const | 2020-05-15 | Chris Colvin | 2020-05-19 | Mike Tabbert
GND-01 | GND-01 | PI16437 | Verified | South gate to raw water not complete. | A | E | Chris Colvin | McD | 2020-01-28 | Chris Colvin | Const |  |  | 2020-01-31 | Mike Tabbert
GND-01 | GND-01 | PI15539 | Verified | W Super Heat/Reheat Sec-Ground in Landing-punchlist item - relocate ground | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Const | 2020-04-09 | Chris Colvin | 2020-04-14 | Joe Wickline
GND-01 | GND-01 | PI15523 | Verified | W-LP Preheater Sec - Landing has Ground Wire - punchlist item - relocate ground | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Const | 2020-04-09 | Chris Colvin | 2020-04-14 | Joe Wickline
GND-01 | GND-01 | PI15526 | Verified | E -Slope Manway - Ground wire in landing - punchlist item - relocate ground | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Const | 2020-04-09 | Chris Colvin | 2020-04-14 | Joe Wickline
GND-01 | GND-01 | PI16540 | Verified | Bury ground cable at north end of fuel gas area by calorie meter. | C | E | Chris Colvin | McD | 2020-02-04 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-04 | John Watts
GND-01 | GND-01 | PI17845 | Verified | 1B-CTS-GEN-0001 Grounding - Ground cable was ran through grating. In the event the grating would need to be removed, this would affect this setup. | C | E | Chris Colvin | McD | 2020-03-16 | Chris Colvin | Const | 2020-04-16 | Chris Colvin | 2020-06-04 | Cintrel Spears
GND-02 | GND-02 | PI00665 | Verified | Adjust the gound locations on the the south perimeter fence. | A | E | Shannon Savoy | McD | 2019-04-23 | Shannon Savoy | Const | 2019-04-30 | Richard Cruz | 2019-05-01 | Neil Simon
GND-02 | GND-02 | PI00666 | Verified | Fence poles need caps at the isolators on the south perimeter fence. | A | C | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-08 | Neil Simon | 2019-05-08 | Neil Simon
GND-02 | GND-02 | PI00667 | Verified | Bolt missing on permiter fence near the isolator under the 1A transmission line. | A | C | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-08 | Neil Simon | 2019-05-08 | Neil Simon
GND-02 | GND-02 | PI00668 | Verified | Tighten the barbed wire on permiter fence near the isolator under the 1A transmission line. | B | C | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-08 | Neil Simon | 2019-05-08 | Neil Simon
GND-02 | GND-02 | PI00669 | Verified | The bottom guy-wire is tied in on both sides of the isolator. Need to cut & isolate the isolation panels. Check entire fencing under transmission lines. | A | C | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-08 | Neil Simon | 2019-05-08 | Neil Simon
GND-02 | GND-02 | PI00670 | Verified | Complete the fence at the drive through gate at the south perimeter fence. | C | C | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
GND-02 | GND-02 | PI00671 | Verified | Isolation Panel Insulators Have Weld Spatter. | A | E | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-01 | Mike Tabbert | 2019-05-01 | Mike Tabbert
GND-02 | GND-02 | PI00672 | Verified | Several Isolation Panel Insulators are chipped | A | E | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-01 | Mike Tabbert | 2019-05-01 | Mike Tabbert
GND-02 | GND-02 | PI00673 | Verified | Isolation Panel Touching Earth. | A | E | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-01 | Mike Tabbert | 2019-05-01 | Mike Tabbert
GND-02 | GND-02 | PI00674 | Verified | Insulator Bolts not Seated in Several Panels. | A | E | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-01 | Mike Tabbert | 2019-05-01 | Mike Tabbert
GND-02 | GND-02 | PI00675 | Verified | Brackets for one Isolation Panel May need to be reworked, Unable to Remove Bolts. | A | E | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-01 | Mike Tabbert | 2019-05-01 | Mike Tabbert
GND-02 | GND-02 | PI00676 | Verified | Isolation Panel Welds Not Cleaned Before Touch-Up Paint, needs to be repainted. | A | E | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-01 | Mike Tabbert | 2019-05-01 | Mike Tabbert
GND-02 | GND-02 | PI00677 | Verified | Isolation Panel Bracetts Welded over Fence Straps. | A | E | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-01 | Mike Tabbert | 2019-05-01 | Mike Tabbert
GND-02 | GND-02 | PI00678 | Verified | Did not install Isolation Panels per DETAIL 2 on drawing CMS-830-07-SD-46056. | A | E | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-01 | Mike Tabbert | 2019-05-01 | Mike Tabbert
GND-02 | GND-02 | PI00679 | Verified | Fix isolation panels. | A | E | Sheri Fritz | PSC | 2019-04-23 | Sheri Fritz | Const | 2019-05-01 | Mike Tabbert | 2019-05-01 | Mike Tabbert
GND-02 | GND-02 | PI14998 | Verified | W. Perimeter fence at CCW pump area, pole cap missing on top of fence by barbed wire | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Const | 2020-03-05 | Randy Carpenter | 2020-03-05 | Randy Carpenter
GSC-01 | GSC-01 | PI01014 | Verified | Tag valve 1A-GSC-V-0102. | C | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-22 | Terry Deaton | 2019-06-03 | Kelvin Cook
GSC-01 | GSC-01 | PI01015 | Verified | Tag valve 1B-GSC-V-0102. | C | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-22 | Terry Deaton | 2019-06-03 | Kelvin Cook
GSC-01 | GSC-01 | PI02452 | Verified | ISO 100-3 - wrong bolt lengths at the U/G A/G flange. | B | P | Damon Turner | McD | 2019-07-22 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GSC-01 | GSC-01 | PI02453 | Verified | ISO 100-1 - wrong bolt lengths at the TP flange. | B | P | Damon Turner | McD | 2019-07-22 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GSC-01 | GSC-01 | PI02454 | Verified | 10-GSC-RC-0100 is incorrect size. | B | P | Damon Turner | McD | 2019-07-22 | Damon Turner | Const | 2019-08-05 | Damon Turner | 2019-08-09 | Justin Houdeshell
GSC-01 | GSC-01 | PI02455 | Verified | Cold galv. all supports. | C | P | James Beech | McD | 2019-07-22 | James Beech | Const | 2020-02-10 | Fred Michael | 2020-02-14 | Shannon Scott
GSC-01 | GSC-01 | PI02456 | Verified | Apply never sieze to all bolts during torque. | B | P | Damon Turner | McD | 2019-07-22 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Kelvin Cook
GSC-01 | GSC-01 | PI02457 | Verified | Seal all conduits. | A | E | Chris Colvin | McD | 2019-07-22 | Chris Colvin | Const | 2019-09-04 | Dustin Futrell | 2020-01-21 | Michael Law
GSC-01 | GSC-01 | PI02469 | Verified | LK-GSC-P41-0104-01 Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-22 | Damon Turner | Const | 2019-07-24 | Damon Turner | 2019-07-24 | Tom Noble
GSC-01 | GSC-01 | PI02470 | Verified | LK-GSC-P41-0101-02 Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-22 | Damon Turner | Const | 2019-07-24 | Damon Turner | 2019-07-24 | Tom Noble
GSC-01 | GSC-01 | PI02538 | Verified | Complete concrete work for conduit stub-ups as per EF-830-07-SD-36410. | B | C | Johnny Campbell | McD | 2019-07-23 | Johnny Campbell | Const | 2019-07-30 | Johnny Campbell | 2019-08-21 | Fred Michael
GSC-01 | GSC-01 | PI02539 | Verified | Turn in all completion forms. | A | E | Luis Cantu | McD | 2019-07-23 | Luis Cantu | Const | 2019-07-27 | Ed Gober | 2019-07-27 | Ed Gober
GSC-01 | GSC-01 | PI02573 | Verified | ISO 10-GSC-PD-P41-0104-02 Install restraints as per detail for 10-GSC-PD-HGR-0010. | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Kelvin Cook
GSC-01 | GSC-01 | PI02574 | Verified | ISO 10-GSC-PD-P41-0103-05 rework spool and lower evelation to align to CO2 control unit. | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Kelvin Cook
GSC-01 | GSC-01 | PI02637 | Verified | LK-10-GSC-PD-P41-0104-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-25 | Tom Noble
GSC-01 | GSC-01 | PI02752 | Verified | ON ISO 1B-GSC-PD-P41-0105-02 pipe support 1B-GSC-PD-HGR-0057 needs to be grouted. | C | C | Johnny Campbell | McD | 2019-07-24 | Johnny Campbell | Const | 2019-07-31 | Jack Fields | 2019-08-08 | Kelvin Cook
GSC-01 | GSC-01 | PI02753 | Verified | ON ISO 1B-GSC-PD-P41-0105-03 pipe support 1B-GSC-PD-HGR-0058 needs to be grouted. | C | C | Johnny Campbell | McD | 2019-07-24 | Johnny Campbell | Const | 2019-07-31 | Jack Fields | 2019-08-08 | Kelvin Cook
GSC-01 | GSC-01 | PI13039 | Verified | Tighten all U-Bolts at CO2 supply header, CO2 Storage Area, Line No. 2-10-GSC-0100 | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2019-11-21 | Kelvin Cook | 2019-12-13 | Blake Boudreaux
GSC-01 | GSC-01 | PI13040 | Verified | Tighten U-Bolts downstream of first above ground flange at STG Bldg, Line No. 2-10-GSC-0102 | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-17 | Charlie English | 2020-01-23 | Blake Boudreaux
GSC-01 | GSC-01 | PI13041 | Verified | Unions installed backwards on Pressure Relief Valve at 10-CTS-MKG11; CO2 Gas Supply Unit, W of GT A, Line No. 2-10-GSC-0103 | A | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2019-11-20 | Michael Law | 2019-12-05 | Blake Boudreaux
GSC-01 | GSC-01 | PI13042 | Verified | Angle iron support for U-Bolt 1B-GSC-PD-HGR-0042 is inadequate at Line No. 2-10-GSC-0104, W side of GT B | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2019-11-22 | Bobby Williams | 2019-12-13 | Blake Boudreaux
GSC-01 | GSC-01 | PI13043 | Verified | Hanger 10-GSC-PD-HGR-0093 has bent rod at supply to Toshiba CO2/Hydrogen Manifold, 1-1C-GSC-0106 | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-14 | Charlie English | 2020-02-12 | Shannon Scott
GSC-01 | GSC-01 | PI13044 | Verified | Hanger 10-GSC-PD-HGR-0014 has incorrect clamps, NE side STG mezzanine | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2019-11-21 | Kelvin Cook | 2019-12-13 | Blake Boudreaux
GSC-01 | GSC-01 | PI13045 | Verified | Remove all tape, rope, wire, and old tags from all system piping and components | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm |  |  | 2020-02-13 | Shannon Scott
GSC-01 | GSC-01 | PI13046 | Verified | Install identification tag on all system components | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-04-08 | Bernard Stasse
GSC-01 | GSC-01 | PI13047 | Verified | Clean off rust and paint all system piping | C | C | Jorge Alexander | McD | 2019-11-14 | Jorge Alexander | Comm |  |  | 2020-02-13 | Shannon Scott
GSC-01 | GSC-01 | PI16460 | Verified | Need SRV certificate on relief valve RV-1 | C | I | James Strange | MHI | 2020-01-30 | James Strange | Comm | 2020-04-03 | James Strange | 2020-04-07 | Randy Carpenter
GSC-02 | GSC-02 | PI01010 | Verified | Paint all piping. | C | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-08 | Michael Law | 2019-05-08 | Michael Law
GSC-02 | GSC-02 | PI13048 | Verified | Angle iron support for hanger 1A-GSC-PD-HGR-0021 is inadequate, Line No. 1.5-1A-GSC-0105, W side of GT A | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-14 | Charlie English | 2020-01-23 | Blake Boudreaux
GSC-02 | GSC-02 | PI13049 | Verified | Remove rope, wire, and unused tags from all subsystem piping and components | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm |  |  | 2020-02-13 | Shannon Scott
GSC-02 | GSC-02 | PI13050 | Verified | Install tags for all subsystem components | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm |  |  | 2020-02-14 | Shannon Scott
GSC-02 | GSC-02 | PI13051 | Verified | Remove rust and paint throughout subsystem piping | C | P | Jorge Alexander | McD | 2019-11-14 | Jorge Alexander | Comm |  |  | 2020-02-13 | Shannon Scott
GSC-02 | GSC-02 | PI13052 | Verified | Remove rust and cold gal all supports throughout subsystem piping | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm |  |  | 2020-02-13 | Shannon Scott
GSC-03 | GSC-03 | PI01011 | Verified | Paint all piping. | C | P | Terry Deaton | McD | 2019-05-08 | Terry Deaton | Const | 2019-05-08 | Michael Law | 2019-05-08 | Michael Law
GSC-03 | GSC-03 | PI13053 | Verified | Flange bird mouthed at CO2 piping tie-in to 1B Gas Control Unit, Line No. 1.5-1B-GSC-0105, S side of GT B | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2019-11-22 | Bobby Williams | 2019-12-13 | Blake Boudreaux
GSC-03 | GSC-03 | PI13054 | Verified | Install cap at 1B-GSC-V-0103; GT B CO2 Vent Valve, Line No. 2-10-GSC-0104, S of GT B | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2019-11-22 | Bobby Williams | 2019-12-20 | Bernard Stasse
GSC-03 | GSC-03 | PI13055 | Verified | Flange bolts too long, install correct size bolts at CO2 piping tie-in to 1B Gas Control Unit, Line No. 1.5-1B-GSC-0105, S side of GT B | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2019-11-22 | Bobby Williams | 2019-12-13 | Blake Boudreaux
GSC-03 | GSC-03 | PI13056 | Verified | Replace rusted U-Bolt at hanger 1B-GSC-PD-HGR-0046, Line No. 1.5-GSC-0105, W side of GT B | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-23 | Charlie English | 2020-02-12 | Shannon Scott
GSC-03 | GSC-03 | PI13057 | Verified | Clean off rust and cold gal supports throughout system | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm |  |  | 2020-02-13 | Shannon Scott
GSC-03 | GSC-03 | PI13058 | Verified | Remove rust and paint piping throughout system | C | C | Jorge Alexander | McD | 2019-11-14 | Jorge Alexander | Comm |  |  | 2020-02-13 | Shannon Scott
GSC-03 | GSC-03 | PI13059 | Verified | Remove wire, tape, rope, and old tags from pipe and supports throughout system | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm |  |  | 2020-02-13 | Shannon Scott
GSC-03 | GSC-03 | PI13060 | Verified | Cut CO2 and Hydrogen piping support stanchion's anchor bolts to correct size at S end of GT B | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-02-24 | Bobby Williams | 2020-03-04 | John Watts
GSC-03 | GSC-03 | PI13061 | Verified | Tag all subsystem components | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm |  |  | 2020-02-14 | Shannon Scott
GSC-04 | GSC-04 | PI03529 | Verified | Tag all valves, replace with stainless steel wire | C | P | Tim Green | McD | 2019-08-09 | Tim Green | Const | 2021-01-22 | Eric Policarpio | 2021-01-22 | Eric Policarpio
GSC-04 | GSC-04 | PI13063 | Verified | Remove stainless steel flashing from 10-GSC-PD-HGR-0097 at tie-in to Toshiba CO2/Hydrogen manifold | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2020-01-14 | Charlie English | 2020-02-12 | Shannon Scott
GSC-04 | GSC-04 | PI13064 | Verified | Install missing U-Bolt 10-GSC-PD-0096 at CO2 supply header piping, Line No. 1.5-1C-0106, STG Bldg. | B | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm | 2019-11-21 | Kelvin Cook | 2019-12-13 | Blake Boudreaux
GSC-04 | GSC-04 | PI13065 | Verified | Remove all tape, rope, wire, and unused tags from subsystem piping | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm |  |  | 2020-02-14 | Shannon Scott
GSC-04 | GSC-04 | PI13066 | Verified | Remove rust and touch up paint throughout subsystem | C | C | Jorge Alexander | McD | 2019-11-14 | Jorge Alexander | Comm |  |  | 2020-02-14 | Shannon Scott
GSC-04 | GSC-04 | PI13067 | Verified | Remove rust and cold gal supports throughout subsystem | C | P | Bobby Williams | McD | 2019-11-14 | Bobby Williams | Comm |  |  | 2020-02-14 | Shannon Scott
HBH-01 | HBH-01 | PI06844 | Verified | Terminate cable for mixer motor. | A | E | Dustin Futrell | McD | 2019-09-23 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-11-20 | Fred Michael
HBH-01 | HBH-01 | PI06845 | Verified | Ground 1A-HBH-CP-0110. | A | E | Dustin Futrell | McD | 2019-09-23 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Fred Michael
HBH-01 | HBH-01 | PI06846 | Verified | Install drain in panel 1A-HBH-CP-0110. | A | E | Chris Colvin | McD | 2019-09-23 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2020-01-13 | Fred Michael
HBH-01 | HBH-01 | PI06847 | Verified | Wipe down inside panel 1A-HBH-CP-0110. | A | E | Chris Colvin | McD | 2019-09-23 | Chris Colvin | Const | 2019-10-10 | Dustin Futrell | 2020-01-13 | Fred Michael
HBH-01 | HBH-01 | PI06848 | Verified | No LP drains on skid conduit. | D | E | Michael Law | McD | 2019-09-23 | Michael Law | Const |  |  | 2020-01-13 | Fred Michael
HBH-01 | HBH-01 | PI06849 | Verified | Install calibration columns (4). | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-01 | HBH-01 | PI06850 | Verified | Install 1A-HBH-DMP-0120A. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-01 | HBH-01 | PI06851 | Verified | Install 1A-HBH-DMP-0120B. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-01 | HBH-01 | PI06852 | Verified | Install 1A-HBH-DMP-0130A. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-01 | HBH-01 | PI06853 | Verified | Install 1A-HBH-DMP-0130B. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-01 | HBH-01 | PI06854 | Verified | Install 1A-HBH-PI-0120A. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-01 | HBH-01 | PI06855 | Verified | Install 1A-HBH-PI-0120B. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-01 | HBH-01 | PI06856 | Verified | Install 1A-HBH-PI-0130A. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-01 | HBH-01 | PI06857 | Verified | Install 1A-HBH-PI-0130B. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-01 | HBH-01 | PI06858 | Verified | Install mixer motor 1A-HBH-M-0110. | A | M | Shane Crowe | McD | 2019-09-23 | Shane Crowe | Const | 2019-09-25 | Shane Crowe | 2019-09-26 | John Schanno
HBH-01 | HBH-01 | PI06859 | Verified | Ground all motors. | A | E | Dustin Futrell | McD | 2019-09-23 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Fred Michael
HBH-01 | HBH-01 | PI06860 | Verified | 1A-HBH-V-0110 at the phosphate tank is not installed per the ProMinent P&ID. Red line is okay per Randy Carpenter. | C | P | Charles Worthington | McD | 2019-09-23 | Charles Worthington | Const | 2020-04-28 | Charles Worthington | 2020-07-28 | Keith Pollock
HBH-01 | HBH-01 | PI06861 | Verified | Control panel conduit needs drain. | B | E | Chris Colvin | McD | 2019-09-23 | Chris Colvin | Const | 2019-10-24 | Brad Stanford | 2020-01-13 | Fred Michael
HBH-01 | HBH-01 | PI06862 | Verified | Seal all conduits. | B | E | Chris Colvin | McD | 2019-09-23 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
HBH-01 | HBH-01 | PI06956 | Verified | Ground Phosphate skd on east and west end, grounding drawings do not call for ground stub-ups. Utilize ground tails at columns R-13.6 and R-14. | A | E | Dustin Futrell | McD | 2019-09-24 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Fred Michael
HBH-01 | HBH-01 | PI06957 | Verified | Missing condulet covers on feeder conduits at cable tray. | A | E | Dustin Futrell | McD | 2019-09-24 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-11-20 | Fred Michael
HBH-01 | HBH-01 | PI07227 | Verified | Grout skid. | C | C | Johnny Campbell | McD | 2019-09-25 | Johnny Campbell | Const | 2019-10-10 | Jack Fields | 2019-12-07 | Michael Law
HBH-01 | HBH-01 | PI07229 | Verified | Complete pipe tie in phophate skid, line 1A-CNM-0285. | A | P | Bobby Williams | McD | 2019-09-25 | Bobby Williams | Const | 2019-10-08 | Bobby Williams | 2019-10-09 | Alex Isaac
HBH-01 | HBH-01 | PI07231 | Verified | Complete line 1A-HBH-0100. | A | I | Albert Burge | McD | 2019-09-25 | Albert Burge | Const | 2019-09-27 | Gonzalo Pena | 2019-11-18 | Alex Isaac
HBH-01 | HBH-01 | PI07232 | Verified | Complete line 1A-HBH-0120. | A | I | Gonzalo Pena | McD | 2019-09-25 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-10-01 | Alex Isaac
HBH-01 | HBH-01 | PI07233 | Verified | Complete line 1A-HBH-0130. | A | I | Gonzalo Pena | McD | 2019-09-25 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-10-01 | Alex Isaac
HBH-01 | HBH-01 | PI07237 | Verified | Tighten union & flange nuts on 1A-HBH-LIT-0110. Missing 1 bolt & nut. | A | I | Gonzalo Pena | McD | 2019-09-25 | Gonzalo Pena | Const |  |  | 2019-09-27 | Alex Isaac
HBH-01 | HBH-01 | PI07239 | Verified | Add tubing for instrument drains. Personnel protection. | B | I | Michael Law | McD | 2019-09-25 | Michael Law | Const | 2019-11-07 | James Tanner | 2019-11-13 | Shannon Scott
HBH-01 | HBH-01 | PI09373 | Verified | Complete hydro testing. | A | P | Bobby Williams | McD | 2019-10-10 | Bobby Williams | Const |  |  | 2019-10-23 | Kelvin Cook
HBH-01 | HBH-01 | PI09812 | Verified | Test Package HBH01-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-26 | Kelvin Cook
HBH-01 | HBH-01 | PI09813 | Verified | Test Package HBH01-T-02 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-26 | Kelvin Cook
HBH-02 | HBH-02 | PI06577 | Verified | Complete lines to chemical feed inlet to IP drum. | A | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-23 | Bobby Williams | 2019-10-01 | Alex Isaac
HBH-02 | HBH-02 | PI06864 | Verified | Terminate cable for mixer motor. | A | E | Chris Colvin | McD | 2019-09-23 | Chris Colvin | Const |  |  | 2019-12-04 | Fred Michael
HBH-02 | HBH-02 | PI06865 | Verified | Ground 1B-HBH-CP-0110. | A | E | Dustin Futrell | McD | 2019-09-23 | Dustin Futrell | Const | 2019-10-16 | Fred Michael | 2019-10-16 | Fred Michael
HBH-02 | HBH-02 | PI06866 | Verified | Clean rust off xfmr inside 1B-HBH-CP-0110. | A | E | Chris Colvin | McD | 2019-09-23 | Chris Colvin | Const | 2019-10-31 | Brad Stanford | 2020-01-13 | Fred Michael
HBH-02 | HBH-02 | PI06867 | Verified | Install drain in panel 1B-HBH-CP-0110. | A | E | Chris Colvin | McD | 2019-09-23 | Chris Colvin | Const | 2019-10-31 | Brad Stanford | 2020-01-13 | Fred Michael
HBH-02 | HBH-02 | PI06868 | Verified | Wipe down inside panel 1B-HBH-CP-0110. | A | E | Chris Colvin | McD | 2019-09-23 | Chris Colvin | Const | 2019-10-31 | Brad Stanford | 2020-01-13 | Fred Michael
HBH-02 | HBH-02 | PI06869 | Verified | No LP drains on skid conduit. | D | E | Michael Law | McD | 2019-09-23 | Michael Law | Const |  |  | 2020-01-13 | Fred Michael
HBH-02 | HBH-02 | PI06870 | Verified | Missing condulet covers at the cable tray. | B | E | Dustin Futrell | McD | 2019-09-23 | Dustin Futrell | Const | 2019-10-31 | Brad Stanford | 2019-11-20 | Fred Michael
HBH-02 | HBH-02 | PI06871 | Verified | Install calibration columns (4). | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-02 | HBH-02 | PI06872 | Verified | Install 1B-HBH-DMP-0120A. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-02 | HBH-02 | PI06873 | Verified | Install 1B-HBH-DMP-0120B. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-02 | HBH-02 | PI06874 | Verified | Install 1B-HBH-DMP-0130A. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-02 | HBH-02 | PI06875 | Verified | Install 1B-HBH-DMP-0130B. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-02 | HBH-02 | PI06876 | Verified | Install 1B-HBH-PI-0120A. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-02 | HBH-02 | PI06877 | Verified | Install 1B-HBH-PI-0120B. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-02 | HBH-02 | PI06878 | Verified | Install 1B-HBH-PI-0130A. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-02 | HBH-02 | PI06879 | Verified | Install 1B-HBH-PI-0130B. | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-26 | Albert Burge
HBH-02 | HBH-02 | PI06880 | Verified | Install mixer motor 1B-HBH-M-0110. | A | M | Shane Crowe | McD | 2019-09-23 | Shane Crowe | Const | 2019-09-25 | Shane Crowe | 2019-09-26 | John Schanno
HBH-02 | HBH-02 | PI06881 | Verified | Ground all motors. | A | E | Dustin Futrell | McD | 2019-09-23 | Dustin Futrell | Const | 2019-10-16 | Fred Michael | 2019-10-16 | Fred Michael
HBH-02 | HBH-02 | PI06882 | Verified | 1B-HBH-V-0110 at the phosphate tank is not installed per the ProMinent P&ID. Red line is okay per Randy Carpenter. | C | P | Charles Worthington | McD | 2019-09-23 | Charles Worthington | Const | 2020-04-28 | Charles Worthington | 2021-01-15 | John Watts
HBH-02 | HBH-02 | PI06883 | Verified | Seal all conduits. | B | E | Chris Colvin | McD | 2019-09-23 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-02-27 | Fred Michael
HBH-02 | HBH-02 | PI06959 | Verified | Ground Phosphate skd on east and west end, grounding drawings do not call for ground stub-ups. Utilize ground tails at columns R-13.6 and R-14. | A | E | Dustin Futrell | McD | 2019-09-24 | Dustin Futrell | Const | 2019-11-11 | Brad Stanford | 2019-11-20 | Fred Michael
HBH-02 | HBH-02 | PI06960 | Verified | The following cable trays do not have hold down clamps from Phophate Skid to HRSG PDC, 1BTK153002, 1BTC153002 and 1BTX153002. | A | E | Dustin Futrell | McD | 2019-09-24 | Dustin Futrell | Const |  |  | 2019-11-27 | Fred Michael
HBH-02 | HBH-02 | PI07228 | Verified | Grout skid. | C | C | Johnny Campbell | McD | 2019-09-25 | Johnny Campbell | Const | 2019-10-10 | Jack Fields | 2019-12-12 | Joshua Sturgeon
HBH-02 | HBH-02 | PI07230 | Verified | Complete pipe tie in phophate skid, line 1B-CNM-0285. | A | P | Bobby Williams | McD | 2019-09-25 | Bobby Williams | Const | 2019-10-08 | Bobby Williams | 2019-10-09 | Alex Isaac
HBH-02 | HBH-02 | PI07234 | Verified | Complete line 1B-HBH-0100. | B | I | Gonzalo Pena | McD | 2019-09-25 | Gonzalo Pena | Const | 2019-12-03 | James Tanner | 2019-12-13 | Ethan Byrd
HBH-02 | HBH-02 | PI07235 | Verified | Complete line 1B-HBH-0120. | A | I | Gonzalo Pena | McD | 2019-09-25 | Gonzalo Pena | Const | 2019-11-26 | Gonzalo Pena | 2019-12-04 | Shane Copeland
HBH-02 | HBH-02 | PI07236 | Verified | Complete line 1B-HBH-0130. | A | I | Gonzalo Pena | McD | 2019-09-25 | Gonzalo Pena | Const | 2019-12-03 | Gonzalo Pena | 2019-12-04 | Shane Copeland
HBH-02 | HBH-02 | PI07238 | Verified | Tighten union & flange nuts on 1B-HBH-LIT-0110. | A | I | Gonzalo Pena | McD | 2019-09-25 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
HBH-02 | HBH-02 | PI07240 | Verified | Add tubing for instrument drains. Personnel protection. | B | I | Michael Law | McD | 2019-09-25 | Michael Law | Const | 2019-11-07 | James Tanner | 2019-11-13 | Shannon Scott
HBH-02 | HBH-02 | PI09374 | Verified | Complete hydro testing. | A | P | Bobby Williams | McD | 2019-10-10 | Bobby Williams | Const |  |  | 2019-11-11 | Kelvin Cook
HBH-02 | HBH-02 | PI09814 | Verified | Test Package HBH02-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-03 | Kelvin Cook
HBH-02 | HBH-02 | PI09815 | Verified | Test Package HBH02-T-02 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-03 | Kelvin Cook
HRS-01 | HRS-01 | PI06884 | Verified | Remove all rigging. | A | P | James Beech | McD | 2019-09-23 | James Beech | Const |  |  | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06885 | Verified | Remove all rigging prior to hydro | A | P | Damon Turner | McD | 2019-09-23 | Damon Turner | Const | 2019-09-25 | Kelvin Cook | 2019-09-25 | Kelvin Cook
HRS-01 | HRS-01 | PI06886 | Verified | Remove all tape, rope, wire etc prior to insulation release | A | P | James Beech | McD | 2019-09-23 | James Beech | Const |  |  | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06887 | Verified | On ISO 1A-HRS-PD-P40-0010-02 pipe support 1A-HRS-PD-HGR-0510 is not welded | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06888 | Verified | On ISO 1A-HRS-PD-P40-0010-03 instrument 1A-HRS-TW-031 is not installed | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-03 | Kelvin Cook
HRS-01 | HRS-01 | PI06889 | Verified | On ISO 1A-HRS-PD-P40-0010-03 instrument 1A-HRS-TW-040 is not installed | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-03 | Kelvin Cook
HRS-01 | HRS-01 | PI06890 | Verified | On ISO 1A-HRS-PD-P40-0010-03 pipe support 1A-HRS-PD-HGR-0511 has no weep holes | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-12 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06891 | Verified | On ISO 1A-HRS-PD-P40-0010-03 pipe support 1A-HRS-PD-HGR-0530 set shoe proper per detail & tighten bolts | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-26 | Bobby Williams | 2019-12-06 | Kelvin Cook
HRS-01 | HRS-01 | PI06892 | Verified | 1A-HRS-PD-P40-0040-02 - HGR0037 is incomplete | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-24 | James Beech | 2020-01-06 | Ethan Byrd
HRS-01 | HRS-01 | PI06893 | Verified | 1A-HRS-PD-P40-0040-02 - 1A-HRS-TV-0087 Actuator to be installed after steam blows | B | P | James Beech | McD | 2019-09-23 | James Beech | Const |  |  | 2019-11-15 | Alex Isaac
HRS-01 | HRS-01 | PI06894 | Verified | 1A-HRS-PD-P40-0040-02 - Cover open pipe at the Attemperator tie point. | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-08 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06895 | Verified | 1A-HRS-PD-P40-0040-02 - Install blind flange for Steam Blow Attemperator | B | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-12-14 | Michael Law | 2019-12-14 | Michael Law
HRS-01 | HRS-01 | PI06896 | Verified | ISO 1A-HRS-PD-P40-0045-01 HGR-0038 is missing bolts that hold the support bases together | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-06 | James Beech | 2019-12-14 | Kelvin Cook
HRS-01 | HRS-01 | PI06897 | Verified | On ISO 1A-HRS-PD-P40-0045-01 pipe support 1A-HRS-PD-HGR-0038 is not intalled | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06898 | Verified | 1A-HRS-PD-P40-0040-01 Install pipe in lieu of HRS-FE-0081 for steam blows | A | P | James Beech | McD | 2019-09-23 | James Beech | Const |  |  | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06902 | Verified | ISO 1A-HRS-PD-P41-0040-02 missing threaded cap | A | P | Kelvin Cook | McD | 2019-09-23 | Kelvin Cook | Const |  |  | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06903 | Verified | ISO 1A-HRS-PD-P41-0040-03 missing threaded cap | A | P | Kelvin Cook | McD | 2019-09-23 | Kelvin Cook | Const |  |  | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06906 | Verified | ISO 1A-HRS-PD-P41-0045-01 missing threaded cap | A | P | Kelvin Cook | McD | 2019-09-23 | Kelvin Cook | Const |  |  | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06907 | Verified | On ISO 1B-HRS-PD-P40-0010-01 pipe support 1B-HRS-PD-HGR-0500 is not installed | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-12 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06908 | Verified | On ISO 1B-HRS-PD-P40-0010-01 pipe support 1B-HRS-PD-HGR-0522 loose nuts & out of plumb | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-12 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06909 | Verified | Remove all rigging prior to hydro | A | P | Damon Turner | McD | 2019-09-23 | Damon Turner | Const | 2019-09-25 | Kelvin Cook | 2019-09-25 | Kelvin Cook
HRS-01 | HRS-01 | PI06910 | Verified | On ISO 1B-HRS-PD-P40-0010-02 - 1B-HRS-PD-HGR-0501 needs to be set level per the detail | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-25 | Bobby Williams | 2019-12-06 | Kelvin Cook
HRS-01 | HRS-01 | PI06911 | Verified | On ISO 1B-HRS-PD-P40-0010-02 pipe support 1B-HRS-PD-HGR-0524 has the incorrect offset | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-25 | Bobby Williams | 2019-12-06 | Kelvin Cook
HRS-01 | HRS-01 | PI06912 | Verified | On ISO 1B-HRS-PD-P40-0010-03 remove rigging from pipe | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-12 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06913 | Verified | On ISO 1B-HRS-PD-P40-0010-03 pipe support 1B-HRS-PD-HGR-0505 off more like 4 3/4 -5" | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-12 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06914 | Verified | On ISO 1B-HRS-PD-P40-0010-03 pipe support 1B-HRS-PD-HGR-0536 set off proper | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-25 | Bobby Williams | 2019-12-06 | Kelvin Cook
HRS-01 | HRS-01 | PI06915 | Verified | On ISO 1B-HRS-PD-P40-0010-03 pipe support 1B-HRS-PD-HGR-0538 set shoe to proper offset | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-08 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06916 | Verified | On ISO 1B-HRS-PD-P40-0010-04 instrument 1B-HRS-TW-0040 is not installed | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const |  |  | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06918 | Verified | 1B-HRS-PD-P40-0040-02 spool through the FE. | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-08 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06919 | Verified | ISO 1B-HRS-PD-P40-0040-02 HGR-0039 is incomplete | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-08 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06920 | Verified | On ISO 1B-HRS-PD-P40-0040-02 - 10-HRS-TV-0087 Actuator to be installed after Steam Blows. | B | P | James Beech | McD | 2019-09-23 | James Beech | Const |  |  | 2019-11-15 | Alex Isaac
HRS-01 | HRS-01 | PI06921 | Verified | ISO 1B-HRS-PD-P40-0040-02 Install Blind Flange for Steam Blow Attemperation | B | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-12-14 | Michael Law | 2019-12-14 | Michael Law
HRS-01 | HRS-01 | PI06922 | Verified | On ISO 1B-HRS-PD-P40-0045-01 HGR-0040 missing bolts that hold the two sections of the support together. | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-06 | James Beech | 2019-12-14 | Kelvin Cook
HRS-01 | HRS-01 | PI06923 | Verified | On ISO 1B-HRS-PD-P40-0045-01 HGR-0040 pipe clamps on the shoe support are loose. | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06926 | Verified | On ISO 1B-HRS-PD-P41-0010-01 instrument 1B-HRS-PIT-0030 is not installed | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-11-24 | James Beech | 2019-12-14 | Kelvin Cook
HRS-01 | HRS-01 | PI06927 | Verified | ISO 1B-HRS-PD-P41-0020-01 is not intalled | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-12 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06928 | Verified | ISO 1B-HRS-PD-P41-0025-01 is not intalled | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-08 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06929 | Verified | ISO 1B-HRS-PD-P41-0025-02 is not intalled | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-08 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06930 | Verified | ISO 1B-HRS-PD-P41-0040-04 missing a threaded cap | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-08 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06931 | Verified | ISO 1B-HRS-PD-P41-0040-05 missing a threaded cap | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-08 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06934 | Verified | ISO 1B-HRS-PD-P41-0045-01 missing a threaded cap | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-08 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06935 | Verified | On ISO 1C-HRS-PD-P40-0010-01 pipe support 1A-HRS-PD-HGR-0508-2 is incomplete | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-12 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06936 | Verified | On ISO 1C-HRS-PD-P40-0010-03 instruments 1C-HRS-TW-9013, 0015, 0017 are not installed | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06937 | Verified | On ISO 1C-HRS-PD-P40-0010-03 pipe support 1C-HRS-PD-HGR-0534 item 3 is not installed | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-08 | James Beech | 2019-12-19 | Kelvin Cook
HRS-01 | HRS-01 | PI06938 | Verified | On ISO 1C-HRS-PD-P40-0010-04 instrument 1C-HRS-TW-0020 is not installed | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-03 | Kelvin Cook
HRS-01 | HRS-01 | PI06939 | Verified | On ISO 1C-HRS-PD-P40-0020-01 instrument 1C-HRS-TW-0020 is not installed | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-03 | Kelvin Cook
HRS-01 | HRS-01 | PI06940 | Verified | On ISO 1C-HRS-PD-P40-0020-02 instrument 1C-HRS-TW-0023 A & 0023B are not installed | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-03 | Kelvin Cook
HRS-01 | HRS-01 | PI06941 | Verified | On ISO 1C-HRS-PD-P40-0020-02 pipe support 1C-HRS-PD-0516 must bet set to bottom of lugs | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-08 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06942 | Verified | On ISO 1C-HRS-PD-P40-0030-01 instrument 1C-HRS-TW-0040 is not installed | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-03 | Kelvin Cook
HRS-01 | HRS-01 | PI06943 | Verified | On ISO 1C-HRS-PD-P40-0030-02 instrument 1C-HRS-TW-0026A & 0026B are not installed | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-03 | Kelvin Cook
HRS-01 | HRS-01 | PI06944 | Verified | On ISO 1C-HRS-PD-P40-0030-02 pipe support 1C-HRS-PD-HGR-0515 tighten all nuts per detail | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-08 | James Beech | 2019-11-23 | Kelvin Cook
HRS-01 | HRS-01 | PI06945 | Verified | On ISO 1C-HRS-PD-P40-0030-02 pipe support 1C-HRS-PD-HGR-0515 must be rest at bottom of all lugs | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-12-02 | Bobby Williams | 2019-12-14 | Kelvin Cook
HRS-01 | HRS-01 | PI06946 | Verified | On ISO 1C-HRS-PD-P41-0010-01 instrument 1C-HRS-PIT-9010A is not installed | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-11-24 | James Beech | 2019-12-14 | Kelvin Cook
HRS-01 | HRS-01 | PI06947 | Verified | On ISO 1C-HRS-PD-P41-0010-02 instrument 1C-HRS-PIT-9010B is not installed | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-11-24 | James Beech | 2019-12-14 | Kelvin Cook
HRS-01 | HRS-01 | PI06948 | Verified | On ISO 1C-HRS-PD-P41-0010-03 instrument 1C-HRS-PP-0010 missing tubing cap | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-11-24 | James Beech | 2019-12-15 | Kelvin Cook
HRS-01 | HRS-01 | PI06949 | Verified | ISO 1C-HRS-PD-P41-0018-01 missing threaded cap on drain valve 1C-HRS-V-0018 | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-26 | Bobby Williams | 2019-12-15 | Kelvin Cook
HRS-01 | HRS-01 | PI06950 | Verified | On ISO 1C-HRS-PD-P41-0020-01 instrument 1C-HRS-PP-0021 missing tubing cap | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-11-24 | James Beech | 2019-12-14 | Kelvin Cook
HRS-01 | HRS-01 | PI06951 | Verified | ISO 1C-HRS-PD-P41-0026-01 - 1C-HRS-V-0033 is missing a valve handle | A | P | James Beech | McD | 2019-09-23 | James Beech | Const |  |  | 2020-02-10 | Kelvin Cook
HRS-01 | HRS-01 | PI06952 | Verified | ISO 1C-HRS-PD-P41-0028-01 missing threaded cap on drain valve 1C-HRS-V-0032 | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-26 | Bobby Williams | 2019-12-04 | Kelvin Cook
HRS-01 | HRS-01 | PI06953 | Verified | On ISO 1C-HRS-PD-P41-0030-01 instrument 1C-HRS-PP-0024 missing tubing cap | A | I | Gonzalo Pena | McD | 2019-09-23 | Gonzalo Pena | Const | 2019-11-24 | James Beech | 2019-12-15 | Kelvin Cook
HRS-01 | HRS-01 | PI06954 | Verified | ISO 1C-HRS-PD-P41-0036-01 - 1C-HRS-V-0043 is missing a valve handle | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-08 | James Beech | 2020-01-17 | Kelvin Cook
HRS-01 | HRS-01 | PI06955 | Verified | ISO 1C-HRS-PD-P41-0038-01 missing a threaded cap | A | P | James Beech | McD | 2019-09-23 | James Beech | Const | 2019-11-25 | Bobby Williams | 2019-12-06 | Kelvin Cook
HRS-01 | HRS-01 | PI06962 | Verified | 1C-HRS-PD-P41-0038-01 - Replace 1C-HRS-V-0041 (per Quality Department). | A | P | James Beech | McD | 2019-09-24 | James Beech | Const |  |  | 2019-11-07 | Kelvin Cook
HRS-01 | HRS-01 | PI07045 | Verified | Set all spring cans to cold settings. | A | P | James Beech | McD | 2019-09-24 | James Beech | Const |  |  | 2019-12-20 | Michael Law
HRS-01 | HRS-01 | PI07046 | Verified | Tag all valves. | C | P | James Beech | McD | 2019-09-24 | James Beech | Const |  |  | 2020-02-10 | Kelvin Cook
HRS-01 | HRS-01 | PI09876 | Verified | 1AHRSC0001 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09877 | Verified | 1AHRSC0003 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09878 | Verified | 1AHRSC0006 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09879 | Verified | 1AHRSX0014 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09880 | Verified | 1AHRSX0015 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09881 | Verified | 1AHRSX0016 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09882 | Verified | 1AHRSX0018 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09883 | Verified | 1BHRSC0001 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09884 | Verified | 1BHRSK0002 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09885 | Verified | 1BHRSX0002 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09886 | Verified | 1BHRSX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09887 | Verified | 1BHRSX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09888 | Verified | 1BHRSX0012 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09889 | Verified | 1BHRSX0013 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09890 | Verified | 1AHRSC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09891 | Verified | 1AHRSC0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09892 | Verified | 1AHRSC0006 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09893 | Verified | 1AHRSX0008 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09894 | Verified | 1AHRSX0009 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09895 | Verified | 1AHRSX0010 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09896 | Verified | 1AHRSX0014 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09897 | Verified | 1AHRSX0015 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09898 | Verified | 1AHRSX0016 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09899 | Verified | 1AHRSX0018 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09900 | Verified | 1AMBLX0012 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09901 | Verified | 1BHRSC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09902 | Verified | 1BHRSC0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09903 | Verified | 1BHRSK0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09904 | Verified | 1BHRSX0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09905 | Verified | 1BHRSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09906 | Verified | 1BHRSX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09907 | Verified | 1BHRSX0012 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI09908 | Verified | 1BHRSX0013 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
HRS-01 | HRS-01 | PI10249 | Verified | There is broken glass on the face of Temperature indicator 1A-HRS-TI-8426. | A | I | Gonzalo Pena | McD | 2019-10-23 | Gonzalo Pena | Const | 2019-11-19 | James Tanner | 2019-12-11 | Shannon Scott
HRS-01 | HRS-01 | PI12860 | Verified | 1A-HRS-PD-P41-0040-02: Install a 4" 300 lb blind flange after steam blows | B | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2020-01-30 | James Beech | 2020-01-31 | Kelvin Cook
HRS-01 | HRS-01 | PI12861 | Verified | 1B-HRS-PD-P41-0040-02: Install a 4" 300 lb blind flange after steam blows | B | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2020-01-30 | James Beech | 2020-01-31 | Kelvin Cook
HRS-01 | HRS-01 | PI13076 | Verified | Install Spray Nozzles on valve 1A-HRS-PV-0030 | A | P | James Beech | CCI | 2019-11-15 | James Beech | Const |  |  | 2020-01-09 | Bobby Williams
HRS-01 | HRS-01 | PI13077 | Verified | Remove flush trim and install final trim and actuator on valve 1A-HRS-TV-0087 (AFTER STEAM BLOW) | A | P | James Beech | CCI | 2019-11-15 | James Beech | Const | 2020-02-06 | James Beech | 2020-02-06 | Kelvin Cook
HRS-01 | HRS-01 | PI13081 | Verified | Install Spray Nozzles on valve 1B-HRS-PV-0030 | A | P | James Beech | CCI | 2019-11-15 | James Beech | Const |  |  | 2020-01-09 | Bobby Williams
HRS-01 | HRS-01 | PI13082 | Verified | Remove flush trim and install final trim and actuator on valve 1B-HRS-TV-0087 (AFTER STEAM BLOW) | A | P | James Beech | CCI | 2019-11-15 | James Beech | Const | 2019-12-17 | James Beech | 2019-12-18 | Shane Copeland
HRS-01 | HRS-01 | PI13237 | Verified | Pipe Support Number: 1A-HRS-PD-HGR-0539: Ref. Iso. LK-1A-HRS-PD-P40-0025-01: Rod size appears small. Size 1" Rod Required. It appears that 3/4" or smaller was installed or supplied. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-11-25 | Bobby Williams | 2019-12-12 | Gary Pickeral
HRS-01 | HRS-01 | PI13238 | Verified | Pipe Support Number: 1A-HRS-PD-HGR-0535: Ref. Iso. LK-1A-HRS-PD-P40-0025-01: Incorect Gaps. N-S Guide has 1/4" Gap on North side and 1 3/4" Gap on South Side. Both Gaps should be 1" | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-02 | Bobby Williams | 2019-12-12 | Gary Pickeral
HRS-01 | HRS-01 | PI13239 | Verified | Pipe Support Number: 1A-HRS-PD-HGR-0523: Ref. Iso. LK-1A-HRS-PD-P40-0025-03: Pipe Support Shoe is not welded to Trapeze. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-11-26 | Bobby Williams | 2019-12-19 | Gary Pickeral
HRS-01 | HRS-01 | PI13240 | Verified | Pipe Support Number: 1A-HRS-PD-HGR-0543: Ref. Iso. LK-1A-HRS-PD-P40-0025-03: West Gap must be shimmed to equal 1" in Cold, Installed position (See Field Note 1 and Design Movement). | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-11-26 | Bobby Williams | 2019-12-12 | Gary Pickeral
HRS-01 | HRS-01 | PI13241 | Verified | Pipe Support Number: 1B-HRS-PD-HGR-0506: Ref. Iso. LK-1B-HRS-PD-P40-0010-04: Please confirm that 4" Guide Post (Item 3 & 4) are installed. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-11-25 | Bobby Williams | 2020-01-07 | Ethan Byrd
HRS-01 | HRS-01 | PI13242 | Verified | Pipe Support Number: 1B-HRS-PD-HGR-0553: Ref. Iso. LK-1B-HRS-PD-P40-0025-02: Pipe Shoe is not Welded to Trapeze. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-11-25 | Bobby Williams | 2020-01-07 | Ethan Byrd
HRS-01 | HRS-01 | PI13243 | Verified | Pipe Support Number: 1C-HRS-PD-HGR-0512: Ref. Iso. LK-1C-HRS-PD-P40-0010-01: Pipe Shoe may not be welded to Trapeze. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-11-25 | Bobby Williams | 2020-01-07 | Ethan Byrd
HRS-01 | HRS-01 | PI13244 | Verified | Pipe Support Number: 1C-HRS-PD-HGR-0513: Ref. Iso. LK-1C-HRS-PD-P40-0010-03: Pipe Shoe is not welded to Trapeze. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-11-25 | Bobby Williams | 2020-01-16 | Ethan Byrd
HRS-01 | HRS-01 | PI13245 | Verified | Pipe Support Number: 1C-HRS-PD-HGR-0534: Ref. Iso. LK-1C-HRS-PD-P40-0010-03: Must remove small Lifting Lug on North 8X8 Tube Steel to allow thermal Expansion of pipe 1.09" Eastward. Item 2 is offset in the wrong direction, but installed as designed. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-11-25 | Bobby Williams | 2019-12-12 | Gary Pickeral
HRS-01 | HRS-01 | PI13246 | Verified | Pipe Support Number: 1C-HRS-PD-HGR-0516: Ref. Iso. LK-1C-HRS-PD-P40-0020-02: The Lower South Bolt of the Riser Clamp is Loose. May have been repaired by field craft who was installing sister hanger 1C-HRS-HGR-0515, but could not convey issue due to language barrier. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-11-25 | Bobby Williams | 2019-12-12 | Gary Pickeral
HRS-01 | HRS-01 | PI13915 | Verified | Replace damaged TE 1B-HRS-TE-0031. | C | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const |  |  | 2019-12-14 | James Tanner
HRS-01 | HRS-01 | PI13944 | Verified | 1C-HRS-AOV-0030 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2019-12-06 | James Tanner | 2020-01-01 | Albert Burge
HRS-01 | HRS-01 | PI13945 | Verified | 1C-HRS-AOV-0030 - replace open / close indicator (color change). | B | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2020-01-20 | Gonzalo Pena | 2020-01-24 | Albert Burge
HRS-01 | HRS-01 | PI13946 | Verified | 1C-HRS-AOV-0040 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2019-12-06 | James Tanner | 2020-01-01 | Albert Burge
HRS-01 | HRS-01 | PI13947 | Verified | 1C-HRS-AOV-0040 - replace open / close indicator (color change). | B | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2020-01-20 | Gonzalo Pena | 2020-01-24 | Albert Burge
HRS-01 | HRS-01 | PI13948 | Verified | 1C-HRS-TE-9013 - flex too short. | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2019-12-05 | Brad Stanford | 2020-01-01 | Albert Burge
HRS-01 | HRS-01 | PI13949 | Verified | 1C-HRS-TE-0017 - flex too short. | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2019-12-05 | Brad Stanford | 2020-01-01 | Albert Burge
HRS-01 | HRS-01 | PI13950 | Verified | 1C-HRS-AOV-0020 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2019-12-06 | James Tanner | 2020-01-01 | Albert Burge
HRS-01 | HRS-01 | PI13951 | Verified | 1A-HRS-PIT-0030 - missing tag. | C | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2020-01-03 | Gonzalo Pena | 2020-01-13 | Fred Michael
HRS-01 | HRS-01 | PI13952 | Verified | 1B-HRS-AOV-0086 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2019-12-07 | James Tanner | 2019-12-13 | Albert Burge
HRS-01 | HRS-01 | PI13953 | Verified | 1B-HRS-AOV-0086 - complete conduit. | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-09 | Fred Michael
HRS-01 | HRS-01 | PI13954 | Verified | 1B-HRS-AOV-0086 - replace open / close indicator (color change). | B | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2020-01-20 | Gonzalo Pena | 2020-01-22 | Albert Burge
HRS-01 | HRS-01 | PI13955 | Verified | 1B-HRS-FE-0081 - plug spare taps. | A | P | James Beech | McD | 2019-12-04 | James Beech | Const | 2019-12-09 | Michael Law | 2019-12-13 | Albert Burge
HRS-01 | HRS-01 | PI13956 | Verified | 1B-HRS-FE-0081 - run tubing to 1B-HRS-FIT-0081. | A | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2019-12-07 | James Tanner | 2019-12-13 | Albert Burge
HRS-01 | HRS-01 | PI13957 | Verified | 1A-HRS-AOV-0086 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2019-12-07 | James Tanner | 2019-12-13 | Albert Burge
HRS-01 | HRS-01 | PI13958 | Verified | 1A-HRS-AOV-0086 - replace open / close indicator (color change). | B | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2020-01-20 | Gonzalo Pena | 2020-01-22 | Albert Burge
HRS-01 | HRS-01 | PI13959 | Verified | 1A-HRS-AOV-0086 - tighten flex. | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-09 | Fred Michael
HRS-01 | HRS-01 | PI13960 | Verified | 1A-HRS-FE-0081 - run tubing to 1A-HRS-FIT-0081. | A | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2019-12-09 | James Tanner | 2019-12-09 | Fred Michael
HRS-01 | HRS-01 | PI13961 | Verified | 1C-HRS-PIT-9010A - complete tubing. | A | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2019-12-07 | James Tanner | 2020-01-13 | Fred Michael
HRS-01 | HRS-01 | PI13962 | Verified | 1C-HRS-PIT-9010B - complete tubing. | A | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2019-12-07 | James Tanner | 2020-01-13 | Fred Michael
HRS-01 | HRS-01 | PI13963 | Verified | 1C-HRS-PIT-9010A & B - re-tag instruments (currently tagged 1V-1C-HRS-PIT-9010A / B). | C | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2019-12-12 | James Tanner | 2020-01-01 | Albert Burge
HRS-01 | HRS-01 | PI13964 | Verified | 1C-HTS-CAB-0300 - clean inside instrument box. | B | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2019-12-12 | James Tanner | 2020-01-01 | Albert Burge
HRS-01 | HRS-01 | PI14011 | Verified | 1AHRSX0004, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
HRS-01 | HRS-01 | PI14012 | Verified | 1AHRSX0006, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
HRS-01 | HRS-01 | PI14013 | Verified | 1BHRSX0006, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
HRS-01 | HRS-01 | PI14014 | Verified | 1AHRSX0004, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
HRS-01 | HRS-01 | PI14015 | Verified | 1AHRSX0006, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
HRS-01 | HRS-01 | PI14662 | Verified | 1CSDSC0011, Terminate cable both ends. | A | E | Chris Colvin | McD | 2019-12-10 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
HRS-01 | HRS-01 | PI14663 | Verified | 1CSDSC0012, Terminate cable both ends. | A | E | Chris Colvin | McD | 2019-12-10 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
HRS-01 | HRS-01 | PI14664 | Verified | 1CSDSC0013, Terminate cable both ends. | A | E | Chris Colvin | McD | 2019-12-10 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
HRS-01 | HRS-01 | PI14665 | Verified | 1CSDSC0014, Terminate cable both ends. | A | E | Chris Colvin | McD | 2019-12-10 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
HRS-01 | HRS-01 | PI14671 | Verified | Complete tubing connection to FE-0081B | A | I | James Tanner | McD | 2019-12-10 | James Tanner | Const | 2019-12-17 | Gonzalo Pena | 2019-12-23 | Michael Law
HRS-01 | HRS-01 | PI14694 | Verified | 1A-HRS-PIT-0025-WIRE LOOSE IN INSTRUMENT. | A | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const | 2019-12-13 | John Sullivan | 2019-12-13 | John Sullivan
HRS-01 | HRS-01 | PI14695 | Verified | 1C-HTS-CAB-0300-CONDUIT COVERS MISSING 2 SCREWS BELOW BOX. | B | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const |  |  | 2019-12-13 | John Sullivan
HRS-01 | HRS-01 | PI14696 | Verified | 1B-HRS-PIT-0025-LOOSE FLEX CONNECTOR | C | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const | 2020-04-01 | Chris Colvin | 2020-04-02 | Michael Law
HRS-01 | HRS-01 | PI14697 | Verified | 1A-HRS-PIT-0025-NEED TO SHRINK BOOT ON TUBE BUNDLE. | B | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-13 | John Sullivan
HRS-01 | HRS-01 | PI14698 | Verified | 1B-HRS-PIT-0025-NEED TO SHRINK BOOT ON TUBE BUNDLE. | B | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-13 | John Sullivan
HRS-01 | HRS-01 | PI14699 | Verified | 1A-HRS-PIT-0025-NEED TO INSTALL I.D. TAG. | C | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-14 | John Sullivan
HRS-01 | HRS-01 | PI14700 | Verified | 1B-HRS-PIT-0025-NEED TO INSTALL I.D. TAG. | C | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-14 | John Sullivan
HRS-01 | HRS-01 | PI14715 | Verified | 1B-HRS-PD-P41-0036-01: 1B-HRS-HGR-0001 was located on 12/7/2019. Verify the installed spring can is correct | A | P | James Beech | McD | 2019-12-12 | James Beech | Const |  |  | 2019-12-20 | Michael Law
HRS-01 | HRS-01 | PI14798 | Verified | 1A-HRS-PIT-0030-NEED I.D. TAG INSTALLED(10-HTS-CAB-0202) - DUPLICATE PUNCH ITEM - JOHN S. | C | I | James Tanner | McD | 2019-12-15 | James Tanner | Const |  |  | 2019-12-15 | Eric Policarpio
HRS-01 | HRS-01 | PI14799 | Verified | 1B-HRS-PIT-0030-FINISH INSTALLING TUBE BUNDLE.(10-HTS-CAB-0202) | A | I | James Tanner | McD | 2019-12-15 | James Tanner | Const |  |  | 2019-12-17 | John Sullivan
HRS-01 | HRS-01 | PI14800 | Verified | 1A-HRS-FIT-0081-NEED I.D. TAG INSTALLED(10-HTS-CAB-0201) | C | I | James Tanner | McD | 2019-12-15 | James Tanner | Const |  |  | 2019-12-17 | John Sullivan
HRS-01 | HRS-01 | PI14801 | Verified | 1B-HRS-FIT-0081-NEED I.D. TAG INSTALLED(10-HTS-CAB-0201) | C | I | James Tanner | McD | 2019-12-15 | James Tanner | Const |  |  | 2019-12-17 | John Sullivan
HRS-01 | HRS-01 | PI14802 | Verified | 10-HTS-CAB-0201-NEED TO TIGHTEN LOOSE FLEX CONNECTORS AT BOX. | B | E | James Tanner | McD | 2019-12-15 | James Tanner | Const | 2019-12-16 | John Sullivan | 2019-12-17 | John Sullivan
HRS-01 | HRS-01 | PI14803 | Verified | 10-HTS-CAB-0201-NEED TO CLEAN OUT BOX INSIDE AND OUT. | B | I | James Tanner | McD | 2019-12-15 | James Tanner | Const | 2019-12-17 | Gonzalo Pena | 2019-12-18 | John Sullivan
HRS-01 | HRS-01 | PI15905 | Verified | 1A-HRS-AOV-0040, 1A-HRS-V-0033, 1A-HRS-V-0034 - The Hot Reheat drip pot manual valve handwheels are broken and leaking steam. | C | P | Tim Green | McD | 2020-01-13 | Tim Green | Comm | 2020-08-07 | Tim Green | 2021-02-01 | Dave Goldak
HRS-01 | HRS-01 | PI17194 | Verified | Replace 3 TE's 1A-HRS-TE-0087 A/B/C | A | I | Gonzalo Pena | McD | 2020-02-25 | Gonzalo Pena | Const | 2020-03-05 | Tim Green | 2020-03-09 | Michael Law
HRS-01 | HRS-01 | PI17196 | Verified | Complete RV drains UB HRSG | A | I | Gonzalo Pena | McD | 2020-02-25 | Gonzalo Pena | Const | 2020-03-06 | Tim Green | 2020-03-09 | Michael Law
HRS-01 | HRS-01 | PI17195 | Verified | Replace 3 TE's 1B-HRS-TE-0087 A/B/C | A | I | Gonzalo Pena | McD | 2020-02-25 | Gonzalo Pena | Const | 2020-03-05 | Tim Green | 2020-03-09 | Michael Law
HRS-01 | HRS-01 | PI17199 | Verified | 1A-HRS-AOV-0086 – Valve will not operate when pressure is on the line. The valve datasheet says the instrument air should be set to 80 psi but the valve will not open. Instrument air pressure was increased to 110 psi but it still will not open. Valve is currently forced open from the DCS not allowing it to close - 3/27 to contact vendor, waiting for comments | C | I | Charles Worthington | McD | 2020-02-25 | Charles Worthington | Comm | 2020-06-18 | Jason Ezell | 2020-06-18 | Jason Ezell
HRS-01 | HRS-01 | PI17200 | Verified | 1B-HRS-AOV-0086 – Valve will not operate when pressure is on the line. The valve datasheet says the instrument air should be set to 80 psi but the valve will not open. Instrument air pressure was increased to 110 psi but it still will not open. Valve is currently forced open from the DCS not allowing it to close - 3/27 to contact vendor, waiting for comments | C | I | Charles Worthington | McD | 2020-02-25 | Charles Worthington | Comm | 2020-06-18 | Jason Ezell | 2020-06-18 | Jason Ezell
HRS-01 | HRS-01 | PI17449 | Verified | 1A-HRS-PIT-0030 is leaking and needs to be repaired. It is welded, needs to be cut and swaged. | B | I | James Beech | McD | 2020-03-02 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-03-07 | Albert Burge
HRS-01 | HRS-01 | PI17450 | Verified | 1B-HRS-PIT-0030 is leaking and needs to be repaired. It is welded, needs to be cut and swaged. | B | I | James Beech | McD | 2020-03-02 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-03-07 | Albert Burge
HRS-01 | HRS-01 | PI17841 | Verified | 1A-HRS-PV-0030 - The Hot Reheat Bypass to the Condenser Valve on 1A Unit leaks through. | C | P | William Mitchell | McD | 2020-03-16 | William Mitchell | Const | 2020-04-15 | William Mitchell | 2021-01-05 | Keith Pollock
HRS-01 | HRS-01 | PI18011 | Verified | Hot Reheat Bypass to Condenser on 1B Unit valve seizes up. | C | M | William Mitchell | McD | 2020-03-17 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2021-01-05 | Keith Pollock
HRS-01 | HRS-01 | PI18040 | Verified | See attached photo DSC00002; Broken valve handle, 1A-HRS-V-0033 | C | P | James Beech | McD | 2020-03-18 | James Beech | Comm | 2020-04-16 | James Beech | 2020-04-16 | Michael Law
HRS-01 | HRS-01 | PI18041 | Verified | See attached photo DSC00004; Missing/"Home-made" handle, 1A-HRS-V-0032 | C | P | James Beech | McD | 2020-03-18 | James Beech | Comm | 2020-04-16 | James Beech | 2020-04-16 | Michael Law
HRS-01 | HRS-01 | PI18042 | Verified | See attached photo DSC00006; Ground on flex not connected, 1A-HRS-TE-0040 | C | E | Chris Colvin | McD | 2020-03-18 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2021-02-01 | Dave Goldak
HRS-01 | HRS-01 | PI14034 | Verified | 1BHRSX0019, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
HRS-01 | HRS-01 | PI14033 | Verified | 1BHRSX0018, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
HRS-01 | HRS-01 | PI14032 | Verified | 1BHRSX0008, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
HRS-01 | HRS-01 | PI14031 | Verified | 1BHRSX0006, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
HRS-01 | HRS-01 | PI14030 | Verified | 1BHRSX0003, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
HRS-01 | HRS-01 | PI14029 | Verified | 1BHRSX0002, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-09 | Chris Caywood
HRS-01 | HRS-01 | PI14028 | Verified | 1BHRSK0002, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
HRS-01 | HRS-01 | PI14027 | Verified | 1BHRSC0002, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
HRS-01 | HRS-01 | PI14026 | Verified | 1AHRSX0019, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
HRS-01 | HRS-01 | PI14025 | Verified | 1AHRSX0018, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
HRS-01 | HRS-01 | PI14024 | Verified | 1AHRSX0010, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
HRS-01 | HRS-01 | PI14023 | Verified | 1AHRSX0009, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
HRS-01 | HRS-01 | PI14022 | Verified | 1AHRSX0006, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
HRS-01 | HRS-01 | PI14021 | Verified | 1AHRSX0004, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
HRS-01 | HRS-01 | PI14020 | Verified | 1AHRSX0003, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
HRS-01 | HRS-01 | PI14019 | Verified | 1AHRSC0003, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
HRS-01 | HRS-01 | PI14018 | Verified | 1BHRSX0006, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
HRS-01 | HRS-01 | PI14017 | Verified | 1BHRSX0002, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
HRS-01 | HRS-01 | PI14016 | Verified | 1BHRSK0002, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
HRS-01 | HRS-01 | PI18043 | Verified | See attached photo DSC00008; Shoe not squarely set on pipe, shoe not square on trapeze, Trapeze not aligned with support beams, 1C-HRS-PD-HGR-0512 | C | P | Gary Pickeral | McD | 2020-03-18 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-22 | Dave Goldak
HRS-01 | HRS-01 | PI18044 | Verified | See attached photo DSC00011; Support installed with no gap to the north and 1-1.5" gap to the south, 1C-HRS-PD-HGR-0507 | C | P | Gary Pickeral | McD | 2020-03-18 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-22 | Dave Goldak
HRS-01 | HRS-01 | PI18045 | Verified | See attached photo DSC00014; Pipe clamp not per design, 1C-HRS-PD-HGR-0521 | C | P | Gary Pickeral | McD | 2020-03-18 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-08-14 | Dave Goldak
HRS-01 | HRS-01 | PI18046 | Verified | See attached photo DSC00018; need to verify 'Pipe Tech & Prod.' Are on approved vendor list, 1C-HRS-PD-HGR-0516 | D | P | Dave Goldak | McD | 2020-03-18 | Dave Goldak | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
HRS-01 | HRS-01 | PI18047 | Verified | See attached photo DSC00021; Missing/"Home-made" handle, 1B-HRS-V-0032 | C | P | James Beech | McD | 2020-03-18 | James Beech | Comm | 2020-04-16 | James Beech | 2020-04-16 | Michael Law
HRS-01 | HRS-01 | PI18048 | Verified | See attached photo DSC00023; Trapeze not plumb, 1C-HRS-HGR-0513 | C | P | James Beech | McD | 2020-03-18 | James Beech | Comm | 2020-05-27 | James Beech | 2021-05-27 | John Watts
HRS-01 | HRS-01 | PI18049 | Verified | See attached photo DSCN1883; #9 wire installed in lieu of cotter pin, 1C-HRS-HGR-0521 | C | P | Tim Green | McD | 2020-03-18 | Tim Green | Comm | 2020-06-11 | Tim Green | 2021-02-01 | Dave Goldak
HRS-01 | HRS-01 | PI18050 | Verified | See attached photo DSC00043; Equipment used not per design, 1B-HRS-HGR-0522 | C | P | Gary Pickeral | McD | 2020-03-18 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-24 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18051 | Verified | See attached photo DSC00061; Flex conduit grounding disconnected, 1A-HRS-TW-0087B | C | E | Chris Colvin | McD | 2020-03-18 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2020-07-28 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18052 | Verified | See attached photo DSC00063; Equipment used not per design, 1B-HRS-HGR-0520 | C | P | Gary Pickeral | McD | 2020-03-18 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-24 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18053 | Verified | See attached photo DSC00065; Flex conduit grounding disconnected, 1B-HRS-TW-0087A, 1B-HRS-TW-0087B, 1B-HRS-TW-0087C | C | E | Chris Colvin | McD | 2020-03-18 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2020-07-28 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18054 | Verified | See attached photo DSC00067; Equipment used not per design, 1B-HRS-HGR-0533 | C | P | Gary Pickeral | McD | 2020-03-18 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-24 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18055 | Verified | See attached photo DSC00069; Equipment used not per design and North Hanger rod not plumb, 1B-HRS-HGR-0540. Pipe Suports 1A-HRS-PD-HGR-0539 and 1A-HRS-PD-HGR-0523 to be put on Cold Position | C | P | Tim Green | McD | 2020-03-18 | Tim Green | Comm | 2020-05-29 | James Beech | 2020-07-24 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18056 | Verified | See attached photo DSC00077; Equipment used not per design, 1A-HRS-HGR-0517 | C | P | Tim Green | McD | 2020-03-18 | Tim Green | Comm | 2020-08-07 | Tim Green | 2020-08-14 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18057 | Verified | See attached photo DSC00079; Equipment used not per design, 1A-HRS-HGR-0539 | C | P | Tim Green | McD | 2020-03-18 | Tim Green | Comm | 2020-05-29 | James Beech | 2020-07-24 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18058 | Verified | See attached photo DSC00081; hanger not centered North/south. 2"Gap south, 0" gap North. , 1A-HRS-HGR-0535 | C | P | Gary Pickeral | McD | 2020-03-18 | Gary Pickeral | Comm | 2020-05-21 | Gary Pickeral | 2020-07-24 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18059 | Verified | See attached photo DCS00085; TE is clamped onto line, not shown in PID or isometric, 1A-HRS-P41-0036-01 | C | P | Tim Green | McD | 2020-03-18 | Tim Green | Comm | 2020-05-29 | James Beech | 2020-07-24 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18060 | Verified | See attached photo DSC00087; Hanger rod is bent, 1B-HRS-HGR-0001 | C | P | Tim Green | McD | 2020-03-18 | Tim Green | Comm | 2020-05-29 | James Beech | 2020-07-28 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18061 | Verified | See attached photo DSC00090; Shoe not flat on support, 1B-HRS-HGR-0002 | C | P | James Beech | McD | 2020-03-18 | James Beech | Comm | 2020-05-27 | James Beech | 2020-07-28 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18062 | Verified | See attached photo DCS00092; TE is clamped onto line, not shown in PID or isometric, 1B-HRS-P41-0036-01 | C | P | James Beech | McD | 2020-03-18 | James Beech | Comm | 2020-05-27 | James Beech | 2020-07-24 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18063 | Verified | See attached photo DSC00094; Hanger rod is bent, 1B-HRS-HGR-0003 | C | P | Tim Green | McD | 2020-03-18 | Tim Green | Comm | 2020-08-12 | Tim Green | 2020-08-14 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18064 | Verified | See attached photo DSC00098; not centered East/West, 1B-HRS-HGR-0039 | C | P | James Beech | McD | 2020-03-18 | James Beech | Comm | 2020-05-27 | James Beech | 2020-07-28 | Nelson Eichelberger
HRS-01 | HRS-01 | PI18128 | Verified | Hot Reheat bypass valves do not seat on 1A Unit. | C | P | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2020-04-30 | John Watts
HRS-01 | HRS-01 | PI18129 | Verified | Hot Reheat bypass valves do not seat on 1B Unit. | C | P | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2021-01-05 | Keith Pollock
HRS-01 | HRS-01 | PI18135 | Verified | Hot Reheat Bypass Valve Accumulator tanks for instrument AIR draw the header down every time the valve is operated. | C | P | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-05-05 | William Mitchell | 2021-02-01 | Dave Goldak
HTS-01 | HTS-01 | PI09744 | Verified | Complete heat trace and insulation on .5 inch Service Air Receiver drain piping. | C | E | Sheri Fritz | TRI | 2019-10-22 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI13708 | Verified | Complete heat trace and isulation for SWS-01. | C | E | Sheri Fritz | TRI | 2019-12-01 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI14582 | Verified | Complete heat trace at discharge Line No. 8-10-OWS-0010 (sample point) | C | E | Sheri Fritz | TRI | 2019-12-07 | Sheri Fritz | Comm | 2020-04-29 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI15753 | Verified | Install heat trace, line 6-1A-FGS-0265-601D2-FP-2.0-ET | C | E | Sheri Fritz | TRI | 2020-01-09 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI15754 | Verified | Install heat trace, line 8-1A-FGS-0270-301D1-FP-2.0-ET | C | E | Sheri Fritz | TRI | 2020-01-09 | Sheri Fritz | Comm | 2020-01-20 | Tim Smith | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI15755 | Verified | Install heat tracel, line 1-1A-FGS-0265-601D2-FP-2.0-ET | C | E | Sheri Fritz | TRI | 2020-01-09 | Sheri Fritz | Comm | 2020-01-20 | Tim Smith | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI15756 | Verified | Install heat tracel, line 2-1A-FGS-0270-301D1-FP-2.0-ET | C | E | Sheri Fritz | TRI | 2020-01-09 | Sheri Fritz | Comm | 2020-01-20 | Tim Smith | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI15757 | Verified | Install heat trace, line 6-1A-FGS-0270-301D1-FP-2.0-ET | C | E | Sheri Fritz | TRI | 2020-01-09 | Sheri Fritz | Comm | 2020-01-20 | Tim Smith | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI15758 | Verified | Install heat trace, line 8-1A-FGS-0275-301D1-FP-2.0-ET | C | E | Sheri Fritz | TRI | 2020-01-09 | Sheri Fritz | Comm | 2020-01-20 | Tim Smith | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI15759 | Verified | Install heat trace, line 2-1A-FGS-0215-151D1-FP-2.0-ET | C | E | Sheri Fritz | TRI | 2020-01-09 | Sheri Fritz | Comm | 2020-01-20 | Tim Smith | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI15799 | Verified | Install heat trace, line 1-1A-FGS-0238-601D2-FP-2.0-ET | C | E | Sheri Fritz | TRI | 2020-01-09 | Sheri Fritz | Comm | 2020-01-20 | Tim Smith | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI15800 | Verified | Install heat trace, line 1-1A-FGS-0239-601D2-FP-2.0-ET | C | E | Sheri Fritz | TRI | 2020-01-09 | Sheri Fritz | Comm | 2020-01-20 | Tim Smith | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI15801 | Verified | Install heat trace, line 1-1A-FGS-0301-601D2-FP-2.0-ET | C | E | Sheri Fritz | TRI | 2020-01-09 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI15621 | Verified | Install heat trace, line 0.25-10-FGS-0114-996X2-AS-1.0-ET | C | E | Sheri Fritz | TRI | 2020-01-08 | Sheri Fritz | Comm | 2020-04-03 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI16030 | Verified | 1B-HTS-DSW-0002 - Conduit feeding disconnect needs additional support (above BFW BLDG) | C | E | Chris Colvin | McD | 2020-01-14 | Chris Colvin | Const | 2020-05-06 | Matt Gilmore | 2020-05-07 | Michael Law
HTS-01 | HTS-01 | PI16054 | Verified | Seal penetrations in Section 9 of 1B-NJS_MCC-0005 for 1B-HTS-DSW-0001 & 0002 in the HRSG B PDC. | B | E | Chris Colvin | McD | 2020-01-16 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI16057 | Verified | Complete heat trace at Line No. 1-1A-CTS-0115, 1" drain line at GT Blade Wash Drain, north end, outside of GT A enclosure | C | E | Sheri Fritz | TRI | 2020-01-16 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-04-08 | Bernard Stasse
HTS-01 | HTS-01 | PI16177 | Verified | Finish heat trace and insulation on 10-TSW-V-0004; 1" Sample line | C | E | Sheri Fritz | PCI | 2020-01-20 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI16178 | Verified | Finish heat trace and insulation on 1.5-FP-2.0-ET 1.5" line to 10-TSW-AE-0011; Analysis Sensing Element | C | E | Sheri Fritz | PCI | 2020-01-20 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI16357 | Verified | Heat trace cable installed over equipment ID tag, 1B-FGS-SRV-0270 | C | E | Sheri Fritz | TRI | 2020-01-28 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI16461 | Verified | 10-HTS-PNL-0007 - conduit needs additional support (Raw Water). | C | E | Sheri Fritz | TRI | 2020-01-31 | Sheri Fritz | Const | 2020-04-29 | Michael Law | 2020-04-29 | Michael Law
HTS-01 | HTS-01 | PI16462 | Verified | 10-HTS-PNL-0007 - install drain plug in bottom LB cover (Raw Water). | C | E | Sheri Fritz | TRI | 2020-01-31 | Sheri Fritz | Const | 2020-04-29 | Michael Law | 2020-04-29 | Michael Law
HTS-01 | HTS-01 | PI16463 | Verified | 10-HTS-PNL-0007 - seal conduits (Raw Water). | C | E | Sheri Fritz | TRI | 2020-01-31 | Sheri Fritz | Const | 2020-04-29 | Michael Law | 2020-04-29 | Michael Law
HTS-01 | HTS-01 | PI16464 | Verified | 10-HTS-XFM-0007 - clamp ground to concrete (Raw Water). | C | E | Chris Colvin | McD | 2020-01-31 | Chris Colvin | Const | 2020-05-04 | Matt Gilmore | 2020-05-06 | Michael Law
HTS-01 | HTS-01 | PI16919 | Verified | Complete heat trace and insulation on MBL03AA934 AND MBL03AA933 1" drain valves, downstream of MBL03AA704; GT Anti-Icing Air Temperature Control Valve (B), GT A Inet Air Filter House grating platform, East side | C | Q | Sheri Fritz | TRI | 2020-02-18 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI16921 | Verified | Complete heat trace on MBL03AA924 AND MBL03AA923 1" drain valves, downstream of MBL03AA703; GT Anti-Icing Air Temperature Control Valve (A), GT A Inet Air Filter House grating platform, East side | C | Q | Sheri Fritz | TRI | 2020-02-18 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-04-07 | Randy Carpenter
HTS-01 | HTS-01 | PI16991 | Verified | Complete heat trace and insulation on 1" drain line downstream of MBL03AA704; GT B Anti-Icing Air Temperature Control Valve, GT B Inlet Air Filter House grating platform, West side | C | E | Sheri Fritz | TRI | 2020-02-18 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-04-07 | Randy Carpenter
HTS-01 | HTS-01 | PI16992 | Verified | Complete heat trace and insulation on 1" drain line downstream of MBL03AA101; GT B 10" Anti-Icing Isolation Valve , GT B Inlet Air Filter House grating platform, West side | C | E | Sheri Fritz | TRI | 2020-02-18 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-04-07 | Randy Carpenter
HTS-01 | HTS-01 | PI16993 | Verified | Complete heat trace and insulation on 1" drain line downstream of MBL03AA703; GT B Anti-Icing Air Temperature Control Valve , GT B Inlet Air Filter House grating platform, West side | C | E | Sheri Fritz | TRI | 2020-02-18 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-04-07 | Randy Carpenter
HTS-01 | HTS-01 | PI17154 | Verified | Complete heat trace as required on CWC | C | E | Sheri Fritz | TRI | 2020-02-22 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17162 | Verified | Wiring incomplete at South side of Clearwell Pumps A & B | C | E | Sheri Fritz | TRI | 2020-02-22 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17166 | Verified | Incomplete wiring at Clarifier Sludge Transfer Pump skid | C | E | Sheri Fritz | TRI | 2020-02-22 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17167 | Verified | Incomplete wiring at Clarifier Sludge Transfer Pump Tank | C | E | Sheri Fritz | TRI | 2020-02-22 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17168 | Verified | Incomplete wiring at MWS-P-0100 A & B; Clarifier Sand Recirculation Pump A & B | C | E | Sheri Fritz | TRI | 2020-02-22 | Sheri Fritz | Comm | 2020-04-29 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17184 | Verified | Complete wiring at Clarifier 25% Caustic Metering Pumps A & B skid | C | E | Sheri Fritz | TRI | 2020-02-22 | Sheri Fritz | Comm | 2020-04-29 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17187 | Verified | Complete wiring at Clarifier Coagulant Metering Pump A & B skid | B | E | Chris Colvin | McD | 2020-02-22 | Chris Colvin | Comm |  |  | 2020-02-27 | Michael Law
HTS-01 | HTS-01 | PI17188 | Verified | Complete wiring at South side of Polymer Feed Pump skid enclosure | B | E | Chris Colvin | McD | 2020-02-22 | Chris Colvin | Comm |  |  | 2020-02-27 | Michael Law
HTS-01 | HTS-01 | PI17238 | Verified | Complete heat trace at 1B-DWS-SWR-0017; 1B GT Control Package Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17241 | Verified | Complete heat trace at 10-DWS-SWR-0012; Aqueous Ammonia Tank and Unloading Pad Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17243 | Verified | Complete heat trace at 10-DWS-SWR-0013; Aqueous Ammonia Tank and Unloading Pad Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17245 | Verified | Complete heat trace at 1B-DWS-SWR-0010; Phosphate Feed Skid Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17248 | Verified | Complete heat trace at 1A-DWS-SWR-0006; 1A Phosphate Feed Skid Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17251 | Verified | Complete heat trace at 1C-DWS-SWR-0009; 1C Condensate Chem Feed Skid Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17254 | Verified | Complete heat trace at 10-DWS-SWR-0008; Filter Press Area Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17256 | Verified | Complete heat trace at 10-DWS-SWR-0007; Filter Press Area Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17258 | Verified | Complete heat trace at 10-DWS-SWR-0005; Cooling Tower Chemical Storage Area Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17263 | Verified | Complete heat trace at 10-DWS-SWR-0004; Makeup Water Treatment Area Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17266 | Verified | Complete heat trace at 10-DWS-SWR-0003; Water Treatment Building Chemical Storage Area Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-29 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17269 | Verified | Complete heat trace at 10-DWS-SWR-0002; Water Treatment Building Equipment Area Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-29 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17272 | Verified | Complete heat trace at 10-DWS-SWR-0015; Batch Neutralization Area Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-29 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17275 | Verified | Complete heat trace at 1A-DWS-SWR-0016; 1A GT Control Package Emergency Shower/Eyewash station | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-01 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17286 | Verified | Finish heat trace inside 1B Feedwater Pump B enclosure | C | E | Sheri Fritz | TRI | 2020-02-28 | Sheri Fritz | Comm | 2020-04-29 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI18167 | Verified | 1B-HTS-PNL-0001 Seal off panel after commissioning | C | E | Sheri Fritz | TRI | 2020-03-21 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI18168 | Verified | 1B-HTS-PNL-0001 Missing clip on panel cover | C | E | Sheri Fritz | TRI | 2020-03-21 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI18169 | Verified | 1B-HTS-PNL-0001 Loose cables on terminal strip | C | E | Sheri Fritz | TRI | 2020-03-21 | Sheri Fritz | Comm | 2020-04-03 | Sheri Fritz | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI18171 | Verified | 1B-HTS-PNL-0001 Grounding bushing on 1 1/2 conduit | C | E | Sheri Fritz | TRI | 2020-03-21 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI17779 | Verified | DSC00018; ASF Lines P41-0051, P41-0050, Entire lines not insulated and heat traced not per specification and drawings. | C | I | Sheri Fritz | PCI | 2020-03-12 | Sheri Fritz | Const | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
HTS-01 | HTS-01 | PI18292 | Verified | 10-HTS-PNL-0007 Place laminated panel schedule inside panel | C | E | Josh Koerner | TRI | 2020-05-15 | Josh Koerner | Comm | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18293 | Verified | Provide laminated panel schedule : 10-HTS-PNL-0001 | C | E | Josh Koerner | TRI | 2020-05-18 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18294 | Verified | Replace bolts on the HTS transformer : 10-HTS-PNL-0001 | C | E | Josh Koerner | TRI | 2020-05-18 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18295 | Verified | Remove insulation to take out flex chem feed safety shower sodium hypochlorite bleach tank | C | E | Sheri Fritz | TRI | 2020-05-18 | Sheri Fritz | Const | 2020-05-26 | Sheri Fritz | 2020-06-01 | Mike Tabbert
HTS-01 | HTS-01 | PI18296 | Verified | HTS JB on filter press to move JB box to allow good access for the totes | C | E | Josh Koerner | TRI | 2020-05-18 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18297 | Verified | MWS area missing drain on conduit inside sodium hydroxide caustic bundwall | C | E | Sheri Fritz | TRI | 2020-05-18 | Sheri Fritz | Const | 2020-05-26 | Sheri Fritz | 2020-06-01 | Mike Tabbert
HTS-01 | HTS-01 | PI18298 | Open | Tag all JB's : 10-HTS-PNL-0001 | C | E | Richard McSpadden | TRI | 2020-05-18 | Richard McSpadden | Const
HTS-01 | HTS-01 | PI18299 | Verified | Drain missing on conduit fire pump house cover X3 | C | E | Sheri Fritz | TRI | 2020-05-18 | Sheri Fritz | Const | 2020-05-26 | Sheri Fritz | 2020-06-01 | Mike Tabbert
HTS-01 | HTS-01 | PI18300 | Verified | Demin area drain missing on conduit multiple spots, covers also missing | C | E | Sheri Fritz | TRI | 2020-05-18 | Sheri Fritz | Const | 2020-05-26 | Sheri Fritz | 2020-06-01 | Mike Tabbert
HTS-01 | HTS-01 | PI18301 | Verified | Additional support on the conduit at demin pump area | C | E | Sheri Fritz | TRI | 2020-05-18 | Sheri Fritz | Const | 2020-05-26 | Sheri Fritz | 2020-06-01 | Mike Tabbert
HTS-01 | HTS-01 | PI18302 | Verified | Drains on conduit missing demin tank area, multiple spots | C | E | Josh Koerner | TRI | 2020-05-18 | Josh Koerner | Const | 2020-06-01 | Josh Koerner | 2020-06-09 | Mike Tabbert
HTS-01 | HTS-01 | PI18366 | Verified | Install Laminated Panel Schedules in all Heat Trace Control Panels | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2021-03-03 | John Watts
HTS-01 | HTS-01 | PI18367 | Verified | Pour Sealoffs after Check Out | C | E | Richard McSpadden | TRI | 2020-05-27 | Richard McSpadden | Const | 2021-03-03 | Eric Policarpio | 2021-03-03 | John Watts
HTS-01 | HTS-01 | PI18368 | Verified | Check all conduit for low point drain fittings, install if needed. | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2021-03-03 | John Watts
HTS-01 | HTS-01 | PI18369 | Verified | Clean out all heat trace control panels | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2021-03-03 | John Watts
HTS-01 | HTS-01 | PI18370 | Verified | 1A-0003, install kick plate around conduit openings in grading. | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-01 | Josh Koerner | 2020-06-09 | Mike Tabbert
HTS-01 | HTS-01 | PI18371 | Verified | 1A-0003, Install conduit supports within 30 inches of panel. | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-01 | Josh Koerner | 2020-06-09 | Mike Tabbert
HTS-01 | HTS-01 | PI18372 | Verified | 1A HRSG Top, install conduit supports within 30 inches of transformer. | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-09 | Mike Tabbert | 2020-06-09 | Mike Tabbert
HTS-01 | HTS-01 | PI18373 | Verified | 1A HRSG Top, Install conduit supports 30 inches from device. | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18374 | Verified | 1A HRSG Top, Replace J-Bolts on strut support, north east corner. | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-01 | Josh Koerner | 2020-06-09 | Mike Tabbert
HTS-01 | HTS-01 | PI18375 | Verified | 1A HRSG Top, west end of steam drum conduit not supported and loss. | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18376 | Verified | 1A HRSG Top, Conduit on southwest corner not supported. | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18377 | Open | 1B-0003, door will not open due to bent frame. | C | E | Richard McSpadden | TRI | 2020-05-27 | Richard McSpadden | Const
HTS-01 | HTS-01 | PI18378 | Verified | 1B-0003, Install conduit supports 30 inches from panel. | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18379 | Verified | 1B HRSG top, install conduit support north west corner 3/4 inch riser. | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18380 | Verified | 1B HRSG Top, install conduit support 10-HTS-CAB-0108. | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18381 | Verified | 1B HRSG Top, install end cap on tube bundle heat trace next to 9225C. | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-01 | Josh Koerner | 2020-06-16 | Mike Tabbert
HTS-01 | HTS-01 | PI18382 | Verified | 1B HRSG Top, install conduit supports within 30 inches of transformer. | C | E | Josh Koerner | TRI | 2020-05-27 | Josh Koerner | Const | 2020-06-01 | Josh Koerner | 2020-06-09 | Mike Tabbert
HTS-01 | HTS-01 | PI18405 | Verified | 1A HRSG West Platform #27 : Heat trace tube support bracket connection failed. Support hanging from one clamp. | C | P | Tim Green | McD | 2020-06-08 | Tim Green | Const | 2020-06-08 | Tim Green | 2020-06-18 | Dave Goldak
HTS-01 | HTS-01 | PI18454 | Verified | 1A Nooter Platform #52. Bolt down heat trace tubing support to deck. | C | E | Richard McSpadden | TRI | 2020-06-09 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
HTS-01 | HTS-01 | PI18519 | Verified | 1A HRSG Top, MI cables need to be formed in a neat and workmanship like manner, cables laying on grading, cables are unsopported and in some cases in harms way | C | E | Josh Koerner | TRI | 2020-06-09 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18646 | Verified | 1C-HTS-PNL-0002, Needs tag installed outside front door. | C | E | Josh Koerner | TRI | 2020-06-19 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18647 | Verified | 1C-HTS-PNL-0002, Transformer ground cable needs to be strapped in place. | C | E | Richard McSpadden | TRI | 2020-06-19 | Richard McSpadden | Const | 2021-02-22 | Eric Policarpio | 2021-02-22 | Dave Goldak
HTS-01 | HTS-01 | PI18648 | Open | 1C-HTS-PNL-0002, Pour seals after commisioning is complete and paint plugs red. | C | E | Richard McSpadden | TRI | 2020-06-19 | Richard McSpadden | Const |  |  | 2021-07-22 | John Watts
HTS-01 | HTS-01 | PI18649 | Open | 1C-HTS-PNL-0002, Conduilet covers missing top fo conduit runs above panel. | C | E | Richard McSpadden | TRI | 2020-06-19 | Richard McSpadden | Const |  |  | 2021-07-22 | John Watts
HTS-01 | HTS-01 | PI18650 | Verified | 1C-HTS-PNL-0002, Generate and install laminated panel schedule. | C | E | Josh Koerner | TRI | 2020-06-19 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18651 | Verified | 1C-HTS-PNL-0002, Install 3 door clamps at bottom of door. | C | E | Josh Koerner | TRI | 2020-06-19 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18652 | Verified | 1C-HTS-PNL-0002, Clean out bottom of panel. | C | E | Josh Koerner | TRI | 2020-06-19 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18653 | Open | 10-HTS-CAB-0200, Enclosure heater not hooked up. | C | E | Richard McSpadden | TRI | 2020-06-19 | Richard McSpadden | Const |  |  | 2021-07-23 | John Watts
HTS-01 | HTS-01 | PI18654 | Verified | West end of condenser, ground floor, MI cable needs to be rerouted and formed. | C | E | Josh Koerner | TRI | 2020-06-19 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18655 | Verified | Tighten all sealtight connectors STG heat trace, about 50 % are loose. | C | E | Josh Koerner | TRI | 2020-06-19 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18656 | Verified | 1C-HTS-CAB-0202, Remove tape and replace with tie raps to secure cable. | C | E | Josh Koerner | TRI | 2020-06-19 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18657 | Verified | 1C-HTS-CAB-0206, Reroute heat trace cable in enclosure. | C | E | Josh Koerner | TRI | 2020-06-19 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18658 | Verified | 1C-HTS-PNL-0003, Pour all conduit seals after commisioning. | A | E | Chris Colvin | McD | 2020-06-19 | Chris Colvin | Const | 2020-07-10 | Mike Tabbert | 2020-07-10 | Mike Tabbert
HTS-01 | HTS-01 | PI18659 | Verified | 1C-HTS-PNL-0003, Missing LB covers from conduits coming out of bottom of panel | C | E | Chris Colvin | McD | 2020-06-19 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18660 | Verified | 1C-HTS-PNL-0003, Need laminated panel schedule installed in panel. | C | E | Josh Koerner | TRI | 2020-06-19 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18661 | Verified | 1C-HTS-PNL-0003, Install wireway cover. | C | E | Josh Koerner | TRI | 2020-06-19 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18662 | Verified | 1C-HTS-PNL-0003, Need drains installed in backside Tee's. | C | E | Chris Colvin | McD | 2020-06-19 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18663 | Verified | 1C-HTS-XFM-0003, Bolts missing from top cover of transformer. | B | E | Josh Koerner | TRI | 2020-06-19 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18664 | Verified | 1C-HTS-PNL-0003, Panel needs tag front cover. | C | E | Josh Koerner | TRI | 2020-06-19 | Josh Koerner | Const | 2020-06-24 | Tim Smith | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18665 | Verified | 1C-HTS-PNL-0003, LB covers missing 2" conduitabove panel, LB and Tee covers missing ground level STG east end. | C | E | Chris Colvin | McD | 2020-06-19 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18666 | Verified | 1C-HTS-CAB-6301, Loose sealtight connectors | C | E | Chris Colvin | McD | 2020-06-19 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18667 | Verified | Loose sealtight connectors and covers missing in Some areas of heat trace installation. | C | E | Chris Colvin | McD | 2020-06-19 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-08-24 | Mike Tabbert
HTS-01 | HTS-01 | PI18668 | Verified | J-Box needs to be supported 32 44 at safety shower heater. | C | E | Chris Colvin | McD | 2020-06-19 | Chris Colvin | Const | 2020-08-20 | Chris Colvin | 2020-08-21 | Mike Tabbert
HTS-01 | HTS-01 | PI18669 | Open | Connection box supported by tie wire, finger rack A, South Top. | C | E | Richard McSpadden | TRI | 2020-06-19 | Richard McSpadden | Const
HTS-01 | HTS-01 | PI18670 | Verified | MI Cable not terminated LP Steam, NE Mez, 1C-LPS-PDIT-0013. | C | E | Chris Colvin | McD | 2020-06-19 | Chris Colvin | Const | 2020-08-20 | Chris Colvin | 2020-08-21 | Mike Tabbert
HTS-01 | HTS-01 | PI18682 | Verified | Remove HTS tubing and electrical supports suspended from CO2 and Service Air Piping - north side of condenser. Multiple locations. | C | P | Richard McSpadden | TRI | 2020-06-24 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
HTS-01 | HTS-01 | PI18892 | Verified | 1B HRSG West - elev 577 : two severed HTS cables | C | E | Richard McSpadden | TRI | 2020-07-08 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
HTS-01 | HTS-01 | PI18893 | Verified | 1B HRSG West - elev 577 : incomplete jacket/insulation (blue) Sample lines | C | Q | Richard McSpadden | PCI | 2020-07-08 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-11-11 | Dave Goldak
HTS-01 | HTS-01 | PI18894 | Verified | 1B HRSG West - elev 590 +/- : incomplete jacket/insulation (yellow) Sample line | C | Q | Richard McSpadden | PCI | 2020-07-08 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-11-11 | Dave Goldak
HTS-01 | HTS-01 | PI18895 | Verified | 1B HRSG West - elev 590 +/- : one severed HTS cable | C | E | Richard McSpadden | TRI | 2020-07-08 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-11-11 | Dave Goldak
HTS-01 | HTS-01 | PI18896 | Verified | 1B HRSG West - elev 590 +/- : one incomplete jacket/insulation (green) Sample line | C | Q | Richard McSpadden | PCI | 2020-07-08 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-11-11 | Dave Goldak
IAS-01 | IAS-01 | PI01152 | Verified | Missing cable tags in compressor A disconnect switch panel. | A | E | Shannon Savoy | McD | 2019-05-24 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-06-06 | Shannon Scott
IAS-01 | IAS-01 | PI01153 | Verified | Install instrument/plug-in cable at compressor skids A & B panels 10-IAS-CP-0100A & B. | B | E | Stuart Herring | McD | 2019-05-24 | Stuart Herring | Const | 2019-10-07 | Stuart Herring | 2019-10-07 | Stuart Herring
IAS-01 | IAS-01 | PI01154 | Verified | Tighten seal tite at compressor skid B. | A | E | Shannon Savoy | McD | 2019-05-24 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-06-06 | Shannon Scott
IAS-01 | IAS-01 | PI01155 | Verified | Tighten condulet for comp. B disconnect switch panel. | A | E | Shannon Savoy | McD | 2019-05-24 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
IAS-01 | IAS-01 | PI01156 | Verified | Missing bolts on condulet for comp. B disconnect switch panel. | B | E | Shannon Savoy | McD | 2019-05-24 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
IAS-01 | IAS-01 | PI01157 | Verified | Complete fiber patch panel (located at compressor B). | B | E | Luis Cantu | McD | 2019-05-24 | Luis Cantu | Const | 2019-06-13 | Luis Cantu | 2019-06-13 | Mike Tabbert
IAS-01 | IAS-01 | PI01158 | Verified | Missing cable tags in comp. B disconnect switch panel. | A | E | Shannon Savoy | McD | 2019-05-24 | Shannon Savoy | Const | 2019-06-07 | Shannon Savoy | 2019-06-07 | Mike Tabbert
IAS-01 | IAS-01 | PI01159 | Verified | Cold galv. all conduit supports where needed. | C | E | Luis Cantu | McD | 2019-05-24 | Luis Cantu | Const | 2019-06-19 | Luis Cantu | 2019-06-28 | Mike Tabbert
IAS-01 | IAS-01 | PI01160 | Verified | Dress up cables in compressor A control panel. | A | E | Shannon Savoy | McD | 2019-05-24 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
IAS-01 | IAS-01 | PI01161 | Verified | Missing 2 condulet covers at 10-IAS-PIT-0106 - located on STG mezz. deck ( 1 at instrument, 1 below grating). | B | E | Shannon Savoy | McD | 2019-05-24 | Shannon Savoy | Const | 2019-05-31 | Shannon Savoy | 2019-06-03 | Mike Tabbert
IAS-01 | IAS-01 | PI01162 | Verified | Adjust seal tite at compressor A control panel. | A | E | Shannon Savoy | McD | 2019-05-24 | Shannon Savoy | Const | 2019-05-28 | Shannon Savoy | 2019-05-30 | Mike Tabbert
IAS-01 | IAS-01 | PI01163 | Verified | Replace plastic plug with steel plug for 10-IAS-PIT-0106 - STG mezz. deck. | A | I | Gonzalo Pena | McD | 2019-05-24 | Gonzalo Pena | Const | 2019-05-29 | Gonzalo Pena | 2019-05-30 | Mike Tabbert
IAS-01 | IAS-01 | PI01164 | Verified | Tighten seal tite at 10-IAS-PIT-0106 - STG mezz. deck. | A | E | Shannon Savoy | McD | 2019-05-24 | Shannon Savoy | Const | 2019-05-29 | Shannon Savoy | 2019-05-30 | Mike Tabbert
IAS-01 | IAS-01 | PI01165 | Verified | Seal penetrations in main PDC (after comm.) | C | E | Luis Cantu | McD | 2019-05-24 | Luis Cantu | Const | 2019-07-18 | Ken Mundy | 2019-07-29 | Mike Tabbert
IAS-01 | IAS-01 | PI01167 | Verified | 10IASC0001 . Install Conduits, Pull & Terminate the cable | B | E | Shannon Savoy | McD | 2019-05-24 | Shannon Savoy | Const | 2019-06-07 | Shannon Savoy | 2019-06-07 | Mike Tabbert
IAS-01 | IAS-01 | PI01168 | Verified | 10IASC0003 . Install Conduits, Pull & Terminate the cable | B | E | Shannon Savoy | McD | 2019-05-24 | Shannon Savoy | Const | 2019-06-07 | Shannon Savoy | 2019-06-07 | Mike Tabbert
IAS-01 | IAS-01 | PI01169 | Verified | 10IASK0005 . Install Conduits, Pull & Terminate the cable | B | E | Luis Cantu | McD | 2019-05-24 | Luis Cantu | Const | 2019-06-13 | Luis Cantu | 2019-06-13 | Mike Tabbert
IAS-01 | IAS-01 | PI01170 | Verified | 10DCSX0149 . Install Conduits, Pull & Terminate the cable | B | E | Luis Cantu | McD | 2019-05-24 | Luis Cantu | Const | 2019-06-13 | Luis Cantu | 2019-06-13 | Mike Tabbert
IAS-01 | IAS-01 | PI01171 | Verified | 10DCSX0150 . Install Conduits, Pull & Terminate the cable | B | E | Luis Cantu | McD | 2019-05-24 | Luis Cantu | Const | 2019-06-13 | Luis Cantu | 2019-06-13 | Mike Tabbert
IAS-01 | IAS-01 | PI01172 | Verified | 10DCSX0151 . Install Conduits, Pull & Terminate the cable | B | E | Luis Cantu | McD | 2019-05-24 | Luis Cantu | Const | 2019-06-13 | Luis Cantu | 2019-06-13 | Mike Tabbert
IAS-01 | IAS-01 | PI01173 | Verified | Missing tags in panels 10-IAS-CP0100A/B, 10-IAS-DSW-0100A/B | A | E | Luis Cantu | McD | 2019-05-24 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-06-13 | Mike Tabbert
IAS-01 | IAS-01 | PI01174 | Verified | Missing vendor cable tags in panels 10-IAS-CP0100A/B, 10-IAS-DSW-0100A/B | A | E | Luis Cantu | McD | 2019-05-24 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-06-13 | Mike Tabbert
IAS-01 | IAS-01 | PI01175 | Verified | Install panels 1C-ESH-PNL-0002 & 10-ESF-PNL-0001 | A | E | Luis Cantu | McD | 2019-05-24 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-06-13 | Mike Tabbert
IAS-01 | IAS-01 | PI01176 | Verified | Install fiber optic patch panel 10 -IAS-PNL-0001 | A | E | Sheri Fritz | ITS | 2019-05-24 | Sheri Fritz | Const | 2019-06-13 | Luis Cantu | 2019-06-13 | Mike Tabbert
IAS-01 | IAS-01 | PI01177 | Verified | Complete Meg Sheets and Torque Sheets & equipment completions forms | A | E | Luis Cantu | McD | 2019-05-24 | Luis Cantu | Const | 2019-06-14 | Luis Cantu | 2019-06-24 | Mike Tabbert
IAS-01 | IAS-01 | PI01257 | Verified | 10-IAS-SKID-0100A missing tagging on all valves, instruments, gauges, etc that are labeled in P&ID | B | M | Joshua Sturgeon | ACS | 2019-05-28 | Joshua Sturgeon | Const | 2019-08-02 | Joshua Sturgeon | 2019-08-07 | Joshua Sturgeon
IAS-01 | IAS-01 | PI01258 | Verified | 10-IAS-SKID-0100B missing tagging on all valves, instruments, gauges, etc that are labeled in P&ID | B | M | Joshua Sturgeon | ACS | 2019-05-28 | Joshua Sturgeon | Const | 2019-08-02 | Joshua Sturgeon | 2019-08-07 | Joshua Sturgeon
IAS-01 | IAS-01 | PI01260 | Verified | Instrument Air Receiver Information Tag painted over | B | M | Joshua Sturgeon | ACS | 2019-05-28 | Joshua Sturgeon | Const | 2019-08-08 | Joshua Sturgeon | 2019-08-08 | Joshua Sturgeon
IAS-01 | IAS-01 | PI01427 | Verified | Check for hanger installation at air receiver. | C | P | Kelvin Cook | McD | 2019-06-07 | Kelvin Cook | Const | 2019-06-10 | Kelvin Cook | 2019-06-11 | Shannon Scott
IAS-01 | IAS-01 | PI01428 | Verified | Grout instrument tubing support at air receiver. | C | C | Johnny Campbell | McD | 2019-06-07 | Johnny Campbell | Const | 2019-10-10 | Jack Fields | 2019-10-15 | Shannon Scott
IAS-01 | IAS-01 | PI01429 | Verified | Verify SS instrument tray needs insulator where in contact with galvanized. | C | I | Gonzalo Pena | McD | 2019-06-07 | Gonzalo Pena | Const | 2019-06-21 | Gonzalo Pena | 2019-06-25 | Shannon Scott
IAS-01 | IAS-01 | PI01430 | Verified | Carbon contamination on SS welds at compressor skids. | C | X | James Beech | McD | 2019-06-07 | James Beech | Const | 2019-08-19 | Damon Turner | 2019-12-01 | Stuart Herring
IAS-01 | IAS-01 | PI01431 | Verified | Install 10-IAS-SRV-0100A&B at air compressor skids. | A | P | Damon Turner | McD | 2019-06-07 | Damon Turner | Const | 2019-06-17 | Damon Turner | 2019-06-17 | Kelvin Cook
IAS-01 | IAS-01 | PI01432 | Verified | Tag all valves in subsystem. | C | P | Kelvin Cook | McD | 2019-06-07 | Kelvin Cook | Const |  |  | 2020-02-06 | Kelvin Cook
IAS-01 | IAS-01 | PI01433 | Verified | Valve at Ammonia Tank missing bolts and gasket. | A | P | Terry Deaton | McD | 2019-06-07 | Terry Deaton | Const | 2019-06-07 | Terry Deaton | 2019-06-07 | Kelvin Cook
IAS-01 | IAS-01 | PI01434 | Verified | Complete IA piping at the fire pump house. | A | P | Terry Deaton | McD | 2019-06-07 | Terry Deaton | Const | 2019-06-10 | Terry Deaton | 2019-06-10 | Kelvin Cook
IAS-01 | IAS-01 | PI01435 | Verified | Even out stud spacing on flange at the water treatment building. | B | P | Damon Turner | McD | 2019-06-07 | Damon Turner | Const | 2019-06-10 | Kelvin Cook | 2019-10-07 | J.L. Bickham
IAS-01 | IAS-01 | PI01436 | Verified | Carbon contamination on flange at the water treatment building. | C | X | James Beech | McD | 2019-06-07 | James Beech | Const | 2019-08-19 | Damon Turner | 2020-01-03 | Nelson Eichelberger
IAS-01 | IAS-01 | PI01437 | Verified | Complete the stub-up at the Demin. tank area. | A | P | Terry Deaton | McD | 2019-06-07 | Terry Deaton | Const | 2019-06-10 | Terry Deaton | 2019-06-11 | Kelvin Cook
IAS-01 | IAS-01 | PI01438 | Verified | Clean the Instrument Air skids. | A | M | Shane Crowe | McD | 2019-06-07 | Shane Crowe | Const | 2019-06-14 | Shane Crowe | 2019-07-22 | Danny Pase
IAS-01 | IAS-01 | PI01440 | Verified | ISO 10-IAS-PD-P41-0114 is not installed. Need 1 1/4" x 1/2" NPT flange. | A | I | Gonzalo Pena | McD | 2019-06-07 | Gonzalo Pena | Const | 2019-06-13 | Gonzalo Pena | 2019-06-17 | Kelvin Cook
IAS-01 | IAS-01 | PI01441 | Verified | On ISO 10-IAS-PD-P40-0110-01 pipe support 10-IAS-PD-HGR-0172 is not installed | B | P | Damon Turner | McD | 2019-06-07 | Damon Turner | Const | 2019-06-14 | Damon Turner | 2019-07-26 | Kelvin Cook
IAS-01 | IAS-01 | PI01442 | Verified | On ISO 10-IAS-PD-P40-0111-02 pipe support 10-IAS-PD-HGR-0175 is not installed | B | P | Damon Turner | McD | 2019-06-07 | Damon Turner | Const | 2019-06-14 | Damon Turner | 2019-07-26 | Kelvin Cook
IAS-01 | IAS-01 | PI01443 | Verified | On ISO 10-IAS-PD-P40-0111-02 pipe support 10-IAS-PD-HGR-0176 is not installed | B | P | Damon Turner | McD | 2019-06-07 | Damon Turner | Const | 2019-06-14 | Damon Turner | 2019-07-26 | Kelvin Cook
IAS-01 | IAS-01 | PI01444 | Verified | On ISO 10-IAS-PD-P40-0111-02 pipe support 10-IAS-PD-HGR-0177 is not installed | B | P | Damon Turner | McD | 2019-06-07 | Damon Turner | Const | 2019-06-14 | Damon Turner | 2019-07-26 | Kelvin Cook
IAS-01 | IAS-01 | PI01445 | Verified | On ISO 10-IAS-PD-P40-0111-02 pipe support 10-IAS-PD-HGR-0178 is not installed | B | P | Damon Turner | McD | 2019-06-07 | Damon Turner | Const | 2019-06-14 | Damon Turner | 2019-07-26 | Kelvin Cook
IAS-01 | IAS-01 | PI01446 | Verified | On ISO 10-IAS-PD-P40-0111-02 pipe support 10-IAS-PD-HGR-0179 is not installed | B | P | Damon Turner | McD | 2019-06-07 | Damon Turner | Const | 2019-06-14 | Damon Turner | 2019-07-26 | Kelvin Cook
IAS-01 | IAS-01 | PI01447 | Verified | On ISO 10-IAS-PD-P40-0111-02 pipe support 10-IAS-PD-HGR-0180 is not installed | B | P | Damon Turner | McD | 2019-06-07 | Damon Turner | Const | 2019-06-14 | Damon Turner | 2019-08-08 | Kelvin Cook
IAS-01 | IAS-01 | PI01448 | Verified | ISO 10-IAS-PD-P40-0113-01 is not installed | A | P | Damon Turner | McD | 2019-06-07 | Damon Turner | Const | 2019-06-12 | Damon Turner | 2019-06-14 | Kelvin Cook
IAS-01 | IAS-01 | PI01449 | Verified | Pour foundation for pipe support at Demin. Tank. ISO: LK-10-IAS-PD-P41-0555-01. | B | C | Johnny Campbell | McD | 2019-06-11 | Johnny Campbell | Const | 2019-06-24 | Michael Law | 2019-06-25 | Kelvin Cook
IAS-01 | IAS-01 | PI01450 | Verified | Install pipe support at Demin. Tank. ISO: LK-10-IAS-PD-P41-0555-01. (need foundation poured) | B | P | Terry Deaton | McD | 2019-06-11 | Terry Deaton | Const | 2019-07-19 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-01 | IAS-01 | PI01470 | Verified | Repair internal tank coating and submit Clean & Close documentation. Replace gasket. | C | P | Kelvin Cook | ACS | 2019-06-17 | Kelvin Cook | Const |  |  | 2020-02-06 | Kelvin Cook
IAS-01 | IAS-01 | PI01471 | Verified | Cable 10IASC0001, Two terminations need to be made, Vendor to supply plug in terminal block for circuit board termination. | B | E | Luis Cantu | ACS | 2019-06-18 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-24 | Mike Tabbert
IAS-01 | IAS-01 | PI01472 | Verified | Cable 10IASC0003, Two terminations need to be made, Vendor to supply plug in terminal block for circuit board termination. | B | E | Luis Cantu | ACS | 2019-06-18 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-24 | Mike Tabbert
IAS-01 | IAS-01 | PI04720 | Verified | 10-IAS-FLT-0101A & 10-IAS-V-0101A (Air Compressor A) - Drain/Schader Valve is broken in the open position. Fitting is bent at an angle & valve does not work properly. | B | M | Reggie Brown | McD | 2019-09-03 | Reggie Brown | Comm |  |  | 2020-01-23 | Shannon Scott
IAS-01 | IAS-01 | PI09377 | Verified | Install discharge piping on 10-IAS-SRV-0100A; Compressor A discharge header safety relief valve | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-02-10 | Kelvin Cook | 2020-03-05 | Dave Goldak
IAS-01 | IAS-01 | PI09378 | Verified | Install discharge piping on 10-IAS-SRV-0100B; Compressor B discharge header safety relief valve | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-02-10 | Kelvin Cook | 2020-03-05 | Dave Goldak
IAS-01 | IAS-01 | PI09379 | Verified | Install discharge piping on 10-IAS-SRV-0104; Instrument Air Reciever Safety Relief Valve | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-02-10 | Kelvin Cook | 2020-03-05 | Dave Goldak
IAS-01 | IAS-01 | PI09380 | Verified | Clean and paint Instrument Air/Air Dryer Skid A base plate | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-08-07 | Dave Goldak
IAS-01 | IAS-01 | PI09381 | Verified | Clean and paint Instrument Air/Air Dryer Skid B base plate | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-08-07 | Dave Goldak
IAS-01 | IAS-01 | PI09382 | Verified | Install plastic caps on all unit strut around base of Instrument Air/Air Dryer Skid A | C | E | Chris Colvin | McD | 2019-10-11 | Chris Colvin | Comm | 2020-04-22 | Matt Gilmore | 2020-08-07 | Dave Goldak
IAS-01 | IAS-01 | PI09383 | Verified | Install plastic caps on all unit strut around base of Instrument Air/Air Dryer Skid B | C | E | Chris Colvin | McD | 2019-10-11 | Chris Colvin | Comm | 2020-04-22 | Matt Gilmore | 2020-08-07 | Dave Goldak
IAS-01 | IAS-01 | PI09384 | Verified | Tag all system components | C | P | Kelvin Cook | McD | 2019-10-11 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-08 | Bernard Stasse
IAS-01 | IAS-01 | PI09385 | Verified | Rework cocked upstream flange at 10-IAS-V-0120; Service Air Isolation Valve upstream flange | C | P | Kelvin Cook | McD | 2019-10-11 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-08 | Bernard Stasse
IAS-01 | IAS-01 | PI09386 | Verified | Tighten loose ground cable at 10-IAS-T-0100; Instrument Air Receiver Tank base, ground level N side | C | E | Chris Colvin | McD | 2019-10-11 | Chris Colvin | Comm |  |  | 2020-08-17 | Dave Goldak
IAS-01 | IAS-01 | PI09387 | Verified | Remove carbon contamination from Instrument Air Compressor B discharge piping 3-10-IAS-0105 | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-04-08 | Bernard Stasse
IAS-01 | IAS-01 | PI09388 | Verified | Label 10-IAS-COM-0100 A & B; Instrument Air Compressor's A &B | C | P | Tim Green | McD | 2019-10-11 | Tim Green | Comm | 2020-06-02 | Tim Green | 2021-02-01 | Dave Goldak
IAS-01 | IAS-01 | PI09389 | Verified | Cold gal all supports throughout system as needed | C | X | Johnny Campbell | McD | 2019-10-11 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
IAS-01 | IAS-01 | PI09390 | Verified | Filter Replacement Indicator faceplate is broken at 10-IAS-FLT-0102A2; Dust Particulate After Filter, Compressor B | C | P | Tim Green | McD | 2019-10-11 | Tim Green | Comm | 2020-06-26 | Jason Ezell | 2020-06-26 | Jason Ezell
IAS-01 | IAS-01 | PI09391 | Verified | Remove carbon contamination from 10-ISV-0119; Instrument Air Discharge Header Isolation valve | C | X | Johnny Campbell | McD | 2019-10-11 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-08 | Bernard Stasse
IAS-01 | IAS-01 | PI09392 | Verified | Remove lifting lugs from Compressor A and B skids | C | P | Shane Crowe | McD | 2019-10-11 | Shane Crowe | Comm | 2020-04-09 | Shane Crowe | 2020-06-03 | Dave Goldak
IAS-01 | IAS-01 | PI09393 | Verified | Loose bolts at 1A-IAS-V-0250; Duct Burner and 1A-CRS-AOV-0020 Instrument Air Supply Isolation Valve, Line No: 2-1A-IAS-0203 | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-01 | IAS-01 | PI09394 | Verified | Union installed backward at A Duct Burner Skid 1 inch inlet Instrument Air supply piping | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-05-07 | James Beech | 2020-07-22 | Dave Goldak
IAS-01 | IAS-01 | PI09395 | Verified | Remove wire and tie wraps from A Duct Burner 2" Instrument Air supply piping Line No. 2-1A-IAS-0203 | C | E | Chris Colvin | McD | 2019-10-11 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-04-08 | Bernard Stasse
IAS-01 | IAS-01 | PI09396 | Verified | Replace cap at 1A-IAS-V-0351; 2" Stub Up at S end of CTG A | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-01 | IAS-01 | PI09397 | Verified | Loose bolts at 1B-IAS-V-0245; 2" Instrument Air supply piping to Feedwater Control Valves, Line No. 2-1B-IAS-0202 | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-01 | IAS-01 | PI09398 | Verified | Loose bolts at 1B-IAS-V-0240; 2" Instrument Air supply piping to 1B GT Fuel Gas Heater | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-01 | IAS-01 | PI09399 | Verified | Replace cap at 1B-IAS-V-0351; 2" Stub Up @ S end of CTG B | C | P | Bobby Williams | McD | 2019-10-11 | Bobby Williams | Comm | 2020-02-04 | Bobby Williams | 2020-03-09 | Dave Goldak
IAS-01 | IAS-01 | PI09400 | Verified | Square up 1B-IAS-V-0351; 2" Stub Up @ S end of CTG B | C | P | Bobby Williams | McD | 2019-10-11 | Bobby Williams | Comm | 2020-02-04 | Bobby Williams | 2020-03-09 | Dave Goldak
IAS-01 | IAS-01 | PI09401 | Verified | Loose bolts at 1B-IAS-V-0252; 1 inch isolation valve to 1B-CRS--AOV-0020, Line no. 2-1B-IAS-0203 | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-01 | IAS-01 | PI09402 | Verified | Line No. 2-1B-IAS-0205 to Ammonia Pump Skid is rubbing on adjacent line | C | P | Kelvin Cook | McD | 2019-10-11 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-08 | Bernard Stasse
IAS-01 | IAS-01 | PI09403 | Verified | Union installed backward at B Duct Burner Skid 1 inch inlet Instrument Air supply piping | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-05-07 | James Beech | 2020-07-22 | Dave Goldak
IAS-01 | IAS-01 | PI09404 | Verified | Remove arc mark on Line No. 2-10-IAS-0224 @ E side of Ammonia Tank | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-01 | IAS-01 | PI09405 | Verified | Loose bolts at 10-IAS-V-0357; 1" Instrument Air supply piping to 10-AFS-AOV-0155, E side of Ammonia Tank | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-01 | IAS-01 | PI09406 | Verified | Carbon contamination at 10-IAS-V-0357; 1" Insturment Air supply piping to 10-AFS-AOV-0155, E side of Ammonia Tank | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-04-08 | Bernard Stasse
IAS-01 | IAS-01 | PI09407 | Verified | Loose bolts at 1B-IAS-V-0337; 1" Instrument Air supply to 1A Fuel Gas Filter Separator, Line No. 1-1A-IAS-0209 | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-01 | IAS-01 | PI09408 | Verified | Remove carbon contamination at 10-IAS-V-0506 flange, Cooling Tower Chemical Treatment at W side of containment, Line No. 2-10-IAS-0506 | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-04-08 | Bernard Stasse
IAS-01 | IAS-01 | PI09409 | Verified | Loose bolts at 10-IAS-V-0505; 2 inch Instrument Air supply to Circ Water Pump Forebay, Line No. 2-10-IAS-0505 | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-01 | IAS-01 | PI09410 | Verified | Remove carbon contamination at 10-IAS-V-0505 flange; 2 inch Instrument Air supply to Circ Water Pump Forebay, Line No. 2-10-IAS-0505 | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-04-08 | Bernard Stasse
IAS-01 | IAS-01 | PI09411 | Verified | Remove carbon contamination at 10-IAS-V-0515; 2 inch Instrument Air Supply to Raw Water and Make Up Water area, Line No. 2-10-IAS-0515 | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-20 | Joshua Sturgeon | 2020-04-08 | Bernard Stasse
IAS-01 | IAS-01 | PI09412 | Verified | Line No. 2-10-IAS-0555 at Demin Water Tank needs isolation valve | C | P | Kelvin Cook | McD | 2019-10-11 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-08 | Bernard Stasse
IAS-01 | IAS-01 | PI16202 | Verified | 10-IAS-DRY-0100B - The dew point transmitter has failed & needs to be replaced in order to monitor dryer operations - 3/27 parts on order | C | I | Mike Tabbert | McD | 2020-01-20 | Mike Tabbert | Comm | 2020-04-14 | Mike Tabbert | 2021-05-24 | Keith Pollock
IAS-01 | IAS-01 | PI17661 | Verified | 10-IAS-SKD-0100B - The tower purge muffler broken. The muffler slip is completely apart causing exhauster to be very loud during dryer depressurization. | C | M | Mike Tabbert | McD | 2020-03-04 | Mike Tabbert | Comm | 2020-06-08 | Mike Tabbert | 2020-06-08 | John Watts
IAS-01 | IAS-01 | PI17679 | Verified | A' Air compressor dryer moisture beads are brown and need to be replaced. The normal color is blue - 3/27 on order | C | M | Mike Tabbert | McD | 2020-03-04 | Mike Tabbert | Comm | 2020-04-24 | Mike Tabbert | 2020-04-30 | John Watts
IAS-01 | IAS-01 | PI17840 | Verified | Air compressor control power loss when start boiler feed pump | C | E | Jonathan Donham | McD | 2020-03-16 | Jonathan Donham | Const | 2020-04-14 | Jonathan Donham | 2020-06-03 | Chase Courtade
IAS-01 | IAS-01 | PI18014 | Verified | 10-IAS-COM-0100A - It has a low oil pressure. It will not start when the lead compressor shuts down (i.e., the compressor won't start in lag). | C | M | William Mitchell | McD | 2020-03-17 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2020-04-30 | John Watts
IAS-01 | IAS-01 | PI18133 | Verified | 10-IAS-COM-0100A - 1A Instrument Air Compressor is overdue for 2000 hour maintenance and currently does not stay online. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2020-04-30 | John Watts
IAS-01 | IAS-01 | PI18134 | Verified | 10-IAS-COM-0100B - 1B Instrument Air Compressor is overdue for maintenance. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2020-04-30 | John Watts
IAS-02 | IAS-02 | PI02540 | Verified | LK-1A-IAS-PD-P41-0201-04 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-27 | Terry Deaton | 2019-07-27 | Tom Noble
IAS-02 | IAS-02 | PI02541 | Verified | LK-1A-IAS-PD-P41-0201-15 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-27 | Terry Deaton | 2019-07-27 | Tom Noble
IAS-02 | IAS-02 | PI02542 | Verified | LK-1A-IAS-PD-P41-0201-16 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-27 | Terry Deaton | 2019-07-27 | Tom Noble
IAS-02 | IAS-02 | PI02543 | Verified | LK-1A-IAS-PD-P41-0201-17 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-27 | Terry Deaton | 2019-07-27 | Tom Noble
IAS-02 | IAS-02 | PI02544 | Verified | LK-1A-IAS-PD-P41-0203-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-27 | Terry Deaton | 2019-07-27 | Tom Noble
IAS-02 | IAS-02 | PI02545 | Verified | LK-1A-IAS-PD-P41-0205-08 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-27 | Terry Deaton | 2019-07-27 | Tom Noble
IAS-02 | IAS-02 | PI02546 | Verified | LK-1A-IAS-PD-P41-0205-13 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-27 | Terry Deaton | 2019-07-27 | Tom Noble
IAS-02 | IAS-02 | PI02547 | Verified | LK-1A-IAS-PD-P41-0210-04 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-27 | Terry Deaton | 2019-07-27 | Tom Noble
IAS-02 | IAS-02 | PI02548 | Verified | LK-1A-IAS-PD-P41-0210-06 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-03 | Terry Deaton | 2019-08-03 | Tom Noble
IAS-02 | IAS-02 | PI02549 | Verified | LK-1A-IAS-PD-P41-0216-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-27 | Terry Deaton | 2019-07-27 | Tom Noble
IAS-02 | IAS-02 | PI02550 | Verified | LK-1A-IAS-PD-P41-0216-05 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-27 | Terry Deaton | 2019-07-27 | Tom Noble
IAS-02 | IAS-02 | PI02551 | Verified | LK-1A-IAS-PD-P41-0219-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-29 | Terry Deaton | 2019-07-29 | Tom Noble
IAS-02 | IAS-02 | PI02886 | Verified | ON ISO 1A-IAS-PD-P41-0201-02 cold galve pipe supports 1A-IAS-PD-HGR-0185, 0186, 0188 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02887 | Verified | ON ISO 1A-IAS-PD-P41-0201-03 between pipe supports 1A-IAS-PD-HGR-0194 & 1A-IAS-PD-HGR-0195 remove rigging | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02888 | Verified | ON ISO 1A-IAS-PD-P41-0201-03 spool 1A-IAS-P41-0201-03-152-3 needs ss wrap & clamp/ resting on steel | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02889 | Verified | ON ISO 1A-IAS-PD-P41-0201-03 spool 1A-IAS-P41-0201-03-152-3 trim excess w4 support west side to elimate contact with insulation | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02890 | Verified | ON ISO 1A-IAS-PD-P41-0201-04 pipe support 1A-IAS-PD-HGR-0210 needs ss wrap & clamp | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02891 | Verified | ON ISO 1A-IAS-PD-P41-0201-04 pipe support 1A-IAS-PD-HGR-0209 needs ss wrap & clamp & cold galve | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02892 | Verified | ON ISO 1A-IAS-PD-P41-0201-04 ss wrap & clamp right after the 90 elbow incontact with top of beam | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02893 | Verified | ON ISO 1A-IAS-PD-P41-0201-04 need ss wrap & clamp on Spool 1A-IAS-P41-0201-04-152-3 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02894 | Verified | ON ISO 1A-IAS-PD-P41-0201-04 weld top of 1A-IAS-PD-HGR--0206 & 0207 & 0208 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-03 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-02 | IAS-02 | PI02895 | Verified | ON ISO 1A-IAS-PD-P41-0201-08 need to relocate pipe support 1A-IAS-PD-HGR-0202 to proper location. Install ss wrap and ubolt | B | P | Damon Turner | McD | 2019-07-29 | Damon Turner | Const | 2019-08-09 | Terry Deaton | 2019-10-03 | Kelvin Cook
IAS-02 | IAS-02 | PI02896 | Verified | ON ISO 1A-IAS-PD-P41-0201-14 need ss wrap & clamp at support 1A-IAS-PD-HGR-0217 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-20 | Kelvin Cook
IAS-02 | IAS-02 | PI02897 | Verified | ON ISO 1A-IAS-PD-P41-0201-14 second set of nuts required at ubolt for support 1A-IAS-PD-HGR-0217 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02898 | Verified | ON ISO 1A-IAS-PD-P41-0201-14 pipe support 1A-IAS-PD-HGR-0216 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02899 | Verified | ON ISO 1A-IAS-PD-P41-0202-02 need ss wrap & clamp at support 1A-IAS-PD-HGR-0231 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-02 | IAS-02 | PI02900 | Verified | ON ISO 1A-IAS-PD-P41-0202-02 set ss wrap proper on support 1A-IAS-PD-HGR-0232 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02901 | Verified | ON ISO 1A-IAS-PD-P41-0202-02 need ss wrap & clamp on support 1A-IAS-PD-HGR-0233 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-03 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-02 | IAS-02 | PI02902 | Verified | ON ISO 1A-IAS-PD-P41-0202-02 need second set of nuts support 1A-IAS-PD-HGR-0233 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-03 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-02 | IAS-02 | PI02903 | Verified | ON ISO 1A-IAS-PD-P41-0202-02 need second set of nuts support 1A-IAS-PD-HGR-0234 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02904 | Verified | ON ISO 1A-IAS-PD-P41-0202-02 pipe support 1A-IAS-PD-HGR-0235 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02905 | Verified | ON ISO 1A-IAS-PD-P41-0202-02 need ss wrap & clamp on support 1A-IAS-PD-HGR-0234 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-02 | IAS-02 | PI02906 | Verified | ON ISO 1A-IAS-PD-P41-0202-04 need ss wrap & clamp at support 1A-IAS-PD-HGR-0246 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-27 | Kelvin Cook
IAS-02 | IAS-02 | PI02907 | Verified | ON ISO 1A-IAS-PD-P41-0205-01 need ss wrap & clamp at support 1A-IAS-PD-HGR-0266 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-03 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-02 | IAS-02 | PI02908 | Verified | ON ISO 1A-IAS-PD-P41-0205-01 need ss wrap & clamp at support 1A-IAS-PD-HGR-0272 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-03 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-02 | IAS-02 | PI02909 | Verified | ON ISO 1A-IAS-PD-P41-0205-01 pipe support 1A-IAS-PD-HGR-0270 is not installed | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-03 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-02 | IAS-02 | PI02910 | Verified | ON ISO 1A-IAS-PD-P41-0205-01 remove rope and wire form spool 1A-IAS-P41-0205-01-111-6 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02911 | Verified | ON ISO 1A-IAS-PD-P41-0205-03 missing valve handle stop at 1A-IAS-V-0214 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-03 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-02 | IAS-02 | PI02912 | Verified | ON ISO 1A-IAS-PD-P41-0205-08 need ss wrap & clamp and ubolt on pipe suppport 1A-IAS-PD-HGR-0277 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-03 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-02 | IAS-02 | PI02913 | Verified | ON ISO 1A-IAS-PD-P41-0205-09 need ss wrap & clamp on pipe suppport 1A-IAS-PD-HGR-0280 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-02 | IAS-02 | PI02914 | Verified | ON ISO 1A-IAS-PD-P41-0205-09 need ss wrap & clamp and ubolt on pipe suppport 1A-IAS-PD-HGR-0279 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-02 | IAS-02 | PI02915 | Verified | ON ISO 1A-IAS-PD-P41-0205-010 need ss wrap & clamp and ubolt on pipe suppport 1A-IAS-PD-HGR-0282 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02916 | Verified | ON ISO 1A-IAS-PD-P41-0205-010 pipe suppport 1A-IAS-PD-HGR-0281 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02917 | Verified | ON ISO 1A-IAS-PD-P41-0205-011 need ss wrap & clamp on pipe suppport 1A-IAS-PD-HGR-0283 | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02918 | Verified | ON ISO 1A-IAS-PD-P41-0205-013 rotate 1A-IAS-V-0218 to open top and close to south. | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02919 | Verified | ON ISO 1A-IAS-PD-P41-0205-013 connection 1A-AFS-SKD-8100/TP-04 has gasket & wrong size bolts | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI02920 | Verified | ON ISO 1A-IAS-PD-P41-0205-014 pipe support 1A-IAS-PD-HGR-0692 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-02 | Kelvin Cook
IAS-02 | IAS-02 | PI03229 | Verified | Add additional line & valve for 1A CEMs. | B | P | Terry Deaton | McD | 2019-08-06 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-02 | IAS-02 | PI09445 | Verified | Loose bolts on valve V-0227 - top of HRSG 1A | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-02 | IAS-02 | PI09446 | Verified | Remove carbon contamination V-0205 - top of HRSG 1A | C | X | Johnny Campbell | McD | 2019-10-11 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-08 | Bernard Stasse
IAS-02 | IAS-02 | PI09447 | Verified | Remove carbon contamination V-0215 - top of HRSG 1A | C | X | Johnny Campbell | McD | 2019-10-11 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-08 | Bernard Stasse
IAS-02 | IAS-02 | PI09448 | Verified | Remove carbon contamination V-0210 - top of HRSG 1A | C | X | Johnny Campbell | McD | 2019-10-11 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-08 | Bernard Stasse
IAS-02 | IAS-02 | PI09449 | Verified | Loose bolts on valve V-0209 - top of HRSG 1A | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2019-10-23 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-02 | IAS-02 | PI09631 | Verified | Missing U-Bolts under grating at 1A-IAS-V-0308; 1 Inch Instrument Air Isolation Valve, supply to LP ECO & Drum Bypass Valve 1A-FWS-PV-0513, Line No. 2-1A-IAS-0201 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-02 | IAS-02 | PI09632 | Verified | Loose bolts at 1A-IAS-V-0308; 1 inch Instrument Air Isolation Valve, supply to LP ECO & Drum Bypass Valve 1A-FWS-PV-0513, Line No. 2-1A-IAS-0201 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-02 | IAS-02 | PI09633 | Verified | Loose bolts at 1A-IAS-V-0314; 1 inch Instrument Air Isolation Valve, supply to 1A Fuel Gas Heater Inlet Isolation Valve B, Line No. 2-1A-IAS-0201 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-02 | IAS-02 | PI09634 | Verified | Loose bolts at 1A-IAS-V-0309; 1 inch Instrument Air Isolation Valve, supply 1A Fuel Gas Heater Inlet Isolation Valve A, Line No. 2-1A-IAS-0201 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-02 | IAS-02 | PI09635 | Verified | Loose bolts at 1A-IAS-V-0346; 1 inch Instrument Air Isolation Valve, supply to 1A GT Fuel Gas Scrubber, Line No. 2-1A-IAS-0201 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-02 | IAS-02 | PI09636 | Verified | Loose bolts at 1A-IAS-V-0316; 1 inch Instrument Air Isolation Valve, supply to 1A GT Fuel Gas Emergency Shutoff Valve, Line No. 2-1A-IAS-0201 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-02 | IAS-02 | PI09637 | Verified | Loose bolts at 1A-IAS-V-0341; 1 inch Instrument Air Drain Valve, upstream of 1A GT Casing Cooling Outlet Damper, Line No. 2-1A-IAS-0210 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-02 | IAS-02 | PI09638 | Verified | Loose bolts at 1A-ISV-V-0334; 1 inch Instrument Air supply to 1A GT Casing Cooling Air Shutoff Valve, Line No. 2-1A-IAS-0210 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-02 | IAS-02 | PI09639 | Verified | Repair leaking valve with damaged gasket at 1A-ISV-V-0335; 1 inch Instrument Air supply to 1A GT Casing Cooling Air Supply Valve, Line No. 2-1A-IAS-0210 | C | P | Reggie Brown | McD | 2019-10-16 | Reggie Brown | Comm | 2020-02-04 | Bobby Williams | 2020-04-08 | Bernard Stasse
IAS-02 | IAS-02 | PI09640 | Verified | Loose bolts at 1A-ISV-V-0318; 1 inch Instrument Air supply to 1A GT Exhaust Duct Gas Detector, Line No. 2-1A-IAS-0210 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-02 | IAS-02 | PI09641 | Verified | Loose bolts at 1A-ISV-V-0322; 1 inch Instrument Air supply to 1A GT Enclosure Vent Fans Gas Detector, Line No. 2-1A-IAS-0210 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-02-10 | Nelson Eichelberger
IAS-02 | IAS-02 | PI09642 | Verified | Remove carbon contamination at 1A-ISV-V-0322; 1 inch Instrument Air supply to 1A GT Enclosure Vent Fans Gas Detector, Line No. 2-1A-IAS-0210 | C | X | Johnny Campbell | McD | 2019-10-16 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-07-24 | Nelson Eichelberger
IAS-02 | IAS-02 | PI09643 | Verified | 1A-IAS-V-0323; 1" Instrument Air Supply to 1A GT Cooling Air Cooler Drain Valve B is inaccessible, Line No. 2-1A-IAS-0216 | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-02 | IAS-02 | PI09644 | Verified | 1A-IAS-V-0324; 1" Instrument Air Supply to 1A GT Cooling Air Cooler Drain Valve A is inaccessible, Line No. 2-1A-IAS-0216 | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-02 | IAS-02 | PI09645 | Verified | 1B-IAS-V-0105; 1" Instrument Air Supply to LPS Drain Pot is inaccessible, in pipe rack, Line No. 2-1A-IAS-0216 | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-02 | IAS-02 | PI09646 | Verified | 1B-IAS-V-0226; 1" Instrument Air Supply to MSS Drain Pot is inaccessible, in pipe rack, Line No. 2-1A-IAS-0216 | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-02 | IAS-02 | PI09647 | Verified | Reevaluate Instrument Air tubing support at Unit A Anti-Icing Air Balancing Valve, existing uni-strut support is not sufficient since this valve will move during plant operation | C | P | Tim Green | McD | 2019-10-16 | Tim Green | Comm | 2020-06-04 | Tim Green | 2020-07-24 | Nelson Eichelberger
IAS-02 | IAS-02 | PI09648 | Verified | IA-IAS-V-0370; 2" Instrument Air Isolation Valve Line No. 2-1A-IAS-0219 is inaccessible | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-02 | IAS-02 | PI09649 | Verified | IA-IAS-V-0333; 1" Instrument Air supply to 1A GT Lube Oil Temperature Control Valve Line No. 2-1A-IAS-0219 is inaccessible | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-02 | IAS-02 | PI09650 | Verified | IA-IAS-V-0339; 1.5" Instrument Air supply to 1A GT Package Line No. 2-1A-IAS-0219 is inaccessible | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-02 | IAS-02 | PI09651 | Verified | IA-IAS-V-0365; 2" Instrument Air Isolation Valve, Line No. 2-1A-IAS-0219 is inaccessible | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-02 | IAS-02 | PI09652 | Verified | 1A Anti Icing Air Temperature Control Valve's A and B need to be reversed on P&ID LK-10-IAS-ME-PID-0002 to indicate east (B) and west (A), redline drawing, Line No. 2-1A-IAS-0219 | C | P | Kelvin Cook | McD | 2019-10-16 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-07-24 | Nelson Eichelberger
IAS-02 | IAS-02 | PI09653 | Verified | Remove rope and fire blanket from Line No. 2-1A-IAS-0219 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-02-10 | Nelson Eichelberger
IAS-02 | IAS-02 | PI09654 | Verified | Remove carbon contamination from line No. 2-1A-IAS-0219 | C | X | Tim Green | McD | 2019-10-16 | Tim Green | Comm | 2020-08-06 | Tim Green | 2020-08-14 | Nelson Eichelberger
IAS-02 | IAS-02 | PI17191 | Verified | Valve tag missing on P&ID on IA valve to 1A CEMS | C | P | Kelvin Cook | McD | 2020-02-24 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-03-09 | Michael Law
IAS-03 | IAS-03 | PI02472 | Verified | LK-1B-IAS-P41-0201-04 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-29 | Terry Deaton | 2019-07-29 | Tom Noble
IAS-03 | IAS-03 | PI02473 | Verified | LK-1B-IAS-P41-0201-14 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-29 | Terry Deaton | 2019-07-29 | Tom Noble
IAS-03 | IAS-03 | PI02474 | Verified | LK-1B-IAS-P41-0201-15 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-29 | Terry Deaton | 2019-07-29 | Tom Noble
IAS-03 | IAS-03 | PI02475 | Verified | LK-1B-IAS-P41-0201-16 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-29 | Terry Deaton | 2019-07-29 | Tom Noble
IAS-03 | IAS-03 | PI02476 | Verified | LK-1B-IAS-P41-0201-17 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
IAS-03 | IAS-03 | PI02477 | Verified | LK-1B-IAS-P41-0202-04 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Tom Noble
IAS-03 | IAS-03 | PI02479 | Verified | LK-1B-IAS-P41-0202-05 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Tom Noble
IAS-03 | IAS-03 | PI02480 | Verified | LK-1B-IAS-P41-0202-06 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Tom Noble
IAS-03 | IAS-03 | PI02481 | Verified | LK-1B-IAS-P41-0202-07 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Tom Noble
IAS-03 | IAS-03 | PI02482 | Verified | LK-1B-IAS-P41-0202-08 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Tom Noble
IAS-03 | IAS-03 | PI02483 | Verified | LK-1B-IAS-P41-0202-09 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Tom Noble
IAS-03 | IAS-03 | PI02484 | Verified | LK-1B-IAS-P41-0202-10 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Tom Noble
IAS-03 | IAS-03 | PI02485 | Verified | LK-1B-IAS-P41-0205-11 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-29 | Terry Deaton | 2019-07-29 | Tom Noble
IAS-03 | IAS-03 | PI02486 | Verified | LK-1B-IAS-P41-0205-12 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-29 | Terry Deaton | 2019-07-29 | Tom Noble
IAS-03 | IAS-03 | PI02487 | Verified | LK-1B-IAS-P41-0205-13 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-29 | Terry Deaton | 2019-07-29 | Tom Noble
IAS-03 | IAS-03 | PI02488 | Verified | LK-1B-IAS-P-41-0210-04 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Tom Noble
IAS-03 | IAS-03 | PI02489 | Verified | LK-1B-IAS-P-41-0210-06 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Tom Noble
IAS-03 | IAS-03 | PI02490 | Verified | LK-1B-IAS-P-41-0212-01 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
IAS-03 | IAS-03 | PI02491 | Verified | LK-1B-IAS-P-41-0216-01 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
IAS-03 | IAS-03 | PI02492 | Verified | LK-1B-IAS-P-41-0216-02 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Tom Noble
IAS-03 | IAS-03 | PI02493 | Verified | LK-1B-IAS-P-41-0216-03 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Tom Noble
IAS-03 | IAS-03 | PI02494 | Verified | LK-1B-IAS-P-41-0219-02 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
IAS-03 | IAS-03 | PI02495 | Verified | LK-1B-IAS-P-41-0219-05 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Tom Noble
IAS-03 | IAS-03 | PI02496 | Verified | LK-1B-IAS-P-41-0219-06 Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Tom Noble
IAS-03 | IAS-03 | PI02769 | Verified | Rotate valve handle on 1B-IAS-V-0219 - at Ammonia skid 1B-AFS-SKD-8100. | A | P | Terry Deaton | McD | 2019-07-25 | Terry Deaton | Const | 2019-08-02 | Terry Deaton | 2019-08-03 | Kelvin Cook
IAS-03 | IAS-03 | PI02770 | Verified | Replace internals & tighten valve 1B-IAS-V-0214 - top HRSG north end. | A | P | Terry Deaton | McD | 2019-07-25 | Terry Deaton | Const | 2019-08-02 | Terry Deaton | 2019-08-03 | Kelvin Cook
IAS-03 | IAS-03 | PI02771 | Verified | Tag all valves. | C | P | Justin Houdeshell | McD | 2019-07-25 | Justin Houdeshell | Const |  |  | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02806 | Verified | On ISO 1B-IAS-PD-P41-0201-01 pipe support 1B-IAS-PD-HGR-0296 & 0297 are not installed | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02807 | Verified | On ISO 1B-IAS-PD-P41-0203-01 pipe support 1B-IAS-PD-HGR-0725 has no bolts | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02808 | Verified | ISO 1B-IAS-PD-P41-0202-01 Pipe spools PS-1B-IAS-P41-0202-01-121-1 is not intalled | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02809 | Verified | ISO 1B-IAS-PD-P41-0202-01 Pipe spools PS-1B-IAS-P41-0202-01-121-2 is not intalled | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02810 | Verified | ISO 1B-IAS-PD-P41-0202-01 Pipe spools PS-1B-IAS-P41-0202-01-121-3 is not intalled | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02811 | Verified | ISO 1B-IAS-PD-P41-0202-01 Pipe spools PS-1B-IAS-P41-0202-01-121-4 is not intalled | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02812 | Verified | ISO 1B-IAS-PD-P41-0202-01 Pipe spools PS-1B-IAS-P41-0202-01-121-5 is not intalled | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02813 | Verified | ISO 1B-IAS-PD-P41-0202-01 Pipe spools PS-1B-IAS-P41-0202-01-121-6 is not intalled | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02814 | Verified | ISO 1B-IAS-PD-P41-0202-01 pipe support 1B-IAS-PD-HGR-0336 is not installed | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02815 | Verified | ISO 1B-IAS-PD-P41-0205-01 pipe support 1B-IAS-PD-HGR-0376 ss wrap is not installed | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02816 | Verified | ISO 1B-IAS-PD-P41-0205-01 pipe support 1B-IAS-PD-HGR-0375 ss wrap is not installed | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02817 | Verified | ISO 1B-IAS-PD-P41-0205-01 pipe support 1B-IAS-PD-HGR-0374 ss wrap is not installed | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02818 | Verified | ISO 1B-IAS-PD-P41-0205-01 pipe support 1B-IAS-PD-HGR-0373 ss wrap is not installed | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02819 | Verified | ISO 1B-IAS-PD-P41-0205-01 pipe support 1B-IAS-PD-HGR-0372 ss wrap is not installed | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02820 | Verified | ISO 1B-IAS-PD-P41-0205-01 pipe support 1B-IAS-PD-HGR-0370 ss wrap is not installed | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02821 | Verified | ISO 1B-IAS-PD-P41-0205-01 just before valve 1B-IAS-V-0260 connects to underground connection remove temporary support | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02822 | Verified | ISO 1B-IAS-PD-P41-0205-12 pipe support 1B-IAS-PD-HGR-0728 has a loose ubolt | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02823 | Verified | ISO 1B-IAS-PD-P41-0205-12 pipe support 1B-IAS-PD-HGR-0727 has a loose ubolt | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02824 | Verified | ISO 1B-IAS-PD-P41-0205-13 valve 1B-IAS-V-0218 needs valve handle rotated 180 degrees so that handle opens up and down to close to the south | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02825 | Verified | ISO 1B-IAS-PD-P41-0205-13 valve 1B-IAS-V-0219 needs valve handle rotated 180 degrees so that handle opens up and down to close to the south | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02826 | Verified | ISO 1B-IAS-PD-P41-0210-02 pipe support 1B-IAS-PD-HGR-0111 is not installed | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02827 | Verified | ISO 1B-IAS-PD-P41-0210-04 pipe support 1B-IAS-PD-HGR-0098 is not installed | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02828 | Verified | ISO 1B-IAS-PD-P41-0219-02 pipe spools PS-1B-IAS-P41-0219-02-421-2 is not installed | A | P | Terry Deaton | McD | 2019-07-26 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02846 | Verified | On ISO 1B-IAS-PD-P41-0203-01 pipe support 1B-IAS-PD-HGR-0725 has no bolts | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02847 | Verified | ISO 1B-IAS-PD-P41-0205-01 pipe support 1B-IAS-PD-HGR-0376 ss wrap is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02848 | Verified | ISO 1B-IAS-PD-P41-0205-01 pipe support 1B-IAS-PD-HGR-0375 ss wrap is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02849 | Verified | ISO 1B-IAS-PD-P41-0205-01 pipe support 1B-IAS-PD-HGR-0374 ss wrap is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02850 | Verified | ISO 1B-IAS-PD-P41-0205-01 pipe support 1B-IAS-PD-HGR-0373 ss wrap is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02851 | Verified | ISO 1B-IAS-PD-P41-0205-01 pipe support 1B-IAS-PD-HGR-0372 ss wrap is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02852 | Verified | ISO 1B-IAS-PD-P41-0205-01 pipe support 1B-IAS-PD-HGR-0370 ss wrap is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02853 | Verified | ISO 1B-IAS-PD-P41-0205-12 pipe support 1B-IAS-PD-HGR-0728 has a loose ubolt | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02854 | Verified | ISO 1B-IAS-PD-P41-0205-12 pipe support 1B-IAS-PD-HGR-0727 has a loose ubolt | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02855 | Verified | ISO 1B-IAS-PD-P41-0205-13 valve 1B-IAS-V-0218 needs valve handle rotated 180 degrees so that handle opens up and down to close to the south | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02856 | Verified | ISO 1B-IAS-PD-P41-0205-13 valve 1B-IAS-V-0219 needs valve handle rotated 180 degrees so that handle opens up and down to close to the south | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02857 | Verified | ISO 1B-IAS-PD-P41-0210-01 pipe support 1B-IAS-PD-HGR-0086 is missing 1 pipe clamp | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02858 | Verified | ISO 1B-IAS-PD-P41-0210-01 pipe support 1B-IAS-PD-HGR-0087 has a loose ubolt | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02859 | Verified | ISO 1B-IAS-PD-P41-0210-01 just off pipe support 1B-IAS-PD-HGR-0087 FW is not made | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02860 | Verified | ISO 1B-IAS-PD-P41-0210-01 pipe support 1B-IAS-PD-HGR-0088 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02861 | Verified | ISO 1B-IAS-PD-P41-0210-01 connecting to 1A-212/QFF11-602 has the wrong bolts installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02862 | Verified | ISO 1B-IAS-PD-P41-0210-02 pipe support 1B-IAS-PD-HGR-0112 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02863 | Verified | ISO 1B-IAS-PD-P41-0210-02 pipe support 1B-IAS-PD-HGR-0111 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02864 | Verified | ISO 1B-IAS-PD-P41-0210-02 pipe support 1B-IAS-PD-HGR-0092 missing ubolt | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02865 | Verified | ISO 1B-IAS-PD-P41-0210-03 pipe support 1B-IAS-PD-HGR-0096 has a loose ubolt | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02866 | Verified | ISO 1B-IAS-PD-P41-0210-03 pipe support 1B-IAS-PD-HGR-0095 missing ss wrap & no ubolt | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02867 | Verified | ISO 1B-IAS-PD-P41-0210-03 pipe support 1B-IAS-PD-HGR-0094 missing ss wrap & loose ubolt | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02868 | Verified | ISO 1B-IAS-PD-P41-0210-03 pipe spool PS-1B-IAS-P41-0210-03-421-2 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02869 | Verified | ISO 1B-IAS-PD-P41-0210-04 pipe spool PS-1B-IAS-P41-0210-04-421-1 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02870 | Verified | ISO 1B-IAS-PD-P41-0210-04 pipe support 1B-IAS-PD-HGR-0098 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02871 | Verified | ISO 1B-IAS-PD-P41-0210-07 pipe support 1B-IAS-PD-HGR-0109 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02872 | Verified | ISO 1B-IAS-PD-P41-0210-07 pipe support 1B-IAS-PD-HGR-0110 incomplete | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02873 | Verified | ISO 1B-IAS-PD-P41-0212-01 pipe support 1B-IAS-PD-HGR-0167 missing ss wrap & loose ubolt | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02874 | Verified | ISO 1B-IAS-PD-P41-0212-01 pipe support 1B-IAS-PD-HGR-0168 missing ss wrap & loose ubolt | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02875 | Verified | ISO 1B-IAS-PD-P41-0212-01 pipe support 1B-IAS-PD-HGR-0165 missing ss wrap | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02876 | Verified | ISO 1B-IAS-PD-P41-0212-01 pipe support 1B-IAS-PD-HGR-0166 all threaded rod out of plumb | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02877 | Verified | ISO 1B-IAS-PD-P41-0212-01 connecting ISO 1B-IAS-PD-P42-0209-01 has the wrong size bolts | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02878 | Verified | ISO 1B-IAS-PD-P41-0212-01 connecting to 1BMKO01/641 has the wrong gasket & wrong bolts | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02879 | Verified | ISO 1B-IAS-PD-P41-0216-01 pipe support 1B-IAS-PD-HGR-0117 missing ss wrap | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02880 | Verified | ISO 1B-IAS-PD-P41-0216-01 just off pipe support 1B-IAS-HGR-0118 remove rope | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02881 | Verified | ISO 1B-IAS-PD-P41-0219-01 pipe support 1B-IAS-PD-HGR-0134 missing ss wrap | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02882 | Verified | ISO 1B-IAS-PD-P41-0219-01 pipe support 1B-IAS-PD-HGR-0631 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02883 | Verified | ISO 1B-IAS-PD-P41-0219-02 pipe support 1B-IAS-PD-HGR-0141 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02884 | Verified | ISO 1B-IAS-PD-P41-0219-02 pipe support 1B-IAS-PD-HGR-0140 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02885 | Verified | ISO 1B-IAS-PD-P41-0230-01 connecting to ISO 1B-IAS-PD-P42-0208-01 has the wrong gasket | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-07-30 | Kelvin Cook | 2019-07-30 | Kelvin Cook
IAS-03 | IAS-03 | PI02921 | Verified | ON ISO 1B-IAS-PD-P41-0201-01 pipe support 1B-IAS-PD-HGr-0297 needs ss wrap and clamp | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-03 | IAS-03 | PI02922 | Verified | ON ISO 1B-IAS-PD-P41-0201-01 pipe support 1B-IAS-PD-HGG-0295 has loose ubolt | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-03 | IAS-03 | PI02923 | Verified | ON ISO 1B-IAS-PD-P41-0201-03 pipe support 1B-IAS-PD-HGR-0311 & 0312 & 0313 is not installed | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-03 | IAS-03 | PI02924 | Verified | ON ISO 1B-IAS-PD-P41-0201-03 pipe support 1B-IAS-PD-HGR-0309 pipe in contact with support install ss Wrap and clamp | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-03 | IAS-03 | PI02925 | Verified | ON ISO 1B-IAS-PD-P41-0201-03 pipe support 1B-IAS-PD-HGR-0308 needs ss wrap and clamp | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-03 | IAS-03 | PI02926 | Verified | ON ISO 1B-IAS-PD-P41-0201-07 pipe support 1B-IAS-PD-HGR-0314 missing clamps | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-03 | IAS-03 | PI02927 | Verified | ON ISO 1B-IAS-PD-P41-0201-08 pipe support 1B-IAS-PD-HGR-0315 & 0316 needs ss wrap and clamp | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-03 | IAS-03 | PI02928 | Verified | ON ISO 1B-IAS-PD-P41-0202-01 spool 1 & 2 have no supports installed | B | P | Damon Turner | McD | 2019-07-29 | Damon Turner | Const | 2019-08-26 | Terry Deaton | 2019-09-18 | Kelvin Cook
IAS-03 | IAS-03 | PI02929 | Verified | ON ISO 1B-IAS-PD-P41-0202-01 pipe support 1B-IAS-PD-HGR-0336 needs ss wrap and clamp and tighten loose ubolt | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-20 | Kelvin Cook
IAS-03 | IAS-03 | PI02930 | Verified | ON ISO 1B-IAS-PD-P41-0202-01 pipe support 1B-IAS-PD-HGR-0339 needs ss wrap and clamp | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-20 | Kelvin Cook
IAS-03 | IAS-03 | PI02931 | Verified | ON ISO 1B-IAS-PD-P41-0202-01 pipe support 1B-IAS-PD-HGR-0337 needs ss wrap and clamp and tighten loose ubolt. | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-20 | Kelvin Cook
IAS-03 | IAS-03 | PI02932 | Verified | Remove all rigging and rope and wire. | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-03 | IAS-03 | PI02933 | Verified | ON ISO 1B-IAS-PD-P41-0202-01 pipe support 1B-IAS-PD-HGR-0358 wrong location | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-03 | Kelvin Cook
IAS-03 | IAS-03 | PI02934 | Verified | ON ISO 1B-IAS-PD-P41-0202-02 install ss wrap and clamp for each support | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-03 | IAS-03 | PI02935 | Verified | ON ISO 1B-IAS-PD-P41-0202-04 pipe support 1B-IAS-PD-HGR-0360 wrong location | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-03 | Kelvin Cook
IAS-03 | IAS-03 | PI02936 | Verified | ON ISO 1B-IAS-PD-P41-0202-04 pipe support 1B-IAS-PD-HGR-0359 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-03 | Kelvin Cook
IAS-03 | IAS-03 | PI02937 | Verified | ON ISO 1B-IAS-PD-P41-0202-09 pipe support 1B-IAS-PD-HGR-0740 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-02 | Terry Deaton | 2019-08-03 | Kelvin Cook
IAS-03 | IAS-03 | PI02938 | Verified | ON ISO 1B-IAS-PD-P41-0202-09 pipe support 1B-IAS-PD-HGR-0741 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-02 | Terry Deaton | 2019-08-03 | Kelvin Cook
IAS-03 | IAS-03 | PI02939 | Verified | ON ISO 1B-IAS-PD-P41-0202-09 pipe support 1B-IAS-PD-HGR-0742 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-02 | Terry Deaton | 2019-08-03 | Kelvin Cook
IAS-03 | IAS-03 | PI02940 | Verified | ON ISO 1B-IAS-PD-P41-0202-09 pipe support 1B-IAS-PD-HGR-0743 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const |  |  | 2019-12-18 | Kelvin Cook
IAS-03 | IAS-03 | PI02941 | Verified | ON ISO 1B-IAS-PD-P41-0202-09 pipe support 1B-IAS-PD-HGR-0744 is not installed | A | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-02 | Terry Deaton | 2019-08-03 | Kelvin Cook
IAS-03 | IAS-03 | PI02942 | Verified | ON ISO 1B-IAS-PD-P41-0202-09 pipe support 1B-IAS-PD-HGR-0745 is not installed | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-03 | IAS-03 | PI02943 | Verified | ON ISO 1B-IAS-PD-P41-0205-01 just before 1B-IAS-V-0260 use correct bolts and install clamp | B | P | Damon Turner | McD | 2019-07-29 | Damon Turner | Const | 2019-08-07 | Terry Deaton | 2019-09-18 | Kelvin Cook
IAS-03 | IAS-03 | PI02944 | Verified | ON ISO 1B-IAS-PD-P41-0216-03 pipe support 1B-IAS-PD-HGR-0126 is not installed | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-27 | Kelvin Cook
IAS-03 | IAS-03 | PI02945 | Verified | ON ISO 1B-IAS-PD-P41-0216-03 pipe support 1B-IAS-PD-HGR-0127 is not installed | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-07 | Terry Deaton | 2019-08-27 | Kelvin Cook
IAS-03 | IAS-03 | PI02946 | Verified | ON ISO 1B-IAS-PD-P41-0216-03 pipe support 1B-IAS-PD-HGR-0132 missing set of nuts | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-07 | Terry Deaton | 2019-08-27 | Kelvin Cook
IAS-03 | IAS-03 | PI02947 | Verified | ON ISO 1B-IAS-PD-P41-0216-03 1B-IAS-V-0342 MISSING THREADED CAP | B | P | Terry Deaton | McD | 2019-07-29 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-20 | Kelvin Cook
IAS-03 | IAS-03 | PI03230 | Verified | Add additional line & valve for 1B CEMs. | B | P | Terry Deaton | McD | 2019-08-06 | Terry Deaton | Const | 2019-08-08 | Terry Deaton | 2019-08-08 | Kelvin Cook
IAS-03 | IAS-03 | PI09450 | Verified | Remove pinch pont V-0228 - top of HRSG 1B | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2019-10-23 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09451 | Verified | Loose bolts on valve V-0227 - top of HRSG 1B | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2019-10-23 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09452 | Verified | Need support V-0207 - top of HRSG 1B | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2019-10-23 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09453 | Verified | Need support V-0206 - top of HRSG 1B | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2019-10-23 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09454 | Verified | Loose bolts V-0204 - top of HRSG 1B | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2019-10-23 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09455 | Verified | Remove carbon contamination V-0204 - top of HRSG 1B | C | X | Johnny Campbell | McD | 2019-10-11 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-08 | Bernard Stasse
IAS-03 | IAS-03 | PI09456 | Verified | Remove carbon contamination V-0205 - top of HRSG 1B | C | X | Johnny Campbell | McD | 2019-10-11 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-08 | Bernard Stasse
IAS-03 | IAS-03 | PI09457 | Verified | Loose bolts V-0205 - top of HRSG 1B | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2019-10-17 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09458 | Verified | Fix crooked support between V-0213 and V-0214 - top of HRSG 1B | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09459 | Verified | Missing bolts V-0218 - top of HRSG 1B | C | P | Bobby Williams | McD | 2019-10-11 | Bobby Williams | Comm | 2020-02-04 | Bobby Williams | 2020-04-08 | Bernard Stasse
IAS-03 | IAS-03 | PI09460 | Verified | Remove carbon contamination V-0215 - top of HRSG 1B | C | X | Johnny Campbell | McD | 2019-10-11 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-08 | Bernard Stasse
IAS-03 | IAS-03 | PI09461 | Verified | Remove carbon contamination V-0203 - top of HRSG 1B | C | X | Johnny Campbell | McD | 2019-10-11 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-08 | Bernard Stasse
IAS-03 | IAS-03 | PI09462 | Verified | Loose bolts V-0209 - top of HRSG 1B | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2019-10-23 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09655 | Verified | Line No. 2-1B-IAS-0210 needs additional support downstream of 1B-IAS-V-0319; Instrument Air supply to 1A GT Enclosure Interconnecting Duct Gas Detector | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-18 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09656 | Verified | Remove carbon contamination from 1A-IAS-V-0341; Instrument Air Drain Valve, Line No. 2-1B-IAS-0210 | C | X | Johnny Campbell | McD | 2019-10-16 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-08 | Bernard Stasse
IAS-03 | IAS-03 | PI09657 | Verified | Missing U-Bolt at Line No. 2-1B-IAS-0210, upstream of 1B-IAS-V-0334; Instrument Air supply to 1B GT Casing Cooling Air Shutoff Valve | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-18 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09658 | Verified | Need support at Line No. 2-1B-IAS-0210, upstream of 1B-IAS-0335; 1 inch Instrument Air supply to 1B GT Casing Cooling Air Supply Valve | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-18 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09659 | Verified | Instrument Air tubing leak at 1B GT Casing Cooling Air Supply Valve, Line No. | C | I | Gonzalo Pena | McD | 2019-10-16 | Gonzalo Pena | Comm | 2020-01-31 | Gonzalo Pena | 2020-04-08 | Bernard Stasse
IAS-03 | IAS-03 | PI09660 | Verified | Loose bolts at 1B-IAS-V-0318; 1 inch Instrument Air supply to 1B GT Exhaust Duct Gas Detector, Line No. 2-1B-IAS-0210 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09661 | Verified | Instrument Air tubing not connected from 1B-IAS-V-0318 to 1B GT Exhaust Duct Gas Detector | C | I | Gonzalo Pena | McD | 2019-10-16 | Gonzalo Pena | Comm | 2020-01-03 | Gonzalo Pena | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09662 | Verified | Instrument Air tubing not connected from 1B-IAS-V-0322 to 1B GT Enclosure Vent Fans Gas Detector | C | I | Gonzalo Pena | McD | 2019-10-16 | Gonzalo Pena | Comm | 2020-01-03 | Gonzalo Pena | 2020-01-10 | Blake Boudreaux
IAS-03 | IAS-03 | PI09663 | Verified | Remove tape from Line No. 2-1B-IAS-0216 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-08-20 | Nelson Eichelberger
IAS-03 | IAS-03 | PI09664 | Verified | No access to 1B-IAS-V-0323; 1 inch Instrument Air supply to 1B GT Cooling Air Cooler Drain Valve, Line No. | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-03 | IAS-03 | PI09665 | Verified | No access to 1B-IAS-V-0324; 1 inch Instrument Air supply to 1B GT Cooling Air Cooler Drain Valve, Line No. 2-1B-IAS-0216 | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-03 | IAS-03 | PI09666 | Verified | No access to 1B-IAS-V-0304; 1 inch Instrument Air supply to 1B TCA Cooler Feed Water Flow Control Valve (HRSG Side), Line No. 2-1B-IAS-0216 | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-03 | IAS-03 | PI09667 | Verified | Loose and missing bolts at 1B-IAS-V-0342; 1 inch Instrument Air drain valve, Line No. 2-1B-IAS-0216 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-17 | Bobby Williams | 2020-02-10 | Nelson Eichelberger
IAS-03 | IAS-03 | PI09668 | Verified | 1B Anti Icing Air Temperature Control Valve's A and B need to be reversed on P&ID LK-10-IAS-ME-PID-0003 to indicate east (B) and west (A), redline drawing, Line Line No. 2-1B-IAS-0216 | C | P | Kelvin Cook | McD | 2019-10-16 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-07-28 | Keith Pollock
IAS-03 | IAS-03 | PI09669 | Verified | No access to 1B-IAS-V-0327; 1 inch Instrument Air supply to 1B Anti-Icing Air Supply Valve | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-03 | IAS-03 | PI09670 | Verified | No access to 1B-IAS-V-0328; 1 inch Instrument Air supply to 1B Anti-Icing Air Balancing Valve | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-03 | IAS-03 | PI09671 | Verified | No access to 1B-IAS-V-0329; 1 inch Instrument Air supply to 1B Anti-Icing Air Drain Valve | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-03 | IAS-03 | PI09672 | Verified | No access to 1B-IAS-V-0326; 1 inch Instrument Air supply to 1B GT 2C Cooling Air Flow Control Valve | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-03 | IAS-03 | PI09673 | Verified | No access to 1B-IAS-V-0326; 1 inch Instrument Air supply to 1B GT 2C Cooling Air Flow Control Valve | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-03 | IAS-03 | PI09674 | Verified | Need double nuts on U-Bolt at 1B-IAS-V-0330; 1 inch Instrument Air supply to 1B Anti-Icing Air Temp Control Valve (A) | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-18 | Bobby Williams | 2020-02-10 | Nelson Eichelberger
IAS-03 | IAS-03 | PI09675 | Verified | Need double nuts on U-Bolt at 1B-IAS-V-0331; 1 inch Instrument Air supply to 1B Anti-Icing Air Temp Control Valve (B) | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2019-10-18 | Bobby Williams | 2020-02-10 | Nelson Eichelberger
IAS-03 | IAS-03 | PI09676 | Verified | No access to 1B-IAS-V-0365; 2 inch Instrument Air isolation valve, supply to 1B GT 2C Cooling Air Flow Control Valve's A and B, Line No. 2-1BIAS-0219 | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-03 | IAS-03 | PI09677 | Verified | No access to 1B-IAS-V-0370; 2 inch Instrument Air isolation valve, supply to 1B GT Lube Oil Temperature Control Valve | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-03 | IAS-03 | PI09678 | Verified | No access to 1B-IAS-V-0333; 1 inch Instrument Air supply to 1B GT Lube Oil Temp Control Valve | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
IAS-03 | IAS-03 | PI17192 | Verified | Valve tag missing on P&ID on IA valve to 1B CEMS | C | P | Kelvin Cook | McD | 2020-02-24 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-03-09 | Michael Law
IAS-04 | IAS-04 | PI01576 | Verified | Tag all valves. | C | P | Kelvin Cook | McD | 2019-06-26 | Kelvin Cook | Const |  |  | 2020-02-06 | Kelvin Cook
IAS-04 | IAS-04 | PI01577 | Verified | Tighten bolts on valve 1C-IAS-V-0127 at the STG lube oil skid. | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-07-11 | Stuart Herring
IAS-04 | IAS-04 | PI01578 | Verified | Need to turn valve 1C-IAS-V-0134 - interference with wall - at stator cooler skid area. | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-07-11 | Stuart Herring
IAS-04 | IAS-04 | PI01579 | Verified | Valve 1C-IAS-V-0408 handle missing rubber grip - at stator cooler skid area (at wall). | C | P | James Beech | McD | 2019-06-26 | James Beech | Const | 2019-09-18 | Damon Turner | 2020-01-27 | Michael Law
IAS-04 | IAS-04 | PI01580 | Verified | Need to turn valve 1C-IAS-V-0541 - conflict with column. Northwest corner of STG bldg. ground floor. | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-07-11 | Stuart Herring
IAS-04 | IAS-04 | PI01582 | Verified | U-bolt missing nuts - northwest corner of STG bldg. ground floor. | C | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-26 | Blake Boudreaux
IAS-04 | IAS-04 | PI01584 | Verified | On ISO 1C-IAS-PD-P41-0100-07 pipe support 1C-IAS-PD-HGR-0481 is not installed | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-07-01 | Damon Turner | 2019-07-10 | Kelvin Cook
IAS-04 | IAS-04 | PI01585 | Verified | On ISO 1C-IAS-PD-P41-0140-02 pipe support 1C-IAS-PD-HGR-0469,0470 not installed | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-07-10 | Kelvin Cook
IAS-04 | IAS-04 | PI01586 | Verified | On ISO 1C-IAS-PD-P41-0140-02 pipe support 1C-IAS-PD-HGR-0468 loose nut at eye bolt turnbuckle | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-07-10 | Kelvin Cook
IAS-04 | IAS-04 | PI01587 | Verified | On ISO 1C-IAS-PD-P41-0141-01 pipe support 1C-IAS-PD-HGR-0491 is not installed | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-07-10 | Kelvin Cook
IAS-04 | IAS-04 | PI01588 | Verified | On ISO 1C-IAS-PD-P41-0141-01 pipe support 1C-IAS-PD-HGR-0489 is not installed | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-07-10 | Kelvin Cook
IAS-04 | IAS-04 | PI01589 | Verified | On ISO 1C-IAS-PD-P41-0150-03 pipe support 1C-IAS-PD-HGR-0498 is not installed | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-07-09 | Michael Law | 2019-07-10 | Kelvin Cook
IAS-04 | IAS-04 | PI01590 | Verified | On ISO 1C-IAS-PD-P41-0150-06 valve handle missing rubber cover on 1C-IAS-V-0181 | C | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-09-18 | Damon Turner | 2019-10-03 | Kelvin Cook
IAS-04 | IAS-04 | PI01591 | Verified | On ISO 1C-IAS-PD-P41-0210-01 pipe support 1C-IAS-PD-HGR-0438 is not installed | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-07-09 | Michael Law | 2019-07-10 | Kelvin Cook
IAS-04 | IAS-04 | PI02243 | Verified | On ISO 1C-IAS-PD-P41-0141-01 pipe support 1C-IAS-PD-HGR-0488 no ss wrap. | B | P | Damon Turner | McD | 2019-07-10 | Damon Turner | Const | 2019-07-19 | Damon Turner | 2019-08-02 | Kelvin Cook
IAS-04 | IAS-04 | PI09413 | Verified | Remove carbon contamination from Line No. 2-1C-IAS-0210 vertical and horizontal, STG Bldg | C | X | Johnny Campbell | McD | 2019-10-11 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-08 | Bernard Stasse
IAS-04 | IAS-04 | PI09414 | Verified | Remove carbon contamination from Line No. 2-1C-IAS-0141, STG Bldg | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-04-08 | Bernard Stasse
IAS-04 | IAS-04 | PI09415 | Verified | Remove carbon contamination from Line No. 2-1C-IAS-0100 main header at 2-1C-IAS-0141 'T", STG Bldg. | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-04-08 | Bernard Stasse
IAS-04 | IAS-04 | PI09416 | Verified | Rod hanger not connected at Line No. 2-1C-IAS-V-0130 to Condenser Vacuum Pumps, STG Bldg, S mezzaine deck | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-04 | IAS-04 | PI09417 | Verified | Remove rope from Line No. 2-IC-IAS-0140, STG Bldg, NW corner mezzanine | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-04 | IAS-04 | PI09418 | Verified | Loose bolts at 1C-IAS-V-0412, .75 inch Instrument Air supply to IA-HRS-PV-0030, STG Bldg Turbine Deck | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-04-08 | Bernard Stasse
IAS-04 | IAS-04 | PI09419 | Verified | Remove carbon contamination at 1C-IAS-V-0212, .75 inch Instrument Air supply to 1A-MSS-AOV-0086, STG Bldg Turbine Deck | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-04-08 | Bernard Stasse
IAS-04 | IAS-04 | PI09420 | Verified | Remove carbon contamination at 1C-IAS-V-0216, .75 inch Instrument Air supply to 1A-MSS-AOV-0086, STG Bldg Turbine Deck | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-04-08 | Bernard Stasse
IAS-04 | IAS-04 | PI12696 | Verified | 1C-IAS-V-0123 - Has instrument air leak on the backside of the valve. This valve supplies air to Recirc AOV 10-CCW-PV-0131. | B | I | Gonzalo Pena | McD | 2019-11-01 | Gonzalo Pena | Comm |  |  | 2020-01-23 | Shannon Scott
IAS-04 | IAS-04 | PI13970 | Verified | 10-IAS-PD-P41-0190-10: Install 3/4" SW x 1/2" swage fittings to all six valves. | A | I | Gonzalo Pena | McD | 2019-12-05 | Gonzalo Pena | Comm |  |  | 2019-12-06 | Kelvin Cook
IAS-04 | IAS-04 | PI16203 | Verified | 1C-IAS-V-0298 - Drain valve not working - to repair during outage. valve currently in service | C | P | Albert Burge | McD | 2020-01-20 | Albert Burge | Comm | 2020-03-07 | Tim Green | 2020-04-06 | Bernard Stasse
LAN-01 | LAN-01 | PI02257 | Verified | Cable 1ALANK0001 missing tag in 1A GT control package. | C | E | Dustin Futrell | McD | 2019-07-10 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-16 | Albert Burge
LAN-01 | LAN-01 | PI02258 | Verified | Cable 1BLANK0001 missing tag in 1B GT control package. | C | E | Dustin Futrell | McD | 2019-07-10 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-16 | Albert Burge
LAN-01 | LAN-01 | PI02259 | Verified | Plug the top of the receptacle in 1A-LAN-CAB-0001 in the 1A GT control package. | C | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-22 | Ken Mundy | 2019-08-02 | Fred Michael
LAN-01 | LAN-01 | PI02260 | Verified | Plug the top of the receptacle in 1B-LAN-CAB-0001 in the 1B GT control package. | C | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-22 | Ken Mundy | 2019-08-02 | Fred Michael
LAN-01 | LAN-01 | PI02261 | Verified | Seal conduit in 10-LAN-CAB-0007 in the Main PDC. | B | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-17 | Ken Mundy | 2019-07-23 | Mike Tabbert
LAN-01 | LAN-01 | PI02262 | Verified | Clean 10-LAN-CAB-0007 in the Main PDC. | B | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-17 | Ken Mundy | 2019-07-23 | Mike Tabbert
LAN-01 | LAN-01 | PI02263 | Verified | Clean inside LAN cabinets in the Control Building. | B | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-18 | Ken Mundy | 2019-07-23 | Mike Tabbert
LAN-01 | LAN-01 | PI02264 | Verified | Ground 10-LAN-CAB-0007 in the Main PDC. | A | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-30 | C_AC03
LAN-01 | LAN-01 | PI02265 | Verified | Strut on top of 10-LAN-CAB-0007 missing 2 bolts & nuts - Main PDC. | C | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-19 | Fred Michael
LAN-01 | LAN-01 | PI02266 | Verified | Receptacle in 10-LAN-CAB-0007 missing self tapping screw. | C | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-19 | Fred Michael
LAN-01 | LAN-01 | PI02267 | Verified | Cable 10LANK0008 missing tag - Cooling Tower PDC. | C | E | Dustin Futrell | McD | 2019-07-10 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-10-05 | Mike Tabbert
LAN-01 | LAN-01 | PI02269 | Verified | Ground conduit for 10-LAN-CAB-0008 in the Cooling Tower PDC. | A | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
LAN-01 | LAN-01 | PI02270 | Verified | Ground conduit for 1A-LAN-CAB-0002 in the 1A HRSG PDC. | A | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
LAN-01 | LAN-01 | PI02271 | Verified | Ground conduit for 1B-LAN-CAB-0002 in the 1B HRSG PDC. | A | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
LAN-01 | LAN-01 | PI02272 | Verified | Vacuum out 1B-LAN-CAB-0003 in the 1B CEMs bldg. | A | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
LAN-01 | LAN-01 | PI02273 | Verified | Cable 1BLANK0003 missing tag in the 1B CEMs bldg. | C | E | Chris Colvin | McD | 2019-07-10 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
LAN-01 | LAN-01 | PI02274 | Verified | Label cabinets 1A-LAN-CAB-0001, 1B-LAN-CAB-0001, 10-LAN-CAB-0007, 10-LAN-CAB-0008, 1A-LAN-CAB-0002, 1B-LAN-CAB-0002, 1A-LAN-CAB-0003, 1B-LAN-CAB-0003. | C | E | Dustin Futrell | McD | 2019-07-10 | Dustin Futrell | Const | 2019-07-20 | Ken Mundy | 2019-08-21 | Fred Michael
LAN-01 | LAN-01 | PI02275 | Verified | 10LANO0003, Pull Cable | A | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-29 | Mike Tabbert | 2019-07-29 | Mike Tabbert
LAN-01 | LAN-01 | PI02276 | Verified | 1ALANK0001, Terminate Cable | A | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
LAN-01 | LAN-01 | PI02277 | Verified | 1ALANK0002, Terminate Cable | A | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
LAN-01 | LAN-01 | PI02278 | Verified | 1BLANK0001, Terminate Cable | A | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
LAN-01 | LAN-01 | PI02279 | Verified | 1BLANK0002, Terminate Cable | A | E | Luis Cantu | McD | 2019-07-10 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-16 | Mike Tabbert
LAN-01 | LAN-01 | PI02280 | Verified | 10LANO0001, Terminate Cable | A | E | Sheri Fritz | ITS | 2019-07-10 | Sheri Fritz | Const | 2019-07-19 | Mike Tabbert | 2019-07-19 | Mike Tabbert
LAN-01 | LAN-01 | PI02281 | Verified | 10LANO0003, Terminate Cable | A | E | Sheri Fritz | ITS | 2019-07-10 | Sheri Fritz | Const | 2019-07-29 | Mike Tabbert | 2019-07-29 | Mike Tabbert
LAN-01 | LAN-01 | PI02282 | Verified | Control Building, Terminate all LAN drops in Control Building | A | E | Sheri Fritz | ITS | 2019-07-10 | Sheri Fritz | Const | 2019-07-18 | Mike Tabbert | 2019-07-18 | Mike Tabbert
LAN-01 | LAN-01 | PI02283 | Verified | Control Building, Install JMO cables and Fiber Patch Cables to Operators Console Mitzubitshi and Toshiba. | A | E | Sheri Fritz | ITS | 2019-07-10 | Sheri Fritz | Const | 2019-07-18 | Mike Tabbert | 2019-07-18 | Mike Tabbert
LAN-01 | LAN-01 | PI02284 | Verified | Cooling Tower PDC, Complete LAN Cabinet and Drops. | A | E | Sheri Fritz | ITS | 2019-07-10 | Sheri Fritz | Const | 2019-07-18 | Mike Tabbert | 2019-07-18 | Mike Tabbert
LAN-01 | LAN-01 | PI14528 | Verified | Ground cable connection inside panel is loose at 1A-LAN-CAB-0003; CEMS A LAN Cabinet | B | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
LAN-01 | LAN-01 | PI14529 | Verified | Heat shrink cable 1ALANK0003 ID tag inside 1A-LAN-CAB-0003; CEMS A LAN Cabinet | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-04-06 | Bernard Stasse
LAN-01 | LAN-01 | PI14530 | Verified | Seal building LAN cable penetrations to 1A-LAN-CAB-0003; CEMS A LAN Cabinet | B | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-26 | Chris Colvin | 2020-04-06 | Bernard Stasse
LAN-01 | LAN-01 | PI14531 | Verified | Cable penetration into CEMS Bldg A need CBG's replaced or repaired, currently not weather proof | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-04-07 | Randy Carpenter
LAN-01 | LAN-01 | PI14532 | Verified | Cable penetration into CEMS Bldg B need CBG's replaced or repaired, currently not weather proof | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-04-07 | Randy Carpenter
LAN-01 | LAN-01 | PI14533 | Verified | Panel door ground disconnected inside 1A-LAN-CAB-0002; HRSG A PDC LAN Cabinet (use ring lugs not forks at connection)Fix building cable | B | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-26 | Chris Colvin | 2020-04-06 | Bernard Stasse
LAN-01 | LAN-01 | PI14534 | Verified | Seal 1B-LAN-CAB-0002; HRSG B PDC LAN Cabinet penetration at floor | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-04-28 | Matt Gilmore | 2020-10-06 | Dave Goldak
LAN-01 | LAN-01 | PI14535 | Verified | Panel door, back plate and panel ground disconnected inside 10-LAN-CAB-0008; Cooling Tower PDC LAN Cabinet | B | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-26 | Chris Colvin | 2020-04-06 | Bernard Stasse
LAN-01 | LAN-01 | PI14536 | Verified | Seal 10-LAN-CAB-0008; Cooling Tower PDC LAN Cabinet cable penetration at floor | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-04-22 | Matt Gilmore | 2020-10-06 | Dave Goldak
LAN-01 | LAN-01 | PI14537 | Verified | Tighten 10-LAN-CAB-0008; Cooling Tower PDC LAN Cabinet conduit clamp at floor penetration | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-10-06 | Eric Policarpio | 2020-10-06 | Dave Goldak
LAN-01 | LAN-01 | PI14538 | Verified | Conduit floor penetration floor plate is missing screws at 10-LAN-CAB-0008; Cooling Tower PDC LAN Cabinet | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-04-22 | Matt Gilmore | 2020-10-06 | Dave Goldak
LAN-01 | LAN-01 | PI14539 | Verified | Clean off top of 10-LAN-CAB-0007; Main PDC Lan Cabinet | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-04-07 | Randy Carpenter
LAN-01 | LAN-01 | PI14540 | Verified | Clean out inside of 10-LAN-CAB-0007; Main PDC LAN Cabinet | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-04-01 | Chris Colvin | 2020-04-07 | Randy Carpenter
LAN-01 | LAN-01 | PI14541 | Verified | Clean plexi-glass cover inside 10-LAN-CAB-0007; Main PDC LAN Cabinet | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-04-07 | Bernard Stasse
LAN-01 | LAN-01 | PI14542 | Verified | Remove plywood under 10-LAN-CAB-0007; Main PDC LAN Cabinet | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-04-07 | Bernard Stasse
LAN-01 | LAN-01 | PI14543 | Verified | Seal hole at top of 10-LAN-CAB-0007; Main PDC LAN Cabinet | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-04-01 | Chris Colvin | 2020-04-07 | Bernard Stasse
LAN-01 | LAN-01 | PI14544 | Verified | Door ground is loose on W side of 10-LAN-CAB-0007; Main PDC LAN Cabinet | B | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-26 | Chris Colvin | 2020-04-06 | Bernard Stasse
LAN-01 | LAN-01 | PI14545 | Verified | Seal cable penetration to 10-LAN-CAB-0007; Main PDC LAN Cabinet under Main PDC | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-05-04 | Matt Gilmore | 2020-10-06 | Dave Goldak
LAN-01 | LAN-01 | PI14546 | Verified | Verify isolated ground cable to 10-LAN-CAB-0007; Main PDC LAN Cabinet under Main PDC | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-02-24 | Mike Tabbert | 2020-04-06 | Bernard Stasse
LAN-01 | LAN-01 | PI14547 | Verified | Ground to panel missing at 1A-LAN-CAB-0001; 1A Control Package LAN Cabinet | B | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-26 | Chris Colvin | 2020-04-06 | Bernard Stasse
LAN-01 | LAN-01 | PI14548 | Verified | Seal 1A-LAN-CAB-0001; 1A Control Package LAN Cabinet cable penetration at floor | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-15 | Shannon Scott
LAN-01 | LAN-01 | PI14549 | Verified | Clean off rust and paint inside of 1A-LAN-CAB-0001; 1A Control Package LAN Cabinet | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm |  |  | 2020-02-10 | Fred Michael
LAN-01 | LAN-01 | PI14550 | Verified | 1B-LAN-CAB-0001; 1B Control Package LAN Cabinet panel is not grounded | B | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-26 | Chris Colvin | 2020-04-06 | Bernard Stasse
LAN-01 | LAN-01 | PI14551 | Verified | Seal 1B-LAN-CAB-0001; 1B Control Package LAN Cabinet cable penetration at floor | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-06 | Bernard Stasse
LAN-01 | LAN-01 | PI14552 | Verified | Clean off top of 1B-LAN-CAB-0001; 1B Control Package LAN Cabinet | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm |  |  | 2020-02-10 | Fred Michael
LAN-01 | LAN-01 | PI14553 | Verified | Replace yellow fiber optic tray end covers at 10-LAN-CAB-0001 thru 0005; Control Room LAN Cabinets | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-04-28 | Michael Law | 2021-01-05 | Keith Pollock
LAN-01 | LAN-01 | PI14554 | Verified | Pull 50' of additional fiber optic cable to 10-LAN-CAB-0005 inside Control Room for Entergy Main Fiber tie-in | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-05-12 | Michael Law | 2021-01-05 | Keith Pollock
LAN-01 | LAN-01 | PI14555 | Verified | Need cable penetration protection at 10-LAN-CAB-0001 inside Control Room | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2021-06-10 | Eric Policarpio | 2021-06-10 | John Watts
LAN-01 | LAN-01 | PI14556 | Verified | Turn in all LAN Cabinet keys to Entergy | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-04-07 | Bernard Stasse
LAN-01 | LAN-01 | PI18217 | Verified | 10LANK0014 cable to terminate during outage | C | E | Chris Colvin | McD | 2020-04-20 | Chris Colvin | Comm | 2020-04-30 | Chris Colvin | 2020-05-04 | Mike Tabbert
LAN-01 | LAN-01 | PI18218 | Verified | 10LANO0005 cable to install during outage | C | E | Chris Colvin | McD | 2020-04-20 | Chris Colvin |  | 2020-04-20 | Mike Tabbert | 2020-04-20 | Mike Tabbert
LAN-01 | LAN-01 | PI18219 | Verified | 1CLANK0001 cable to terminate during outage | C | E | Chris Colvin | McD | 2020-04-20 | Chris Colvin | Comm | 2020-04-30 | Chris Colvin | 2020-05-04 | Mike Tabbert
LAN-01 | LAN-01 | PI18220 | Verified | 1CSECK0001 cable to terminate during outage | C | E | Chris Colvin | McD | 2020-04-20 | Chris Colvin | Comm | 2020-04-30 | Chris Colvin | 2020-05-04 | Mike Tabbert
LAN-01 | LAN-01 | PI18236 | Verified | Tag missing on 1CSECK0001 on LAN Panel at 1C Sample building | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
LPS-01 | LPS-01 | PI07047 | Verified | Set all spring cans to cold settings. | A | P | James Beech | McD | 2019-09-24 | James Beech | Const | 2019-12-15 | Bobby Williams | 2020-01-21 | Michael Law
LPS-01 | LPS-01 | PI07048 | Verified | Restore strainer 1C-LPS-STN-9000. STG mezz. | A | P | Damon Turner | McD | 2019-09-24 | Damon Turner | Const |  |  | 2019-10-03 | Alex Isaac
LPS-01 | LPS-01 | PI07049 | Verified | Complete drip legs (2) at condenser. STG mezz. | A | P | James Beech | McD | 2019-09-24 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI07050 | Verified | Tag all valves. | C | P | James Beech | McD | 2019-09-24 | James Beech | Const | 2020-05-04 | Michael Law | 2020-05-04 | Michael Law
LPS-01 | LPS-01 | PI07051 | Verified | Bolt up incomplete at valve 1C-LPS-PV-9000. STG mezz. | A | P | James Beech | McD | 2019-09-24 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI07052 | Verified | Bolt up incomplete at valve 1C-LPS-HYV-9000. STG mezz. | A | P | James Beech | McD | 2019-09-24 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI07053 | Verified | 1C-LPS-PD-HGR-0515 not installed per design. STG mezz. | A | P | Damon Turner | McD | 2019-09-24 | Damon Turner | Const |  |  | 2019-10-03 | Alex Isaac
LPS-01 | LPS-01 | PI07054 | Verified | 1C-LPS-PD-HGR-0514 not installed per design. STG mezz. | A | P | Damon Turner | McD | 2019-09-24 | Damon Turner | Const |  |  | 2019-10-03 | Alex Isaac
LPS-01 | LPS-01 | PI07055 | Verified | 1C-LPS-0049 - line not installed. STG mezz. | A | P | Damon Turner | McD | 2019-09-24 | Damon Turner | Const |  |  | 2019-10-03 | Alex Isaac
LPS-01 | LPS-01 | PI07056 | Verified | 1C-LPS-0010 - line not installed. STG mezz. | A | P | James Beech | McD | 2019-09-24 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI07057 | Verified | 1C-LPS-0040 - line not installed. Turbine deck. | A | P | James Beech | McD | 2019-09-24 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI07774 | Verified | Support 1C-CRS-PD-HGR-0902 not installed per design, should be centered on beam. | A | P | Bobby Williams | McD | 2019-09-28 | Bobby Williams | Const | 2019-10-01 | Alex Isaac | 2019-10-01 | Alex Isaac
LPS-01 | LPS-01 | PI08462 | Verified | Support 1A-LPS-PD-HGR-0502 not set per design, hanger should not be on angle. | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08463 | Verified | Support 1A-LPS-PD-HGR-0504 not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-12-02 | Bobby Williams | 2019-12-09 | Shane Copeland
LPS-01 | LPS-01 | PI08464 | Verified | Support 1A-LPS-PD-HGR-0500 not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-12-02 | Bobby Williams | 2019-12-09 | Shane Copeland
LPS-01 | LPS-01 | PI08465 | Verified | 1A-LPS-FE-8715 not installed (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2020-02-06 | James Beech | 2020-02-07 | Kelvin Cook
LPS-01 | LPS-01 | PI08466 | Verified | Tag not installed on valve 1A-LPS-MOV-0050 | C | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2020-02-07 | Kelvin Cook
LPS-01 | LPS-01 | PI08467 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08468 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08469 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08470 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08471 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08472 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08473 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08474 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08475 | Verified | Install spool PS-1A-LPS-P41-0010-09-152-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2020-02-06 | James Beech | 2020-02-06 | Kelvin Cook
LPS-01 | LPS-01 | PI08476 | Verified | Install spool PS-1A-LPS-P41-0010-10-152-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2020-02-06 | James Beech | 2020-02-06 | Kelvin Cook
LPS-01 | LPS-01 | PI08477 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08478 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08479 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08480 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08481 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08482 | Verified | Support 1B-LPS-PD-HGR-0532 not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-12-02 | Bobby Williams | 2019-12-09 | Shane Copeland
LPS-01 | LPS-01 | PI08483 | Verified | Support 1B-LPS-PD-HGR-0529 not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-12-02 | Bobby Williams | 2019-12-09 | Shane Copeland
LPS-01 | LPS-01 | PI08484 | Verified | Support 1B-LPS-PD-HGR-0526 not set per design | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-12-02 | Bobby Williams | 2019-12-09 | Shane Copeland
LPS-01 | LPS-01 | PI08485 | Verified | 1B-LPS-FE-8715 not installed (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI08486 | Verified | Support 1B-LPS-PD-HGR-0910 not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08487 | Verified | Tag not installed on valve 1B-LPS-MOV-0050 | C | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2020-02-07 | Kelvin Cook
LPS-01 | LPS-01 | PI08488 | Verified | Install spool PS-1B-LPS-P41-0010-09-151-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI08489 | Verified | Install spool PS-1B-LPS-P41-0010-10-151-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI08490 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08491 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08492 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08493 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08494 | Verified | Support 1C-LPS-PD-HGR-0508 not set per design | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-11-22 | Bobby Williams | 2019-11-24 | Alex Isaac
LPS-01 | LPS-01 | PI08495 | Verified | Support 1C-LPS-PD-HGR-0510 not complete | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08496 | Verified | Strainer 1C-LPS-STN-9000 missing bolts and gasket (NEED FOR HYDRO) | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08497 | Verified | Support 1C-LPS-PD-HGR-0512 not installed per design | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08498 | Verified | Loose bolts on support 1C-LPS-PD-HGR-0905, also not welded to steel per design | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08499 | Verified | Support 1C-LPS-PD-HGR-0535 not installed per design | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-11-22 | Bobby Williams | 2019-11-24 | Alex Isaac
LPS-01 | LPS-01 | PI08500 | Verified | Weld not made to TOSHIBA valve 1C-STE-MOV-9510 | A | P | James Beech | McD | 2019-10-03 | James Beech | Const |  |  | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08501 | Verified | Remove permanent support 1C-LPS-PD-HGR-0514-1 AND install hydro support 1C-LPS-PD-HGR-0514-2 | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-11-22 | Bobby Williams | 2019-11-24 | Alex Isaac
LPS-01 | LPS-01 | PI08502 | Verified | Remove permanent support 1C-LPS-PD-HGR-0515-1 AND install hydro support 1C-LPS-PD-HGR-0515-2 | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-11-22 | Bobby Williams | 2019-11-24 | Alex Isaac
LPS-01 | LPS-01 | PI08503 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08504 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08505 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08506 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08507 | Verified | Tag not installed on valve 1C-LPS-V-0086 | C | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08508 | Verified | Tag not installed on valve 1C-LPS-V-0085 | C | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08509 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08510 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08511 | Verified | Line not installed | A | P | James Beech | McD | 2019-10-03 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-16 | Alex Isaac
LPS-01 | LPS-01 | PI08801 | Verified | 1A-LPS-MOV-1052 Valve is under grating and no access. | C | S | James Beech | McD | 2019-10-04 | James Beech | Const | 2021-06-10 | Eric Policarpio | 2021-06-10 | John Watts
LPS-01 | LPS-01 | PI08802 | Verified | 1B-LPS-MOV-1052 Valve is under grating and no access. | C | S | James Beech | McD | 2019-10-04 | James Beech | Const | 2021-06-10 | Eric Policarpio | 2021-06-10 | John Watts
LPS-01 | LPS-01 | PI09816 | Verified | Test Package LPS-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-26 | Kelvin Cook
LPS-01 | LPS-01 | PI09817 | Verified | Test Package LPS-T-02 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-23 | Kelvin Cook
LPS-01 | LPS-01 | PI09909 | Verified | 1BLPSK0004 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
LPS-01 | LPS-01 | PI09910 | Verified | 1BLPSC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
LPS-01 | LPS-01 | PI09911 | Verified | 1BLPSC0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
LPS-01 | LPS-01 | PI09912 | Verified | 1BLPSC0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
LPS-01 | LPS-01 | PI09913 | Verified | 1BLPSK0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
LPS-01 | LPS-01 | PI10256 | Verified | Seal weld 1C-LPS-TW-9017 (AFTER STEAM BLOW). | B | P | James Beech | McD | 2019-10-24 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI10257 | Verified | Seal weld 1C-LPS-TW-0019A (AFTER STEAM BLOW). | B | P | James Beech | McD | 2019-10-24 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI10258 | Verified | Seal weld 1C-LPS-TW-0019B (AFTER STEAM BLOW). | B | P | James Beech | McD | 2019-10-24 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI10259 | Verified | Replace valve 1A-SSS-V-8719 (LEAKED BY DURING HYDRO. | A | P | Bobby Williams | McD | 2019-10-24 | Bobby Williams | Const | 2019-12-03 | Shane Copeland | 2019-12-06 | Shane Copeland
LPS-01 | LPS-01 | PI11793 | Verified | 1BLPSK0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
LPS-01 | LPS-01 | PI12126 | Verified | Replace stem packing on valve 1C-LPS-HYV-9000 (LEAKED DURING HYDRO). | A | P | James Beech | McD | 2019-10-25 | James Beech | Const | 2019-12-03 | Shane Copeland | 2019-12-06 | Shane Copeland
LPS-01 | LPS-01 | PI12127 | Verified | Replace stem packing on valve 1C-LPS-PV-9000 (LEAKED DURING HYDRO). | A | P | James Beech | McD | 2019-10-25 | James Beech | Const | 2019-12-03 | Shane Copeland | 2019-12-06 | Shane Copeland
LPS-01 | LPS-01 | PI13086 | Verified | Install final trim on valve 1C-LPS-PV-0020 AFTER STEAM BLOW) | A | P | James Beech | CCI | 2019-11-15 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI13087 | Verified | Remove flush trim and install final trim and actuator on valve 1C-LPS-TV-0083 (AFTER STEAM BLOW) | A | P | James Beech | CCI | 2019-11-15 | James Beech | Const | 2019-12-17 | James Beech | 2019-12-17 | Shane Copeland
LPS-01 | LPS-01 | PI13102 | Verified | Install internals in valve 1A-LPS-MOV-8710 (AFTER STEAM BLOW) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2020-02-03 | Billy Williams | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI13103 | Verified | Install internals in valve 1B-LPS-MOV-8710 (AFTER STEAM BLOW) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2020-02-03 | Bobby Williams | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI13104 | Verified | Install internals in valve 1A-LPS-CHK-8711 (AFTER STEAM BLOW) | A | P | James Beech | CWX | 2019-11-15 | James Beech | Const | 2020-02-03 | Bobby Williams | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI13105 | Verified | Install internals in valve 1B-LPS-CHK-8711 (AFTER STEAM BLOW) | A | P | Bobby Williams | CWX | 2019-11-15 | Bobby Williams | Const | 2020-02-03 | Bobby Williams | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI13106 | Verified | Install internals in valve 1A-IPS-CHK-8308 (AFTER STEAM BLOW) | A | P | Bobby Williams | CWX | 2019-11-15 | Bobby Williams | Const | 2020-01-31 | Bobby Williams | 2020-01-31 | Kelvin Cook
LPS-01 | LPS-01 | PI13107 | Verified | Install internals in valve 1B-IPS-CHK-8308 (AFTER STEAM BLOW) | A | P | Bobby Williams | CWX | 2019-11-15 | Bobby Williams | Const | 2020-02-02 | Bobby Williams | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI13247 | Verified | Pipe Support Number: 1A-LPS-PD-HGR-0504: Ref. Iso. LK-1A-LPS-PD-P40-0010-01: Pipe Support is not Installed. Need Item 1; 16" Pipe Clamp. Field Craft may be working as scaffolding and chain falls are in place and insulation is removed. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-03 | Bobby Williams | 2019-12-12 | Gary Pickeral
LPS-01 | LPS-01 | PI13248 | Verified | Pipe Support Number: 1A-LPS-PD-HGR-0500: Ref. Iso. LK-1A-LPS-PD-P40-0010-02: This support is FUBAR…Fowled Up Beyond All Recognition. Seriously, there are parts of this support scatterd over an eleven foot section of Pipe. The Structural Frame is installed on location as designed, but supporting nothing. The bottom Shoe is installed 7'-4" South of the designed location and the Welded Pipe Attachemts (welded on at the shop) are located 4 ft. North of the Designed Location and installed at 30 degree angles from horizontal. All components are present, but the Welded Pipe Attachments are at the wrong location and have wrong orentation. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-03 | Bobby Williams | 2019-12-12 | Gary Pickeral
LPS-01 | LPS-01 | PI13249 | Verified | Pipe Support Number: 1A-LPS-PD-HGR-0505: Ref. Iso. LK-1A-LPS-PD-P40-0010-03: This support is missing, or thought to be part of 1A-LPS-PD-HGR-0500 (see punch list item above). When support 1A-LPS-PD-HGR-0500 is repaired, this support 1A-LPS-PD-HGR-0505 must be installed (the vertical span will be too long without this support installed). | A | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-05 | Bobby Williams | 2019-12-05 | James Beech
LPS-01 | LPS-01 | PI13250 | Verified | Pipe Support Number: 1B-LPS-PD-HGR-0532: Ref. Iso. LK-1B-LPS-PD-P40-0010-01: This support is not Installed. Field Craft may be working as scaffolding and chain falls are in place and insulation is removed. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-03 | Bobby Williams | 2019-12-19 | Gary Pickeral
LPS-01 | LPS-01 | PI13251 | Verified | Pipe Support Number: 1B-LPS-PD-HGR-0526: Ref. Iso. LK-1B-LPS-PD-P40-0010-01: This Clamp On Shoe has Rolled Over. Confirm Repair | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-03 | Bobby Williams | 2019-12-12 | Gary Pickeral
LPS-01 | LPS-01 | PI13252 | Verified | Pipe Support Number: 1B-LPS-PD-HGR-0529: Ref. Iso. LK-1B-LPS-PD-P40-0010-01: I cannot see the N-S Strut (Scafolding and plastic are blocking my view). | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-03 | Bobby Williams | 2020-01-07 | Ethan Byrd
LPS-01 | LPS-01 | PI13253 | Verified | Pipe Support Number: 1C-LPS-PD-HGR-0508: Ref. Iso. LK-1C-LPS-PD-P40-0010-01: Pipe Shoe does not appear to be welded to Trapeze. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-03 | Bobby Williams | 2020-01-07 | Ethan Byrd
LPS-01 | LPS-01 | PI13254 | Verified | Pipe Support Number: 1C-LPS-PD-HGR-0516: Ref. Iso. LK-1C-LPS-PD-P40-0010-01: Pipe Shoe does not appear to be welded to Trapeze. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-03 | Bobby Williams | 2020-01-07 | Ethan Byrd
LPS-01 | LPS-01 | PI13255 | Verified | Pipe Support Number: 1C-LPS-PD-HGR-0513: Ref. Iso. LK-1C-LPS-PD-P40-0010-05: This Support has be partially Disassembled and Disengaged from Pipe for valve removal in preparation for Steam Blow. This support must be Re-instated and Travel Stops removed prior to Steam Blow. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-03 | Bobby Williams | 2020-01-07 | Ethan Byrd
LPS-01 | LPS-01 | PI13256 | Verified | Pipe Support Number: 1C-LPS-PD-HGR-0514: Ref. Iso. LK-1C-LPS-PD-P40-0010-06: Pipe Shoe does not appear to be welded to Trapeze. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-03 | Bobby Williams | 2020-01-07 | Ethan Byrd
LPS-01 | LPS-01 | PI13257 | Verified | Pipe Support Number: 1C-LPS-PD-HGR-0515: Ref. Iso. LK-1C-LPS-PD-P40-0010-06: Pipe Shoe does not appear to be welded to Trapeze. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-03 | Bobby Williams | 2020-01-07 | Ethan Byrd
LPS-01 | LPS-01 | PI13438 | Verified | Remove hydro support 1C-LPS-PD-HGR-0514-2 and install permanent support 1C-LPS-PD-HGR-0514-1. | A | P | James Beech | McD | 2019-11-24 | James Beech | Const | 2019-12-06 | Bobby Williams | 2019-12-10 | Shane Copeland
LPS-01 | LPS-01 | PI13439 | Verified | Remove hydro support 1C-LPS-PD-HGR-0515-2 and install permanent support 1C-LPS-PD-HGR-0515-1. | A | P | James Beech | McD | 2019-11-24 | James Beech | Const | 2019-12-06 | Bobby Williams | 2019-12-10 | Shane Copeland
LPS-01 | LPS-01 | PI14449 | Verified | 1C-LPS-AOV-0050 - installed in wrong location. Install after steam blows. | A | P | James Beech | McD | 2019-12-06 | James Beech | Const | 2019-12-17 | James Beech | 2020-01-09 | Albert Burge
LPS-01 | LPS-01 | PI14450 | Verified | 1B-LPS-AOV-0020 - flex too short. (in pipe rack). | A | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const | 2019-12-11 | Brad Stanford | 2019-12-11 | Fred Michael
LPS-01 | LPS-01 | PI14451 | Verified | 1B-LPS-AOV-0020 - complete tubing (in pipe rack). | A | I | Gonzalo Pena | McD | 2019-12-06 | Gonzalo Pena | Const | 2019-12-13 | Michael Law | 2019-12-19 | Albert Burge
LPS-01 | LPS-01 | PI14452 | Verified | 1A-LPS-AOV-0020 - complete tubing (in pipe rack). | A | I | Gonzalo Pena | McD | 2019-12-06 | Gonzalo Pena | Const | 2019-12-13 | Michael Law | 2019-12-19 | Albert Burge
LPS-01 | LPS-01 | PI14453 | Verified | 1C-LPS-PIT-9014B - damaged terminal block in transmitter cover. | A | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
LPS-01 | LPS-01 | PI14454 | Verified | Replace tags for 1C-LPS-PIT-9014A & B. Current tags have 1V-1C-LPS | C | I | Gonzalo Pena | McD | 2019-12-06 | Gonzalo Pena | Const |  |  | 2019-12-13 | John Sullivan
LPS-01 | LPS-01 | PI14455 | Verified | 1A-LPS-CAB-0001 - label. (west side of HRSG A). | C | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const |  |  | 2019-12-13 | John Sullivan
LPS-01 | LPS-01 | PI14456 | Verified | 1A-LPS-CAB-0001 - cap unistrut supports ends. (west side of HRSG A). | C | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-19 | Randy Carpenter
LPS-01 | LPS-01 | PI14457 | Verified | 1B-LPS-CAB-0001 - label (west side of HRSG A). | C | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const |  |  | 2019-12-13 | John Sullivan
LPS-01 | LPS-01 | PI14458 | Verified | 1A-LPS-CAB-0001 - replace all thread nipple to cabinet with proper nipple. (west side of HRSG A). | A | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const | 2019-12-11 | Brad Stanford | 2019-12-14 | Mike Tabbert
LPS-01 | LPS-01 | PI14459 | Verified | 1A-LPS-CAB-0001 - ground conduits (overhead). (west side of HRSG A). | A | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-14 | Mike Tabbert
LPS-01 | LPS-01 | PI14460 | Verified | 1A-LPS-CAB-0001 - grout support for conduit (west side of HRSG A). | C | C | Alan Huntsman | McD | 2019-12-06 | Alan Huntsman | Const | 2020-03-13 | Johnny Campbell | 2020-03-31 | Randy Carpenter
LPS-01 | LPS-01 | PI14461 | Verified | Cables for both 1C-LPS-LEH and LEHH-0060 are landed at the LEHH. Term the wire properly at the LEHH and move the proper cable to the LEH (likely too short). | A | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14462 | Verified | 1C-LPS-PDIT-0013 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-12-06 | Gonzalo Pena | Const | 2019-12-13 | Michael Law | 2019-12-19 | Randy Carpenter
LPS-01 | LPS-01 | PI14463 | Verified | Condulet covers missing at 1C-LPS-TE-9017 (STG mezz). | B | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-18 | Mike Tabbert
LPS-01 | LPS-01 | PI14464 | Verified | 1C-LPS-PIT-0020 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-12-06 | Gonzalo Pena | Const | 2019-12-10 | Gonzalo Pena | 2019-12-10 | Fred Michael
LPS-01 | LPS-01 | PI14465 | Verified | 1C-LPS-PIT-0020 - needs brace / support. | B | I | Gonzalo Pena | McD | 2019-12-06 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2019-12-14 | Fred Michael
LPS-01 | LPS-01 | PI14466 | Verified | 1C-LPS-PIT-0020 - stand base plate needs washers. | C | I | Gonzalo Pena | McD | 2019-12-06 | Gonzalo Pena | Const |  |  | 2019-12-14 | Fred Michael
LPS-01 | LPS-01 | PI14467 | Verified | 1C-LPS-PIT-0020 - tighten flex. | A | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const | 2019-12-11 | Brad Stanford | 2019-12-11 | Fred Michael
LPS-01 | LPS-01 | PI14468 | Verified | 1C-LPS-PIT-9025 - tag instrument. | C | I | Gonzalo Pena | McD | 2019-12-06 | Gonzalo Pena | Const |  |  | 2019-12-13 | John Sullivan
LPS-01 | LPS-01 | PI14469 | Verified | 1C-LPS-PIT-9025 - heat shrink tube bundle. | B | I | Gonzalo Pena | McD | 2019-12-06 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2020-01-15 | Albert Burge
LPS-01 | LPS-01 | PI14470 | Verified | 1C-LPS-TV-0083 - not installed. | A | P | James Beech | McD | 2019-12-06 | James Beech | Const | 2019-12-17 | James Beech | 2019-12-19 | Albert Burge
LPS-01 | LPS-01 | PI14471 | Verified | Cables 1CLPSC0004, 1CLPSX0001, 1CLPSX0013 - all in the same conduit. Split the X cables into separate conduit. | A | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const | 2020-02-21 | Chris Colvin | 2020-02-21 | Mike Tabbert
LPS-01 | LPS-01 | PI14472 | Verified | 1A-LPS-LSH-0040 - missing many components. | A | E | Chris Colvin | McD | 2019-12-06 | Chris Colvin | Const | 2019-12-11 | James Tanner | 2019-12-14 | Mike Tabbert
LPS-01 | LPS-01 | PI14473 | Verified | 1A-LPS-LSH-0040 - covered by insulation. | A | I | Sheri Fritz | McD | 2019-12-06 | Sheri Fritz | Const | 2019-12-11 | James Tanner | 2019-12-14 | Mike Tabbert
LPS-01 | LPS-01 | PI14474 | Verified | 1ALPSC0007, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14475 | Verified | 1ALPSC0008, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14476 | Verified | 1BLPSC0007, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14477 | Verified | 1BLPSC0008, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14478 | Verified | 1BLPSC0011, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14479 | Verified | 1CLPSC0001, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14480 | Verified | 1CLPSC0002, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14481 | Verified | 1CLPSC0003, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14482 | Verified | 1CLPSC0004, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14483 | Verified | 1CLPSC0013, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14484 | Verified | 1CLPSC0014, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14485 | Verified | 1CLPSX0001, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14486 | Verified | 1CLPSX0002, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14487 | Verified | 1CLPSX0005, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14488 | Verified | 1CLPSX0010, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14489 | Verified | 1CLPSX0011, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14490 | Verified | 1CLPSX0012, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14491 | Verified | 1CLPSX0013, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14492 | Verified | 1CLPSX0014, From Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14493 | Verified | 1ALPSC0008, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14494 | Verified | 1ALPSX0005, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const |  |  | 2019-12-14 | Mike Tabbert
LPS-01 | LPS-01 | PI14495 | Verified | 1BLPSC0008, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14496 | Verified | 1BLPSC0010, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
LPS-01 | LPS-01 | PI14497 | Verified | 1BLPSC0011, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
LPS-01 | LPS-01 | PI14498 | Verified | 1BLPSX0004, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
LPS-01 | LPS-01 | PI14499 | Verified | 1BLPSX0005, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const |  |  | 2019-12-14 | Mike Tabbert
LPS-01 | LPS-01 | PI14500 | Verified | 1CLPSC0001, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14501 | Verified | 1CLPSC0002, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14502 | Verified | 1CLPSC0003, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14503 | Verified | 1CLPSC0004, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14504 | Verified | 1CLPSC0013, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
LPS-01 | LPS-01 | PI14505 | Verified | 1CLPSC0014, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
LPS-01 | LPS-01 | PI14506 | Verified | 1CLPSC0015, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14507 | Verified | 1CLPSC0016, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14508 | Verified | 1CLPSC0017, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-20 | Mike Tabbert
LPS-01 | LPS-01 | PI14509 | Verified | 1CLPSC0018, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Mike Tabbert | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14510 | Verified | 1CLPSX0001, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14511 | Verified | 1CLPSX0002, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
LPS-01 | LPS-01 | PI14512 | Verified | 1CLPSX0005, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const |  |  | 2020-02-07 | Mike Tabbert
LPS-01 | LPS-01 | PI14513 | Verified | 1CLPSX0007, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
LPS-01 | LPS-01 | PI14514 | Verified | 1CLPSX0008, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
LPS-01 | LPS-01 | PI14515 | Verified | 1CLPSX0009, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
LPS-01 | LPS-01 | PI14516 | Verified | 1CLPSX0010, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14517 | Verified | 1CLPSX0011, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
LPS-01 | LPS-01 | PI14518 | Verified | 1CLPSX0012, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-20 | Mike Tabbert
LPS-01 | LPS-01 | PI14519 | Verified | 1CLPSX0013, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
LPS-01 | LPS-01 | PI14520 | Verified | 1CLPSX0014, To Termination | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const |  |  | 2020-02-07 | Mike Tabbert
LPS-01 | LPS-01 | PI14521 | Verified | 1C-LPS-TE-0056 Install TE | A | I | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Const | 2019-12-11 | James Tanner | 2019-12-12 | James Tanner
LPS-01 | LPS-01 | PI14522 | Verified | 1C-LPS-TE-0016 Install TE | A | I | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Const | 2019-12-13 | Michael Law | 2019-12-16 | James Tanner
LPS-01 | LPS-01 | PI14684 | Verified | 1ALPSX0003, To Termination | A | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-20 | Mike Tabbert
LPS-01 | LPS-01 | PI14685 | Verified | 1BLPSX0003, To Termination | A | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-20 | Mike Tabbert
LPS-01 | LPS-01 | PI14701 | Verified | 1C-LPS-PIT-0020-NEED TO SHRINK BOOT ON TUBE BUNDLE. | B | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-13 | John Sullivan
LPS-01 | LPS-01 | PI14702 | Verified | 1C-LPS-PIT-0025-NEED TO SHRINK BOOT ON TUBE BUNDLE | B | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-13 | John Sullivan
LPS-01 | LPS-01 | PI14703 | Verified | 1C-LPS-PIT-9014B-INSTRUMENT COVER NEEDS SOME ATTENTION. HARD TO GET ON AND OFF. | C | I | Gonzalo Pena | McD | 2019-12-11 | Gonzalo Pena | Const | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
LPS-01 | LPS-01 | PI14704 | Verified | 1C-LPS-PIT-0025-NEED TO INSTALL I.D. TAG. | C | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-13 | John Sullivan
LPS-01 | LPS-01 | PI14719 | Verified | 1B-LPS-PD-P41-0010-04: 1B-LPS-HGR-0517 was located 12/7/19 need to verify item 3 and 4 are installed per the detail. | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-13 | Bobby Williams | 2019-12-14 | Kelvin Cook
LPS-01 | LPS-01 | PI14730 | Verified | 1C-LPS-PD-P41-0056-01: 1C-LPS-HGR-0072 Located on 12/9/19 and needs to be installed. | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-15 | Bobby Williams | 2019-12-16 | Kelvin Cook
LPS-01 | LPS-01 | PI14744 | Verified | 1A-LPS-TE-0030 Covered by insulation. | A | Q | Sheri Fritz | PCI | 2019-12-12 | Sheri Fritz | Const | 2019-12-13 | Michael Law | 2019-12-16 | James Beech
LPS-01 | LPS-01 | PI14745 | Verified | 1B-LPS-TE-0030 Covered by insulation. | A | Q | Sheri Fritz | PCI | 2019-12-12 | Sheri Fritz | Const | 2019-12-13 | Michael Law | 2019-12-16 | James Beech
LPS-01 | LPS-01 | PI14746 | Verified | 1A-LPS-TE-0030 Not installed. | A | I | Gonzalo Pena | McD | 2019-12-12 | Gonzalo Pena | Const | 2019-12-13 | Michael Law | 2019-12-14 | Fred Michael
LPS-01 | LPS-01 | PI14747 | Verified | 1B-LPS-TE-0030 Not installed. | A | I | Gonzalo Pena | McD | 2019-12-12 | Gonzalo Pena | Const | 2019-12-13 | Michael Law | 2019-12-14 | Fred Michael
LPS-01 | LPS-01 | PI14808 | Verified | NEED TO INSTALL I.D. TAG ON 1C-LPS-PIT-0020.(1C-HTS-CAB-0203) | C | I | James Tanner | McD | 2019-12-15 | James Tanner | Const | 2019-12-31 | Gonzalo Pena | 2020-01-14 | John Sullivan
LPS-01 | LPS-01 | PI14822 | Verified | NEED TO INSTALL TUBE BUNDLE FOR 1A-LPS-FIT-8715.(1A-HTS-CAB-0313) | A | I | Gonzalo Pena | McD | 2019-12-15 | Gonzalo Pena | Const | 2020-02-12 | James Tanner | 2020-02-13 | John Sullivan
LPS-01 | LPS-01 | PI15834 | Verified | Install Condensing Pot (2 each) 1A-LPS-FIT-8715 | B | P | James Beech | McD | 2020-01-09 | James Beech | Const | 2020-02-06 | James Beech | 2020-02-06 | Kelvin Cook
LPS-01 | LPS-01 | PI15835 | Verified | Install Condensing Pot (2 each) 1B-LPS-FIT-8715 | B | P | James Beech | McD | 2020-01-09 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI15836 | Verified | Install Condensing Pot (2 each)1C-LPS-FIT-0013 | B | P | James Beech | McD | 2020-01-09 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI16032 | Verified | Install Final Trim on valve 1C-LPS-PV-0020 | A | P | James Beech | McD | 2020-01-14 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
LPS-01 | LPS-01 | PI17451 | Verified | 1C-LPS-PDIT-0013 is tubed backwards. | B | I | James Beech | McD | 2020-03-02 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-03-07 | Albert Burge
MBL-01 | MBL-01 | PI02047 | Verified | Tag all valves in the subsystem | C | P | James Beech | McD | 2019-07-02 | James Beech | Const | 2019-07-18 | Terry Deaton | 2019-12-19 | Kelvin Cook
MBL-01 | MBL-01 | PI02048 | Verified | Tag all instruments in the sytem | C | I | Gonzalo Pena | McD | 2019-07-02 | Gonzalo Pena | Const | 2019-07-10 | Gonzalo Pena | 2019-10-03 | Kelvin Cook
MBL-01 | MBL-01 | PI02049 | Verified | Grout all pipe supports | C | C | Johnny Campbell | McD | 2019-07-02 | Johnny Campbell | Const | 2019-09-12 | Jack Fields | 2019-10-03 | Kelvin Cook
MBL-01 | MBL-01 | PI02050 | Verified | On ISO 1A-MBL-PD-P40-0020-01 install the proper gasket at flange connection to 1A-MBL-P-0100A | A | P | Terry Deaton | McD | 2019-07-02 | Terry Deaton | Const | 2019-07-18 | Terry Deaton | 2019-07-19 | Kelvin Cook
MBL-01 | MBL-01 | PI02051 | Verified | On ISO 1A-MBL-PD-P40-0020-01 connection to ISO 1A-MBL-PD-P41-0020-02 is not installed | A | P | Terry Deaton | McD | 2019-07-02 | Terry Deaton | Const | 2019-07-18 | Terry Deaton | 2019-07-19 | Kelvin Cook
MBL-01 | MBL-01 | PI02052 | Verified | On ISO 1A-MBL-PD-P40-0021-01 install the proper gasket at flange connection to 1A-MBL-P-0100B | A | P | Terry Deaton | McD | 2019-07-02 | Terry Deaton | Const | 2019-07-18 | Terry Deaton | 2019-07-19 | Kelvin Cook
MBL-01 | MBL-01 | PI02062 | Verified | Torque flanges | A | P | Terry Deaton | McD | 2019-07-02 | Terry Deaton | Const | 2019-07-18 | Terry Deaton | 2019-08-15 | Justin Houdeshell
MBL-01 | MBL-01 | PI02072 | Verified | East side HP Drum Level gauges missing | A | P | Bobby Williams | McD | 2019-07-02 | Bobby Williams | Const | 2019-08-16 | Bobby Williams | 2019-08-16 | Kelvin Cook
MBL-01 | MBL-01 | PI02552 | Verified | LK-10-MBL-PD-P40-0033-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-03 | Terry Deaton | 2019-08-03 | Tom Noble
MBL-01 | MBL-01 | PI02553 | Verified | LK-1A-MBL-PD-P41-0036-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-16 | Tom Noble
MBL-01 | MBL-01 | PI04266 | Verified | Perform clean & close on HRSG Blowdown Sump 1A-MBL-SUMP-0001. | A | P | Shane Crowe | McD | 2019-08-15 | Shane Crowe | Const | 2019-09-05 | Shane Crowe | 2019-09-05 | Joshua Sturgeon
MBL-01 | MBL-01 | PI04267 | Verified | Install plug on 1A-MBL-LG-8803 on Blowdown Tank. | A | P | Bobby Williams | McD | 2019-08-15 | Bobby Williams | Const | 2019-08-27 | Bobby Williams | 2019-08-28 | Kelvin Cook
MBL-01 | MBL-01 | PI04268 | Verified | Complete all tagging. | C | P | Kelvin Cook | McD | 2019-08-15 | Kelvin Cook | Const |  |  | 2020-02-07 | Kelvin Cook
MBL-01 | MBL-01 | PI04269 | Verified | Install valve and sump drain in the Blowdown Tank containment. | A | P | Terry Deaton | McD | 2019-08-15 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-16 | Kelvin Cook
MBL-01 | MBL-01 | PI04270 | Verified | Perform clean & close on the HRSG Atmospheric Blowdown Tank 1A-MBL-T-8801. | A | M | Shane Crowe | McD | 2019-08-15 | Shane Crowe | Const | 2019-08-21 | Joshua Sturgeon | 2019-08-21 | Joshua Sturgeon
MBL-01 | MBL-01 | PI04271 | Verified | Install plug on Blowdown Tank spare port - south side. | A | P | Bobby Williams | McD | 2019-08-15 | Bobby Williams | Const | 2019-08-27 | Bobby Williams | 2019-08-28 | Kelvin Cook
MBL-01 | MBL-01 | PI04272 | Verified | 1A-MBL-LIT-0001 flange missing bolt - at pumps. | A | I | Gonzalo Pena | McD | 2019-08-15 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-08-28 | Kelvin Cook
MBL-01 | MBL-01 | PI04273 | Verified | Remove rigging, etc. from blowdown pump area. | B | P | Terry Deaton | McD | 2019-08-15 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-27 | Kelvin Cook
MBL-01 | MBL-01 | PI04274 | Verified | Restore Blowdown Tank 3" piping after pressure testing ( 5 lines). | B | P | Bobby Williams | McD | 2019-08-16 | Bobby Williams | Const | 2019-12-02 | Bobby Williams | 2019-12-06 | Kelvin Cook
MBL-01 | MBL-01 | PI04601 | Verified | Install stilling well for 1A-MBL-LIT-0001 at HGRS blowdown sump | A | I | Gonzalo Pena | McD | 2019-08-24 | Gonzalo Pena | Const | 2019-09-06 | Gonzalo Pena | 2019-09-11 | Kelvin Cook
MBL-01 | MBL-01 | PI04788 | Verified | Ground BD sump pump motors MBL-0100A & B. | A | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-26 | Logan Holland
MBL-01 | MBL-01 | PI04790 | Verified | Pour seal offs for BD sump pump motors MBL-0100A & B. After commissioning. | B | E | Chris Colvin | McD | 2019-09-06 | Chris Colvin | Const |  |  | 2020-01-13 | Fred Michael
MBL-01 | MBL-01 | PI04792 | Verified | Remove unused conduit at BD sump pump motors MBL-0100A & B & plug heater box. | A | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Fred Michael
MBL-01 | MBL-01 | PI04794 | Verified | Install condulet covers at BD sump pumps and BD tank. | B | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Fred Michael
MBL-01 | MBL-01 | PI04796 | Verified | Cut the 4 bolts in concrete flush on the east side of the BD sump. | B | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Fred Michael
MBL-01 | MBL-01 | PI04798 | Verified | Level up & weld conduit supports at the BD sump pumps. | B | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-11 | Dustin Futrell | 2019-09-11 | Fred Michael
MBL-01 | MBL-01 | PI04800 | Verified | Grounds at the NE & SW corners of the blowdown tank need to be dressed. Cut & seal the conduit. | A | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Mike Tabbert
MBL-01 | MBL-01 | PI04802 | Verified | Grout conduit supports in the Blowdown Tank area. | C | C | Johnny Campbell | McD | 2019-09-06 | Johnny Campbell | Const | 2019-09-11 | Mike Tabbert | 2019-09-25 | Shannon Scott
MBL-01 | MBL-01 | PI04804 | Verified | Cap all supprts / struts in the BD area. | C | C | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Fred Michael
MBL-01 | MBL-01 | PI04806 | Verified | The BD sump LIT stilling well washers / lock washers need to be SS or same material as support. | B | I | Gonzalo Pena | McD | 2019-09-06 | Gonzalo Pena | Const | 2019-09-09 | Gonzalo Pena | 2019-09-11 | Fred Michael
MBL-01 | MBL-01 | PI04807 | Verified | Replace nipple on BD sump pump motor term. boxes 0100A & B. 1-1/2" x close. | A | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Mike Tabbert
MBL-01 | MBL-01 | PI04811 | Verified | Fix conduit at MBL-LIT-0001 at the BD sump and add support. | A | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Fred Michael
MBL-01 | MBL-01 | PI07242 | Verified | 1A-MBL-LIT-8801 not wired from 1A-MBS-JB-8001 to DCS. 1AMBSX0020. | A | E | Chris Colvin | McD | 2019-09-26 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
MBL-01 | MBL-01 | PI12715 | Verified | 1A-MBL-P-0100A - send pump out for bearing modification work. | B | M | Shane Crowe | McD | 2019-11-04 | Shane Crowe | Comm |  |  | 2019-11-22 | Joshua Sturgeon
MBL-01 | MBL-01 | PI12716 | Verified | 1A-MBL-P-0100B - send pump out for bearing modification work. | B | M | Shane Crowe | McD | 2019-11-04 | Shane Crowe | Comm |  |  | 2019-11-22 | Joshua Sturgeon
MBL-01 | MBL-01 | PI14852 | Verified | Install 6" riser clamp and shim accordingly to make the flange level 1A-MLB-LIT-0001 | B | P | James Beech | McD | 2019-12-20 | James Beech | Comm | 2020-01-14 | James Beech | 2020-01-16 | Ethan Byrd
MBL-01 | MBL-01 | PI16676 | Verified | 1B-MBL-CHK-0011A - 1B HRSG Blowdown Sump Pump A, check valve is leaking through | B | M | William Mitchell | McD | 2020-02-07 | William Mitchell | Comm | 2020-03-05 | William Mitchell | 2020-04-06 | Bernard Stasse
MBL-01 | MBL-01 | PI17836 | Verified | 1A-MBL-P-0100A and 1A-MBL-P-0100B - When 1A HRSG Blowdown Sump Pumps A and B get too hot, the motors over amp and trip so we cannot run them. This causes the sump to overflow. | C | M | William Mitchell | McD | 2020-03-16 | William Mitchell | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
MBL-01 | MBL-01 | PI18095 | Verified | 1A-MBL-P-0100A, 1A-MBL-P-0100B, 1A-MBL-TI-8804, and 1A-MBL-T-8801 - HRSG blowdown sump pumps 1A-MBL-P-0100A/B are designed for 200F. However, the temperature range on thermocouple, 1A-MBL-TI-8804, is 0-450F. The normal operation temperature on the tank is on average 200F. Operating of the pumps close to or over max discharge temperature of the pumps can cause severe damage to the pumps. The damage could cause a need for a temporary diesel pump(s). | D | M | Charles Worthington | McD | 2020-03-18 | Charles Worthington | Comm | 2020-05-11 | Michael Law | 2020-07-22 | John Watts
MBL-01 | MBL-01 | PI18096 | Verified | 1B-MBL-P-0100A, 1B-MBL-P-0100B, 1B-MBL-TI-8804, and 1B-MBL-T-8801 - HRSG blowdown sump pumps 1B-MBL-P-0100A/B are designed for 200F. However, the temperature range on thermocouple, 1B-MBL-TI-8804, is 0-450F. The normal operation temperature on the tank is on average 200F. Operating of the pumps close to or over max discharge temperature of the pumps can cause severe damage to the pumps. The damage could cause a need for a temporary diesel pump(s). | D | M | Charles Worthington | McD | 2020-03-18 | Charles Worthington | Comm | 2020-05-11 | Michael Law | 2020-07-22 | John Watts
MBL-01 | MBL-01 | PI18102 | Verified | 1A HRSG - Stainless Steel U-Bolts holding up the baffles in the HRSG. There is a concern of them being used with a dissimilar metal on the baffle, and it leads to failures and damage to the tube bundles. | D | P | Charles Worthington | McD | 2020-03-18 | Charles Worthington | Comm | 2020-05-06 | Michael Law | 2020-07-22 | John Watts
MBL-02 | MBL-02 | PI02053 | Verified | Grout all pipe supports | C | C | Johnny Campbell | McD | 2019-07-02 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2019-12-15 | Kelvin Cook
MBL-02 | MBL-02 | PI02054 | Verified | Tag all valves in the system | C | P | James Beech | McD | 2019-07-02 | James Beech | Const | 2019-07-18 | Terry Deaton | 2019-12-19 | Kelvin Cook
MBL-02 | MBL-02 | PI02055 | Verified | On ISO 1B-MBL-PD-P40-0020-01 install the proper gasket at flange connection to 1B-MBL-P-0100A | A | P | Terry Deaton | McD | 2019-07-02 | Terry Deaton | Const | 2019-07-18 | Terry Deaton | 2019-07-19 | Kelvin Cook
MBL-02 | MBL-02 | PI02056 | Verified | On ISO 1B-MBL-PD-P40-0020-01 connection to ISO 1B-MBL-PD-P41-0020-02 is not installed | A | P | Terry Deaton | McD | 2019-07-02 | Terry Deaton | Const | 2019-07-18 | Terry Deaton | 2019-07-19 | Kelvin Cook
MBL-02 | MBL-02 | PI02057 | Verified | On ISO 1B-MBL-PD-P40-0021-01 install the proper gasket at flange connection to 1B-MBL-P-0100B | A | P | Terry Deaton | McD | 2019-07-02 | Terry Deaton | Const | 2019-07-18 | Terry Deaton | 2019-07-19 | Kelvin Cook
MBL-02 | MBL-02 | PI02058 | Verified | Tag all instruments in the subsytem | C | I | Gonzalo Pena | McD | 2019-07-02 | Gonzalo Pena | Const | 2019-07-10 | Gonzalo Pena | 2019-10-03 | Kelvin Cook
MBL-02 | MBL-02 | PI02059 | Verified | Fix valve stem (replace valve) 1B-MBL-V-0012A | A | P | Terry Deaton | McD | 2019-07-02 | Terry Deaton | Const | 2019-08-05 | Terry Deaton | 2019-08-05 | Justin Houdeshell
MBL-02 | MBL-02 | PI02060 | Verified | Install 10-MBL-P41-0032-01 | A | P | Terry Deaton | McD | 2019-07-02 | Terry Deaton | Const | 2019-08-15 | Terry Deaton | 2019-08-15 | Justin Houdeshell
MBL-02 | MBL-02 | PI02061 | Verified | check 1B-MBL-MOV-0020 Solenoid | A | P | Bobby Williams | McD | 2019-07-02 | Bobby Williams | Const | 2019-08-16 | Bobby Williams | 2020-01-21 | Michael Law
MBL-02 | MBL-02 | PI02063 | Verified | Torque flanges | A | P | Terry Deaton | McD | 2019-07-02 | Terry Deaton | Const | 2019-07-19 | Terry Deaton | 2019-08-15 | Justin Houdeshell
MBL-02 | MBL-02 | PI02064 | Verified | West side of HP Drum is inaccessible | A | P | Bobby Williams | McD | 2019-07-02 | Bobby Williams | Const | 2019-08-16 | Kelvin Cook | 2019-08-16 | Kelvin Cook
MBL-02 | MBL-02 | PI02065 | Verified | East side of IP Level Gauge drains are inaccessible | A | P | Bobby Williams | McD | 2019-07-02 | Bobby Williams | Const | 2019-08-16 | Kelvin Cook | 2019-08-16 | Kelvin Cook
MBL-02 | MBL-02 | PI02066 | Verified | 1" HP-109 to HP-30-A incomplete | A | P | Bobby Williams | McD | 2019-07-02 | Bobby Williams | Const | 2019-08-16 | Bobby Williams | 2019-09-11 | Kelvin Cook
MBL-02 | MBL-02 | PI02067 | Verified | 1" RP-107 to RP-02A incomplete | A | P | Bobby Williams | McD | 2019-07-02 | Bobby Williams | Const | 2019-08-16 | Bobby Williams | 2019-09-11 | Kelvin Cook
MBL-02 | MBL-02 | PI02068 | Verified | 1" HD-01-C incomplete | A | P | Bobby Williams | McD | 2019-07-02 | Bobby Williams | Const | 2019-08-27 | Bobby Williams | 2019-09-04 | Kelvin Cook
MBL-02 | MBL-02 | PI02069 | Verified | 1" HD-01-M incomplete | A | P | Bobby Williams | McD | 2019-07-02 | Bobby Williams | Const | 2019-08-28 | Bobby Williams | 2019-09-04 | Kelvin Cook
MBL-02 | MBL-02 | PI02070 | Verified | Grout Blowdown tank | A | C | Johnny Campbell | McD | 2019-07-02 | Johnny Campbell | Const | 2019-07-25 | Jack Fields | 2019-08-19 | Kelvin Cook
MBL-02 | MBL-02 | PI02071 | Verified | 1-1/2" HP-102 supports missing washers | A | P | Bobby Williams | McD | 2019-07-02 | Bobby Williams | Const | 2019-08-27 | Bobby Williams | 2019-09-04 | Kelvin Cook
MBL-02 | MBL-02 | PI02554 | Verified | LK-10-MBL-PD-P41-0033-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-13 | Tom Noble
MBL-02 | MBL-02 | PI02555 | Verified | LK-1B-CTS-PD-P42-0069-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-13 | Tom Noble
MBL-02 | MBL-02 | PI02556 | Verified | LK-1B-MBL-PD-P41-0036-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-16 | Tom Noble
MBL-02 | MBL-02 | PI04256 | Verified | Valve 1B-MBL-V-0012 handwheel is bent at the BD pumps. | A | P | Bobby Williams | McD | 2019-08-15 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-10-03 | Kelvin Cook
MBL-02 | MBL-02 | PI04257 | Verified | Perform clean & close on HRSG Blowdown Sump 1B-MBL-SUMP-0001. | A | P | Shane Crowe | McD | 2019-08-15 | Shane Crowe | Const | 2019-09-13 | Shane Crowe | 2019-09-13 | Joshua Sturgeon
MBL-02 | MBL-02 | PI04258 | Verified | Install plug on 1B-MBL-LG-8803 on Blowdown Tank. | A | P | Bobby Williams | McD | 2019-08-15 | Bobby Williams | Const | 2019-08-27 | Bobby Williams | 2019-08-28 | Kelvin Cook
MBL-02 | MBL-02 | PI04259 | Verified | Complete all tagging. | C | P | Kelvin Cook | McD | 2019-08-15 | Kelvin Cook | Const |  |  | 2020-02-07 | Kelvin Cook
MBL-02 | MBL-02 | PI04260 | Verified | Restore Blowdown Tank 3" piping after pressure testing ( 5 lines). | B | P | Bobby Williams | McD | 2019-08-15 | Bobby Williams | Const | 2019-12-05 | Bobby Williams | 2019-12-06 | Kelvin Cook
MBL-02 | MBL-02 | PI04261 | Verified | There are manual pushbottons missing on MOV valve operators - west side of Blowdown Tank. | B | E | Chris Boudreaux | McD | 2019-08-15 | Chris Boudreaux | Const | 2019-09-27 | Alex Isaac | 2019-09-27 | Alex Isaac
MBL-02 | MBL-02 | PI04262 | Verified | Install valve and sump drain in the Blowdown Tank containment. | A | P | Terry Deaton | McD | 2019-08-15 | Terry Deaton | Const | 2019-08-16 | Kelvin Cook | 2019-08-16 | Kelvin Cook
MBL-02 | MBL-02 | PI04263 | Verified | Perform clean & close on the HRSG Atmospheric Blowdown Tank 1B-MBL-T-8801. | A | M | Shane Crowe | McD | 2019-08-15 | Shane Crowe | Const | 2019-08-21 | Joshua Sturgeon | 2019-08-21 | Joshua Sturgeon
MBL-02 | MBL-02 | PI04264 | Verified | Install plug on Blowdown Tank spare port - south side. | A | P | Bobby Williams | McD | 2019-08-15 | Bobby Williams | Const | 2019-08-28 | Bobby Williams | 2019-09-04 | Kelvin Cook
MBL-02 | MBL-02 | PI04265 | Verified | Nooter to update P&ID 501 - remove 2" spare port on top of tank and add 1" spare port on south side of tank. | C | M | Alex Isaac | NOO | 2019-08-15 | Alex Isaac | Const |  |  | 2019-11-23 | Kelvin Cook
MBL-02 | MBL-02 | PI04602 | Verified | Install stilling well for 1B-MBL-LIT-0001 at HGRS blowdown sump | A | I | Gonzalo Pena | McD | 2019-08-24 | Gonzalo Pena | Const | 2019-09-09 | Gonzalo Pena | 2019-09-11 | Kelvin Cook
MBL-02 | MBL-02 | PI04789 | Verified | Ground BD sump pump motors MBL-0100A & B. | A | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-09-11 | Fred Michael
MBL-02 | MBL-02 | PI04791 | Verified | Pour seal offs for BD sump pump motors MBL-0100A & B. After commissioning. | B | E | Chris Colvin | McD | 2019-09-06 | Chris Colvin | Const | 2020-02-26 | Mike Tabbert | 2020-02-27 | Fred Michael
MBL-02 | MBL-02 | PI04793 | Verified | Remove unused conduit at BD sump pump motors MBL-0100A & B & plug heater box. | A | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Fred Michael
MBL-02 | MBL-02 | PI04795 | Verified | Install condulet covers at BD sump pumps and BD tank. | B | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Fred Michael
MBL-02 | MBL-02 | PI04797 | Verified | Cut the 4 bolts in concrete flush on the east side of the BD sump. | B | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Fred Michael
MBL-02 | MBL-02 | PI04799 | Verified | Level up & weld conduit supports at the BD sump pumps. | B | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-11 | Dustin Futrell | 2019-09-11 | Fred Michael
MBL-02 | MBL-02 | PI04801 | Verified | Grounds at the NE & SW corners of the blowdown tank need to be dressed. Cut & seal the conduit. | A | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-10-05 | Mike Tabbert
MBL-02 | MBL-02 | PI04803 | Verified | Grout conduit supports in the Blowdown Tank area. | C | C | Johnny Campbell | McD | 2019-09-06 | Johnny Campbell | Const | 2019-09-12 | Jack Fields | 2019-09-25 | Shannon Scott
MBL-02 | MBL-02 | PI04805 | Verified | Cap all supprts / struts in the BD area. | C | C | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Fred Michael
MBL-02 | MBL-02 | PI04808 | Verified | Ground 1B-LIT-8803 at the BD tank. | A | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-09-16 | Albert Burge
MBL-02 | MBL-02 | PI04809 | Verified | Ground seal tite on 1B-MBL-FV-8261. Top of HRSG. | A | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Fred Michael
MBL-02 | MBL-02 | PI04810 | Verified | Connect IA tubing on 1B-MBL-FV-8261. Top of HRSG. | A | I | Gonzalo Pena | McD | 2019-09-06 | Gonzalo Pena | Const | 2019-09-11 | Gonzalo Pena | 2019-09-11 | Fred Michael
MBL-02 | MBL-02 | PI04812 | Verified | Fix conduit at MBL-LIT-0001 at the BD sump and add support. | A | E | Dustin Futrell | McD | 2019-09-06 | Dustin Futrell | Const | 2019-09-11 | Richard Cruz | 2019-09-11 | Fred Michael
MBL-02 | MBL-02 | PI07243 | Verified | 1B-MBL-LIT-8801 not wired from 1B-MBS-JB-8001 to DCS. 1BMBSX0020. | A | E | Chris Colvin | McD | 2019-09-26 | Chris Colvin | Const |  |  | 2020-01-28 | Fred Michael
MBL-02 | MBL-02 | PI12717 | Verified | 1B-MBL-P-0100A - send pump out for bearing modification work. | B | M | Shane Crowe | McD | 2019-11-04 | Shane Crowe | Comm |  |  | 2019-11-22 | Joshua Sturgeon
MBL-02 | MBL-02 | PI12718 | Verified | 1B-MBL-P-0100B - send pump out for bearing modification work. | B | M | Shane Crowe | McD | 2019-11-04 | Shane Crowe | Comm |  |  | 2019-11-22 | Joshua Sturgeon
MBL-02 | MBL-02 | PI14853 | Verified | Install 6" riser clamp and shim accordingly to make the flange level 1B-MLB-LIT-0001 | B | P | James Beech | McD | 2019-12-20 | James Beech | Comm | 2020-01-14 | James Beech | 2020-01-16 | Ethan Byrd
MBL-02 | MBL-02 | PI15566 | Verified | 1B-MBL-MOV-8510 - 1B-MBL-MOV-8510 will not seat fully closed allowing leak by. To isolate flow upstream, the root valve was manually closed. | C | P | Albert Burge | McD | 2020-01-08 | Albert Burge | Comm | 2020-05-20 | Alan Joiner | 2021-06-17 | John Watts
MBL-02 | MBL-02 | PI15567 | Verified | 1B-MBL-MOV-8517 - 1B-MBL-MOV-8517 has no power to it, and it can't be controlled from the control room. There's condensation in the display. The upstream root valves have been isolated. | C | E | Chris Boudreaux | McD | 2020-01-08 | Chris Boudreaux | Comm |  |  | 2020-01-23 | Shannon Scott
MBL-02 | MBL-02 | PI17673 | Verified | 1B-MBL-CHK-0011A - 1B's HRSG Blowdown Sump Pump 'A' has a check valve that's leaking through. | B | M | William Mitchell | McD | 2020-03-04 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-04-30 | John Watts
MBL-02 | MBL-02 | PI17837 | Verified | 1B-MBL-P-0100A and 1B-MBL-P-0100B - When 1B HRSG Blowdown Sump Pumps A and B get too hot, the motors over amp and trip so we cannot run them. This causes the sump to overflow. | C | M | William Mitchell | McD | 2020-03-16 | William Mitchell | Const | 2020-03-31 | William Mitchell | 2020-06-04 | Tanner Hillman
MBL-02 | MBL-02 | PI17838 | Verified | 1B-IPS-V-8240 and 1B-IPS-V-8244 - Unit “B” IP Drum level vent valves leaking. | C | M | William Mitchell | McD | 2020-03-16 | William Mitchell | Const | 2020-03-31 | William Mitchell | 2020-06-04 | Tanner Hillman
MBL-02 | MBL-02 | PI18103 | Verified | 1B HRSG - Stainless Steel U-Bolts holding up the baffles in the HRSG. There is a concern of them being used with a dissimilar metal on the baffle, and it leads to failures and damage to the tube bundles. | D | P | Charles Worthington | McD | 2020-03-18 | Charles Worthington | Comm | 2020-05-06 | Michael Law | 2020-07-22 | John Watts
MBL-02 | MBL-02 | PI18105 | Verified | 1B-MBL-MOV-8517 - 1B-MBL-MOV-8517 preheater 3 drain is failing to close around 26%. The valve must be drove closed by hand. | C | P | Albert Burge | McD | 2020-03-20 | Albert Burge | Comm | 2020-05-20 | Alan Joiner | 2021-06-17 | John Watts
MBS-01 | MBS-01 | PI06543 | Verified | Tag all valves with proper tag numbers, (1A-). Currently tagged 1X-. | C | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-15 | Shannon Scott
MBS-01 | MBS-01 | PI06551 | Verified | Remove all plastic from piping (under HRSG). | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-11-06 | Bobby Williams | 2020-01-21 | Michael Law
MBS-01 | MBS-01 | PI06559 | Verified | Set all spring cans to cold settings. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-12-20 | Bobby Williams | 2020-01-21 | Michael Law
MBS-01 | MBS-01 | PI06976 | Verified | Loose nuts on support HPS01PS07 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI06977 | Verified | Restore valve 1A-FWS-LV-8002A (after degrease) | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const |  |  | 2019-12-02 | Shane Copeland
MBS-01 | MBS-01 | PI06978 | Verified | Handwheel not installed on valve 1A-FWS-V-8008 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Alex Isaac | 2019-09-25 | Alex Isaac
MBS-01 | MBS-01 | PI06979 | Verified | Support HPS01PS02 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-17 | Alex Isaac
MBS-01 | MBS-01 | PI06980 | Verified | Restore valve 1A-FWS-LV-8002B (AFTER degrease) | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const |  |  | 2019-12-02 | Shane Copeland
MBS-01 | MBS-01 | PI06981 | Verified | 1A-FWS-TP-8010 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI06982 | Verified | Line needs better support | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI06983 | Verified | 1A-FWS-TP-8012 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI06984 | Verified | Remove rigging at support HPS19PS04 | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI06985 | Verified | Support HPS20APS01 not set per design | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-02 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI06986 | Verified | 1A-MSS-LIT-8003C not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-01 | MBS-01 | PI06987 | Verified | Line needs better support | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI06988 | Verified | 1A-MSS-LIT-8003B not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-01 | MBS-01 | PI06989 | Verified | 1A-MSS-LIT-8003A not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-01 | MBS-01 | PI06990 | Verified | 1A-MSS-PIT-8007A not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-01 | MBS-01 | PI06991 | Verified | 1A-MSS-PIT-8007B not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-01 | MBS-01 | PI06992 | Verified | 1A-MSS-PI-8006 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI06993 | Verified | 1A-MSS-PIT-8007C not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-01 | MBS-01 | PI06994 | Verified | 1A-MSS-LIT-8009C not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-01 | MBS-01 | PI06995 | Verified | 1A-MSS-LIT-8009B not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-01 | MBS-01 | PI06996 | Verified | 1A-MSS-LIT-8009A not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-01 | MBS-01 | PI06997 | Verified | Tag not installed on valve 1A-MSS-V-8065 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Alex Isaac | 2019-09-25 | Alex Isaac
MBS-01 | MBS-01 | PI06998 | Verified | 1A-MSS-TP-8116 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI06999 | Verified | 1A-MSS-TE-8112 not installed (TW COVERED BY INSULATION) | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2020-02-03 | James Tanner | 2020-02-06 | Kelvin Cook
MBS-01 | MBS-01 | PI07000 | Verified | Incorrect instrument installed at 1A-MSS-TP-8111 location | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07001 | Verified | 1A-MSS-TE-8107 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07002 | Verified | 1A-MSS-TP-8121 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07003 | Verified | Loose nuts on strut on support HPS31PS02 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-07 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07004 | Verified | Tag not installed on valve 1A-MSS-CHK-8134 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Alex Isaac | 2019-09-25 | Alex Isaac
MBS-01 | MBS-01 | PI07005 | Verified | Remove rigging at support HPS31PS05 | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-07 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07006 | Verified | 1A-MSS-TP-8122 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07007 | Verified | 1A-MSS-TP-8123 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07008 | Verified | 1A-MSS-TP-8124 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07009 | Verified | Tag not installed on valve 1A-MSS-V-8131 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Alex Isaac | 2019-09-25 | Alex Isaac
MBS-01 | MBS-01 | PI07010 | Verified | 1A-MSS-PIT-8129 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-01 | MBS-01 | PI07011 | Verified | Restore line to blowdown tank (AFTER degrease) | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-12-02 | Bobby Williams | 2019-12-12 | Shane Copeland
MBS-01 | MBS-01 | PI07012 | Verified | Remove hydro material from high point | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-06 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-01 | MBS-01 | PI07013 | Verified | Guides not installed on support HPS37PS01 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07014 | Verified | Guides not installed on support HPS38PS01 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07015 | Verified | Tag not installed on valve 1A-MSS-FV-8017 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Alex Isaac | 2019-09-25 | Alex Isaac
MBS-01 | MBS-01 | PI07016 | Verified | Guides not installed on support HPS41PS01 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07017 | Verified | Tag not installed on valve 1A-MSS-V-8128 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Alex Isaac | 2019-09-25 | Alex Isaac
MBS-01 | MBS-01 | PI07018 | Verified | Tag not installed on valve 1A-MSS-PV-8129 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Alex Isaac | 2019-09-25 | Alex Isaac
MBS-01 | MBS-01 | PI07019 | Verified | Complete field run drains | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-06 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-01 | MBS-01 | PI07021 | Verified | Loose nuts on support HPS43PS09 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07022 | Verified | Loose nuts on support HPS43PS10 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07023 | Verified | Support HPS43PS07 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07024 | Verified | Support HPS43PS08 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07025 | Verified | Tag not installed on valve 1A-FWS-AOV-8118 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Alex Isaac | 2019-09-25 | Alex Isaac
MBS-01 | MBS-01 | PI07026 | Verified | Support HPS43PS06 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07027 | Verified | 1A-FWS-FIT-8116 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-01 | MBS-01 | PI07028 | Verified | Line needs better support | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-07 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07029 | Verified | Tag not installed on 1A-MBL-TE-8115A | C | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-11-15 | James Tanner | 2019-11-18 | Alex Isaac
MBS-01 | MBS-01 | PI07030 | Verified | Restore line to blowdown tank (AFTER degrease) | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-12-12 | Shane Copeland | 2019-12-12 | Shane Copeland
MBS-01 | MBS-01 | PI07031 | Verified | Grout all supports. | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2020-01-01 | Kelvin Cook
MBS-01 | MBS-01 | PI07032 | Verified | Conduit unistrut support is clamped to pipe support (growth issue) - east side under HRSG. | A | E | Dustin Futrell | McD | 2019-09-24 | Dustin Futrell | Const |  |  | 2019-11-23 | Fred Michael
MBS-01 | MBS-01 | PI07033 | Verified | Loose nuts on HP01 support under 1A-FWS-TI-8004 - top of HRSG. | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-01 | MBS-01 | PI07034 | Verified | Housekeeping needed by all disciplines at top of HRSG. | B | C | Alan Huntsman | McD | 2019-09-24 | Alan Huntsman | Const | 2019-11-12 | Carlos Wallen | 2020-01-21 | Michael Law
MBS-01 | MBS-01 | PI09932 | Verified | 1AMBLC0004 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09933 | Verified | 1AMBLC0026 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09934 | Verified | 1AMBLX0016 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09935 | Verified | 1AMBSX0002 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI09936 | Verified | 1AMBSX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI09937 | Verified | 1AMBSX0004 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI09938 | Verified | 1AMBSX0005 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI09939 | Verified | 1AMBSX0009 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI09940 | Verified | 1AMBSX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI09941 | Verified | 1AMBSX0013 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI09942 | Verified | 1AMBSX0020 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI09943 | Verified | 1AMBSX0022 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI09944 | Verified | 1AMSSX0007 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI09945 | Verified | 1AMSSX0008 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI09946 | Verified | 1AMSSX0059 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI09947 | Verified | 1AMBLC0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09948 | Verified | 1AMBLC0026 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09949 | Verified | 1AMBLX0016 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09950 | Verified | 1AMBSX0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09951 | Verified | 1AMBSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09952 | Verified | 1AMBSX0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09953 | Verified | 1AMBSX0005 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09954 | Verified | 1AMBSX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09955 | Verified | 1AMBSX0009 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI09956 | Verified | 1AMBSX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI09957 | Verified | 1AMBSX0013 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09958 | Verified | 1AMBSX0020 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI09959 | Verified | 1AMBSX0022 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI09960 | Verified | 1AMSSX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09961 | Verified | 1AMSSX0008 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-10-25 | Mike Tabbert
MBS-01 | MBS-01 | PI09962 | Verified | 1AMSSX0059 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10279 | Verified | 1ACNMX0020 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10280 | Verified | 1ACNMX0021 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10281 | Verified | 1ACNMX0022 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10283 | Verified | 1ACRSX0010 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10285 | Verified | 1AFWSX0038 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10286 | Verified | 1AFWSX0039 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10287 | Verified | 1AFWSX0040 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10288 | Verified | 1AFWSX0041 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10289 | Verified | 1AFWSX0044 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10290 | Verified | 1AFWSX0045 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10291 | Verified | 1AFWSX0046 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10294 | Verified | 1AHRSX0001 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10371 | Verified | 1AMBLC0008 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10376 | Verified | 1AMBLX0010 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10377 | Verified | 1AMBSC0001 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10381 | Verified | 1AMBSX0006 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10382 | Verified | 1AMBSX0010 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-12-17 | James Beech | 2019-12-17 | Shane Copeland
MBS-01 | MBS-01 | PI10383 | Verified | 1AMBSX0012 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10386 | Verified | 1AMBSX0016 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10387 | Verified | 1AMBSX0017 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10388 | Verified | 1AMBSX0018 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10389 | Verified | 1AMBSX0019 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10390 | Verified | 1AMBSX0023 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10395 | Verified | 1AMSSX0005 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10396 | Verified | 1AMSSX0006 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10397 | Verified | 1AMSSX0016 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10398 | Verified | 1AMSSX0017 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10399 | Verified | 1AMSSX0018 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10400 | Verified | 1AMSSX0019 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10401 | Verified | 1AMSSX0020 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10405 | Verified | 1AMSSX0026 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10416 | Verified | 1AMSSX0052 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10417 | Verified | 1AMSSX0053 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10418 | Verified | 1AMSSX0054 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10419 | Verified | 1AMSSX0055 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10420 | Verified | 1AMSSX0056 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10865 | Verified | 1ACNMX0019 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-15 | Mike Tabbert | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10872 | Verified | 1AFWSX0038 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-15 | Mike Tabbert | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI10873 | Verified | 1AFWSX0039 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI10874 | Verified | 1AFWSX0040 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI10875 | Verified | 1AFWSX0041 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI10877 | Verified | 1AFWSX0045 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI10878 | Verified | 1AFWSX0046 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11009 | Verified | 1AMBSX0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11024 | Verified | 1AMSSX0005 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11026 | Verified | 1AMSSX0016 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11029 | Verified | 1AMSSX0019 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11030 | Verified | 1AMSSX0020 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11036 | Verified | 1AMSSX0032 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11037 | Verified | 1AMSSX0033 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11038 | Verified | 1AMSSX0034 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11039 | Verified | 1AMSSX0035 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11052 | Verified | 1AMSSX0054 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11499 | Verified | 1ACNMX0019 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11504 | Verified | 1ACRSX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11505 | Verified | 1ACRSX0010 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11507 | Verified | 1AFWSX0038 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11656 | Verified | 1AMBSX0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI11697 | Verified | 1AMSSX0052 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-01 | MBS-01 | PI12890 | Verified | 1A-MSS-MOV-8014 - pull control cable. | A | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-11-19 | Michael Law | 2020-01-21 | Michael Law
MBS-01 | MBS-01 | PI12891 | Verified | 1A-MSS-MOV-8014 - install condulet cover. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-11-24 | Brad Stanford | 2020-01-21 | Michael Law
MBS-01 | MBS-01 | PI12892 | Verified | Install kick plates at all needed penetrations on the HRSG. | C | S | Tim Gallegos | McD | 2019-11-13 | Tim Gallegos | Const | 2020-05-15 | Tim Gallegos | 2020-10-06 | Dave Goldak
MBS-01 | MBS-01 | PI12893 | Verified | Complete conduit to 1A-MSS-TE-8112. | A | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-20 | Mike Tabbert
MBS-01 | MBS-01 | PI12894 | Verified | Tag all instruments, use SS wiring. | C | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-11-15 | James Tanner | 2020-01-08 | Fred Michael
MBS-01 | MBS-01 | PI12895 | Verified | 1A-MSS-LE-8012 - run cable to LIY. | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const | 2019-11-19 | Dustin Futrell | 2019-11-19 | Fred Michael
MBS-01 | MBS-01 | PI12900 | Verified | 1A-MSS-CAB-0205 - run tubing for PITs. | A | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-11-15 | James Tanner | 2019-12-19 | Albert Burge
MBS-01 | MBS-01 | PI12901 | Verified | 1A-MBS-PDIT-8906 needs additional support. | C | I | James Beech | McD | 2019-11-13 | James Beech | Const | 2020-03-11 | Tim Green | 2020-04-06 | Bernard Stasse
MBS-01 | MBS-01 | PI12902 | Verified | Replace tube bundles ty-wrap with SS banding. | B | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-11-15 | James Tanner | 2020-01-30 | Fred Michael
MBS-01 | MBS-01 | PI12903 | Verified | 1A-MSS-PV-8129 - tube up IA. | A | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-11-15 | James Tanner | 2019-12-08 | Mike Tabbert
MBS-01 | MBS-01 | PI12904 | Cleared | All tube bundles at [HRSG 98' -0"] south mezz level need added support. | C | I | Tim Green | McD | 2019-11-13 | Tim Green | Const | 2020-06-02 | Tim Gallegos | 2021-08-02 | John Watts
MBS-01 | MBS-01 | PI12905 | Verified | Skin temps - 1A-MSS-TE-8100A, B, C, D, F, H - need support. | D | I | Michael Law | McD | 2019-11-13 | Michael Law | Const | 2020-01-29 | Michael Law | 2020-01-29 | Michael Law
MBS-01 | MBS-01 | PI12952 | Verified | 1ATK111014, 1ATK111012, 1ATK111013, 1ATK111031, 1ATK111032, Cable Tray, Dividers K, C & X not installed, dividers to be installed and cables to be layed in correct section | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-02 | Brad Stanford | 2019-12-14 | Mike Tabbert
MBS-01 | MBS-01 | PI12953 | Verified | 1ATK111014, 1ATK111012, 1ATK111013, 1ATK111031, 1ATK111032, Cable Tray, Cable Tray Hold Down Clamps not installed, cut off threaded rods so all consistent length. | B | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-23 | Fred Michael
MBS-01 | MBS-01 | PI12954 | Verified | 1ATK111014, 1ATK111012, 1ATK111013, 1ATK111031, 1ATK111032, Cable Tray, Cable Tray Labels not installed. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-02 | Brad Stanford | 2019-12-14 | Mike Tabbert
MBS-01 | MBS-01 | PI12955 | Verified | 1ATK111014, 1ATK111012, 1ATK111013, 1ATK111031, 1ATK111032, Cable Tray, Cable Tray grounding not installed. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-02 | Brad Stanford | 2019-12-14 | Mike Tabbert
MBS-01 | MBS-01 | PI12956 | Verified | 1ATK111014 Cable Tray, offset on east side requires more supports. | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-23 | Fred Michael
MBS-01 | MBS-01 | PI12957 | Verified | All Conduits with exposed threads that have not been Cold Galvanized needs to be done. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-02 | Brad Stanford | 2019-12-18 | Mike Tabbert
MBS-01 | MBS-01 | PI12958 | Verified | All conduits feeding from cable trays need covers on condulets. | C | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-18 | Mike Tabbert
MBS-01 | MBS-01 | PI12959 | Verified | 1ATK111014 Cable Tray, 90 degree elbow northeast corner requires more support. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-11-23 | Richard Cruz | 2019-12-14 | Mike Tabbert
MBS-01 | MBS-01 | PI12960 | Verified | 1ATK111013 Cable Tray, Offset on north side requres more support. | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-23 | Fred Michael
MBS-01 | MBS-01 | PI12961 | Verified | 1ATK111013 Cable Tray, 90 degree elbow north west corner requires more support. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-11-23 | Richard Cruz | 2019-12-14 | Mike Tabbert
MBS-01 | MBS-01 | PI12963 | Verified | 1AMBLC0004, From Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-01 | MBS-01 | PI12964 | Verified | 1AMBLX0016, From Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-01 | MBS-01 | PI12965 | Verified | 1AMBSX0018, From Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-01 | MBS-01 | PI12966 | Verified | 1AMSSX0003, From Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-01 | MBS-01 | PI12967 | Verified | 1AMSSX0026, From Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI12968 | Verified | 1AMSSX0056, From Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-01 | MBS-01 | PI12969 | Verified | 1AFWSX0039, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-01 | MBS-01 | PI12970 | Verified | 1AFWSX0044, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-01 | MBS-01 | PI12971 | Verified | 1AMBLX0016, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-01 | MBS-01 | PI12972 | Verified | 1AMBSX0007, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-01 | MBS-01 | PI12973 | Verified | 1AMBSX0014, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-01 | MBS-01 | PI12974 | Verified | 1AMBSX0015, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-01 | MBS-01 | PI12975 | Verified | 1AMBSX0016, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI12976 | Verified | 1AMBSX0017, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-01 | MBS-01 | PI12977 | Verified | 1AMBSX0018, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-01 | MBS-01 | PI12978 | Verified | 1AMBSX0019, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-01 | MBS-01 | PI12979 | Verified | 1AMSSX0003, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-01 | MBS-01 | PI12980 | Verified | 1AMSSX0016, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI12981 | Verified | 1AMSSX0018, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-15 | Mike Tabbert
MBS-01 | MBS-01 | PI12982 | Verified | 1AMSSX0054, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-01 | MBS-01 | PI12983 | Verified | 1AMSSX0055, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-01 | MBS-01 | PI12984 | Verified | 1AMSSX0056, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-01 | MBS-01 | PI13005 | Verified | 1A-MBL-TE-8115A, B, 8113A, B, 8110 - need tags. | C | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-12-31 | Gonzalo Pena | 2020-01-27 | Michael Law
MBS-01 | MBS-01 | PI13006 | Verified | 1A-MBL-TE-8115A, B, 8113A, B, 8110 - conduit covers missing. Ground floor under HRSG. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2020-01-27 | Michael Law
MBS-01 | MBS-01 | PI13191 | Verified | Install 1A-MSS-TE-8107. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const |  |  | 2019-12-03 | James Tanner
MBS-01 | MBS-01 | PI13192 | Verified | Install 1A-MSS-TE-8108. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const |  |  | 2019-12-03 | James Tanner
MBS-01 | MBS-01 | PI13193 | Verified | Install 1A-MSS-TE-8109. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const |  |  | 2019-12-03 | James Tanner
MBS-01 | MBS-01 | PI13194 | Verified | Install 1A-MSS-TE-8110. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const |  |  | 2019-12-03 | James Tanner
MBS-01 | MBS-01 | PI13195 | Verified | Install 1A-MSS-PV-8129. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const |  |  | 2019-12-03 | James Tanner
MBS-01 | MBS-01 | PI13546 | Verified | 1A-MSS-LE-8011 - cut/modify handrail for access. | A | S | Bobby Williams | McD | 2019-11-26 | Bobby Williams | Const | 2019-12-04 | Bobby Williams | 2019-12-09 | Albert Burge
MBS-01 | MBS-01 | PI13547 | Verified | 1A-MSS-LE-8012 - re-work conduit to allow access. | A | E | Chris Colvin | McD | 2019-11-26 | Chris Colvin | Const | 2019-12-12 | Chris Colvin | 2020-01-01 | Albert Burge
MBS-01 | MBS-01 | PI13549 | Verified | Valve 1A-MSS-MOV-8138 has water damage. Will have to be replaced. | A | P | Chris Boudreaux | McD | 2019-11-26 | Chris Boudreaux | Const | 2019-12-23 | Michael Law | 2020-01-16 | Michael Law
MBS-01 | MBS-01 | PI14358 | Verified | 1A-MSS-MOV-8137 actuator needs to be rotated 90 degrees to plant east. Once scaffold is taken down for first fire we will not be able to access the controls if needed during operations. | A | P | Bobby Williams | McD | 2019-12-05 | Bobby Williams | Const | 2019-12-07 | Michael Law | 2020-01-16 | Michael Law
MBS-01 | MBS-01 | PI14638 | Verified | 1A-MSS-LE-8011 - rework conduit to access level probe. | A | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Const | 2019-12-12 | Chris Colvin | 2019-12-12 | Albert Burge
MBS-01 | MBS-01 | PI14639 | Verified | Re-route three umbilicals that are in contact with 1A-MSS-LE-8011. | A | I | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Const | 2019-12-11 | James Tanner | 2019-12-13 | Albert Burge
MBS-01 | MBS-01 | PI14640 | Verified | Weld level transmitter tubing associated with the main steam water & steam drum. | A | I | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Const | 2019-12-13 | Gonzalo Pena | 2019-12-19 | Albert Burge
MBS-01 | MBS-01 | PI14864 | Verified | 1A-MSS-TE-8100C, Replace TE because of water Damage | A | I | Gonzalo Pena | McD | 2019-12-23 | Gonzalo Pena | Comm | 2020-01-29 | Gonzalo Pena | 2020-01-29 | Gonzalo Pena
MBS-01 | MBS-01 | PI15846 | Verified | Retube the HP Water Drum Level transmitters 1A-MSS-LIT-8003A. | A | I | Gonzalo Pena | McD | 2020-01-10 | Gonzalo Pena | Comm | 2020-02-10 | James Tanner | 2020-02-18 | Albert Burge
MBS-01 | MBS-01 | PI15847 | Verified | Retube the HP Water Drum Level transmitters 1A-MSS-LIT-8003B. | A | I | Gonzalo Pena | McD | 2020-01-10 | Gonzalo Pena | Comm | 2020-02-10 | James Tanner | 2020-02-18 | Albert Burge
MBS-01 | MBS-01 | PI15848 | Verified | Retube the HP Water Drum Level transmitters 1A-MSS-LIT-8003C. | A | I | Gonzalo Pena | McD | 2020-01-10 | Gonzalo Pena | Comm | 2020-02-10 | James Tanner | 2020-02-18 | Albert Burge
MBS-01 | MBS-01 | PI16040 | Verified | Install spray nozzles 1A-FWS-DESC-8100 | B | P | Bobby Williams | McD | 2020-01-14 | Bobby Williams | Const | 2020-01-16 | Bobby Williams | 2020-01-27 | Michael Law
MBS-01 | MBS-01 | PI17855 | Verified | 1A-MBL-TI-8126B 1A HP Superheater 2 Drain Temp reads -4,924 deg F and Bad Quality. | B | E | Albert Burge | McD | 2020-03-16 | Albert Burge | Comm | 2020-03-19 | Albert Burge | 2020-03-26 | Keith Pollock
MBS-01 | MBS-01 | PI18100 | Verified | 1A-MBB-PCV-8113, 1A-MBB-PI-8114 - At St. Charles, it was found after the systems had already been turned over to commissioning from construction that on the Vendor Supplied Duct Burner Skids for 1A, the stainless tubing line connecting PCV 8113 to the “T” fitting going to PI 8114 was never installed before being sent to the site. Tigon tubing was used at St. Charles on this issue for a temporary fix until they were able to run the stainless tubing. LCPS's duct burner skid has the same issue. | C | I | James Beech | McD | 2020-03-18 | James Beech | Comm | 2020-05-19 | Tim Green | 2020-06-04 | Tanner Hillman
MBS-01 | MBS-01 | PI18523 | Verified | 1A HRSG, approx Elev 578, east side: Damaged insulation on large diameter pipe downcomer from IP Drum to ground level. | C | X | Josh Koerner | PCI | 2020-06-09 | Josh Koerner | Const | 2020-06-19 | Jason Ezell | 2020-06-19 | Jason Ezell
MBS-01 | MBS-01 | PI18681 | Verified | Observed MBS-01 TE 8124B HP desuperheater drain thermocouple pipe union disconnected, thermocouple pulled out and bent, and ground wire not connected while performing walkdown of insulation. | C | P | Tim Green | McD | 2020-06-22 | Tim Green |  | 2020-07-10 | Mike Tabbert | 2020-07-24 | Nelson Eichelberger
MBS-02 | MBS-02 | PI04667 | Verified | Weld not made at connection to BOP piping | A | P | Bobby Williams | McD | 2019-08-29 | Bobby Williams | Const | 2019-10-02 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-02 | MBS-02 | PI04668 | Verified | Valve 1A-FWS-V-8215 missing stem indicator | C | P | Bobby Williams | McD | 2019-08-29 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-02 | MBS-02 | PI04669 | Verified | Valve 1A-FWS-LV-8207A needs restoration, no tag installed (RESTORE AFTER FLUSH) | A | P | Bobby Williams | McD | 2019-08-29 | Bobby Williams | Const | 2019-12-02 | Bobby Williams | 2019-12-06 | Shane Copeland
MBS-02 | MBS-02 | PI04670 | Verified | Valve 1A-FWS-V-8214 missing stem indicator | C | P | Bobby Williams | McD | 2019-08-29 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-02 | MBS-02 | PI04671 | Verified | Flow element not installed on 1A-FWS-FE-8207 | B | P | Bobby Williams | McD | 2019-08-29 | Bobby Williams | Const | 2019-12-04 | Bobby Williams | 2019-12-13 | Shane Copeland
MBS-02 | MBS-02 | PI04672 | Verified | Replace damaged flex hose on valve 1A-FWS-V-8212 | C | E | Chris Colvin | McD | 2019-08-29 | Chris Colvin | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
MBS-02 | MBS-02 | PI04673 | Verified | No tag installed on TE 1A-FWS-TE-8204 | C | I | Gonzalo Pena | McD | 2019-08-29 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Alex Isaac
MBS-02 | MBS-02 | PI04674 | Verified | 1A-FWS-TP-8203 not installed | A | I | Gonzalo Pena | McD | 2019-08-29 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Alex Isaac
MBS-02 | MBS-02 | PI04675 | Verified | 1A-FWS-PIT-8206 not installed | A | I | Gonzalo Pena | McD | 2019-08-29 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-02 | MBS-02 | PI04676 | Verified | 1A-FWS-FIT-8207 not installed | A | I | Gonzalo Pena | McD | 2019-08-29 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-02 | MBS-02 | PI04677 | Verified | 1A-IPS-LIT-8202C not installed | A | I | Gonzalo Pena | McD | 2019-08-29 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-02 | MBS-02 | PI04678 | Verified | 1A-IPS-LIT-8202B not installed | A | I | Gonzalo Pena | McD | 2019-08-29 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-02 | MBS-02 | PI04679 | Verified | 1A-IPS-LIT-8202A not installed | A | I | Gonzalo Pena | McD | 2019-08-29 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-02 | MBS-02 | PI04680 | Verified | 1A-IPS-PIT-8204A not installed | A | I | Gonzalo Pena | McD | 2019-08-29 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-02 | MBS-02 | PI04681 | Verified | No tag installed on valve 1A-IPS-V-8251 | C | P | Bobby Williams | McD | 2019-08-29 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-10-01 | Alex Isaac
MBS-02 | MBS-02 | PI04682 | Verified | 1A-IPS-PIT-8204B not installed | A | I | Gonzalo Pena | McD | 2019-08-29 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-02 | MBS-02 | PI04683 | Verified | 1A-IPS-PIT-8204C not installed | A | I | Gonzalo Pena | McD | 2019-08-29 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-02 | MBS-02 | PI04684 | Verified | Grout not installed on support IPS04APS02 | C | C | Johnny Campbell | McD | 2019-08-29 | Johnny Campbell | Const |  |  | 2019-12-06 | Jack Fields
MBS-02 | MBS-02 | PI04685 | Verified | Remove hydro material from high point | B | P | Bobby Williams | McD | 2019-08-29 | Bobby Williams | Const | 2019-09-19 | Bobby Williams | 2019-09-27 | Alex Isaac
MBS-02 | MBS-02 | PI04686 | Verified | No tag installed on TE 1A-IPS-TE-8302 | C | I | Gonzalo Pena | McD | 2019-08-29 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Alex Isaac
MBS-02 | MBS-02 | PI04687 | Verified | Install FE 1A-IPS-FE-8312 (INSTALL AFTER FLUSH) | B | P | Bobby Williams | McD | 2019-08-29 | Bobby Williams | Const | 2019-12-04 | Bobby Williams | 2019-12-13 | Shane Copeland
MBS-02 | MBS-02 | PI04688 | Verified | Valve 1A-IPS-PV-8303 needs restoration, (RESTORE AFTER Steam Blow) | A | P | Bobby Williams | McD | 2019-08-29 | Bobby Williams | Const | 2020-02-06 | Bobby Williams | 2020-02-06 | Kelvin Cook
MBS-02 | MBS-02 | PI04689 | Verified | 1A-IPS-PIT-8303 not installed | A | I | Gonzalo Pena | McD | 2019-08-29 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-02 | MBS-02 | PI04690 | Verified | INSTALL SPOOL IP-07-C-01 (AFTER IA-IPS-FE-8312 INSTALLATION) | B | P | Bobby Williams | McD | 2019-08-29 | Bobby Williams | Const | 2020-01-31 | Bobby Williams | 2020-01-31 | Kelvin Cook
MBS-02 | MBS-02 | PI04691 | Verified | Line not installed (INSTALL AFTER 1A-IPS-FE-8312 INSTALLATION) | B | P | Bobby Williams | McD | 2019-08-29 | Bobby Williams | Const | 2020-01-31 | Bobby Williams | 2020-01-31 | Kelvin Cook
MBS-02 | MBS-02 | PI04692 | Verified | Grout not installed on support IPS10PS01 | C | C | Johnny Campbell | McD | 2019-08-29 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-01 | Kelvin Cook
MBS-02 | MBS-02 | PI04693 | Verified | Grout not installed on support IPS11PS04 | C | C | Johnny Campbell | McD | 2019-08-29 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-01 | Kelvin Cook
MBS-02 | MBS-02 | PI04694 | Verified | Grout not installed on support IPS11PS05 | C | C | Johnny Campbell | McD | 2019-08-29 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-01 | Kelvin Cook
MBS-02 | MBS-02 | PI04695 | Verified | Restore line to blowdown tank (FILL POINT FOR HYDRO) | B | P | Bobby Williams | McD | 2019-08-29 | Bobby Williams | Const | 2019-12-02 | Bobby Williams | 2019-12-12 | Shane Copeland
MBS-02 | MBS-02 | PI04696 | Verified | Grout not installed on support IPS11PS02 | C | C | Johnny Campbell | McD | 2019-08-29 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-01 | Kelvin Cook
MBS-02 | MBS-02 | PI04697 | Verified | Loose/missing bolts at flange connection to 1A-FWS-SRV-8205 | A | P | Bobby Williams | McD | 2019-08-29 | Bobby Williams | Const | 2019-09-19 | Bobby Williams | 2019-09-27 | Alex Isaac
MBS-02 | MBS-02 | PI06544 | Verified | Tag all valves with proper tag numbers, (1A-). Currently tagged 1X-. | C | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-15 | Shannon Scott
MBS-02 | MBS-02 | PI06552 | Verified | Remove all plastic from piping (under HRSG). | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-11-06 | Bobby Williams | 2020-01-21 | Michael Law
MBS-02 | MBS-02 | PI06560 | Verified | Set all spring cans to cold settings. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-12-20 | Bobby Williams | 2020-01-27 | Michael Law
MBS-02 | MBS-02 | PI06579 | Verified | IP-101 - needs added support - south side of IP drum. | A | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Shannon Scott
MBS-02 | MBS-02 | PI06591 | Verified | 1A-FWS-TI-8201 - glass broken - northwest corner, top of HRSG. | B | I | Gonzalo Pena | McD | 2019-09-19 | Gonzalo Pena | Const | 2019-11-06 | Gonzalo Pena | 2019-11-13 | Shannon Scott
MBS-02 | MBS-02 | PI06601 | Verified | Rotate valve (head) on 1A-MBL-MOV-8305, insulation interference. | A | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-02 | MBS-02 | PI09963 | Verified | 1AFWSX0027 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09964 | Verified | 1AFWSX0028 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09965 | Verified | 1AFWSX0043 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09966 | Verified | 1AIPSC0004 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI09967 | Verified | 1AIPSX0006 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09968 | Verified | 1AIPSX0007 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09969 | Verified | 1AIPSX0008 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09970 | Verified | 1AIPSX0009 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09971 | Verified | 1AIPSX0010 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09972 | Verified | 1AIPSX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09973 | Verified | 1AIPSX0012 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09974 | Verified | 1AIPSX0013 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09975 | Verified | 1AIPSX0016 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09976 | Verified | 1AIPSX0017 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09977 | Verified | 1AMBLC0012 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI09978 | Verified | 1AMBLC0015 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI09979 | Verified | 1AMBLX0005 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI09980 | Verified | 1AFWSC0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09981 | Verified | 1AFWSX0027 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09982 | Verified | 1AFWSX0028 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09983 | Verified | 1AFWSX0043 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09984 | Verified | 1AIPSC0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09985 | Verified | 1AIPSX0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09986 | Verified | 1AIPSX0006 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09987 | Verified | 1AIPSX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09988 | Verified | 1AIPSX0008 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI09989 | Verified | 1AIPSX0009 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09990 | Verified | 1AIPSX0010 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09991 | Verified | 1AIPSX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09992 | Verified | 1AIPSX0012 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09993 | Verified | 1AIPSX0013 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09994 | Verified | 1AIPSX0016 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09995 | Verified | 1AIPSX0017 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09996 | Verified | 1AMBLC0012 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09997 | Verified | 1AMBLC0015 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI09998 | Verified | 1AMBLX0005 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI09999 | Verified | 1AMBLX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI10000 | Verified | 1AMBLX0020 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-02 | MBS-02 | PI10894 | Verified | 1AIPSX0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI11000 | Verified | 1AMBLK0011 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI11001 | Verified | 1AMBLK0012 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI11002 | Verified | 1AMBLK0015 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI11644 | Verified | 1AMBLC0025 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI12134 | Verified | 1AFWSX0043 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI12145 | Verified | 1AIPSX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI12285 | Verified | 1AIPSX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI12286 | Verified | 1AIPSX0012 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-02 | MBS-02 | PI12906 | Verified | 1A-MBS-JB-8003 - clean panel. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-11-24 | Brad Stanford | 2019-12-08 | Mike Tabbert
MBS-02 | MBS-02 | PI12907 | Verified | 1A-MBS-JB-8003 - label panel. | C | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-11-24 | Brad Stanford | 2019-12-08 | Mike Tabbert
MBS-02 | MBS-02 | PI12908 | Verified | 1A-MBS-JB-8003 - heat shrink cable tags. | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const | 2019-11-15 | Dustin Futrell | 2019-11-19 | Shannon Scott
MBS-02 | MBS-02 | PI12909 | Verified | Tag all instruments, use SS wiring. | C | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const |  |  | 2019-12-14 | Fred Michael
MBS-02 | MBS-02 | PI12910 | Verified | 1A-IPS-TE-8201A - tubing bent. | A | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-11-15 | James Tanner | 2019-12-19 | Albert Burge
MBS-02 | MBS-02 | PI12911 | Verified | 1A-IPS-TE-8203 - replace cap chain. | C | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2020-01-03 | Gonzalo Pena | 2020-02-17 | Shannon Scott
MBS-02 | MBS-02 | PI12912 | Verified | Remove excess tube bundles. | B | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-12-03 | James Tanner | 2019-12-13 | Mike Tabbert
MBS-02 | MBS-02 | PI12913 | Verified | 1A-IPS-TI-8301 - out of range. | B | I | Billy Williams | McD | 2019-11-13 | Billy Williams | Const | 2019-11-19 | James Tanner | 2019-12-19 | Albert Burge
MBS-02 | MBS-02 | PI12914 | Verified | 1A-IPS-PIT-8303 - tie in tubing. | A | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-11-16 | Gonzalo Pena | 2019-12-19 | Albert Burge
MBS-02 | MBS-02 | PI12915 | Verified | 1A-IPS-TE-8200A & B missing condulet covers. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-18 | Mike Tabbert
MBS-02 | MBS-02 | PI12916 | Verified | Seal tubing penetrations on IP drum. | C | Q | Richard McSpadden | PCI | 2019-11-13 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
MBS-02 | MBS-02 | PI12917 | Verified | 1A-HTS-CAB-0104 - tighten flex. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-02 | Brad Stanford | 2019-12-15 | Shannon Scott
MBS-02 | MBS-02 | PI12918 | Verified | 1A-LPS-LIY- 8208 - label. | C | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2020-04-28 | Matt Gilmore | 2020-04-29 | Mike Tabbert
MBS-02 | MBS-02 | PI12919 | Verified | 1A-LPS-LIY- 8208 - clean. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-18 | Mike Tabbert
MBS-02 | MBS-02 | PI12920 | Verified | 1A-LPS-LIY- 8208 - missing condulet covers. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-18 | Mike Tabbert
MBS-02 | MBS-02 | PI12921 | Verified | 1A-LPS-LIY- 8208 - conduit needs support within 30" of box. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-18 | Mike Tabbert
MBS-02 | MBS-02 | PI12922 | Verified | 1A-LPS-LIY- 8208 - replace printed circuit board with new one. | B | E | Mike Tabbert | McD | 2019-11-13 | Mike Tabbert | Const |  |  | 2019-11-19 | Mike Tabbert
MBS-02 | MBS-02 | PI12923 | Verified | Replace tube bundles ty-wrap with SS banding. | D | I | Michael Law | McD | 2019-11-13 | Michael Law | Const | 2020-07-20 | Jason Ezell | 2021-07-22 | John Watts
MBS-02 | MBS-02 | PI12992 | Verified | 1AFWSX0027, From Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-02 | MBS-02 | PI12993 | Verified | 1AFWSX0028 , From Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-02 | MBS-02 | PI12994 | Verified | 1AIPSX0013, From Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-02 | MBS-02 | PI12995 | Verified | 1AMBLC0011, From Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-02 | MBS-02 | PI12996 | Verified | 1AFWSX0027, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-02 | MBS-02 | PI12997 | Verified | 1AFWSX0028, To Termination | A | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Brad Stanford | 2019-12-07 | Mike Tabbert
MBS-02 | MBS-02 | PI12998 | Verified | 1AIPSX0001, To Termination | A | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const |  |  | 2020-02-07 | Mike Tabbert
MBS-02 | MBS-02 | PI12999 | Verified | 1AIPSX0013, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-02 | MBS-02 | PI13000 | Verified | 1AMBLK0011, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-02 | MBS-02 | PI13001 | Verified | 1AMBLX0020, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-14 | Fred Michael
MBS-02 | MBS-02 | PI13384 | Verified | 1A-MSS-FV-8017 missing wiring. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-12 | John Sullivan | 2019-12-19 | Albert Burge
MBS-02 | MBS-02 | PI13548 | Verified | Valve 1A-MBL-MOV-8257 needs to be rotated and flex reworked as it is right up against the pipe. | A | P | Bobby Williams | McD | 2019-11-26 | Bobby Williams | Const | 2020-02-02 | Bobby Williams | 2020-03-09 | Michael Law
MBS-02 | MBS-02 | PI18101 | Verified | 1B-MBB-PCV-8113, 1B-MBB-PI-8114 - At St. Charles, it was found after the systems had already been turned over to commissioning from construction that on the Vendor Supplied Duct Burner Skids for 1B, the stainless tubing line connecting PCV 8113 to the “T” fitting going to PI 8114 was never installed before being sent to the site. Tigon tubing was used at St. Charles on this issue for a temporary fix until they were able to run the stainless tubing. LCPS's duct burner skid has the same issue. | C | I | James Beech | McD | 2020-03-18 | James Beech | Comm | 2020-05-19 | Tim Green | 2020-06-04 | Tanner Hillman
MBS-02 | MBS-02 | PI18524 | Verified | Pipe hanger strut disconnected from structure | C | P | Tim Green | McD | 2020-06-10 | Tim Green |  | 2020-06-15 | Tim Green | 2020-07-24 | Nelson Eichelberger
MBS-03 | MBS-03 | PI06545 | Verified | Tag all valves with proper tag numbers, (1A-). Currently tagged 1X-. | C | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-15 | Shannon Scott
MBS-03 | MBS-03 | PI06553 | Verified | Remove all plastic from piping (under HRSG). | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-11-06 | Bobby Williams | 2020-01-21 | Michael Law
MBS-03 | MBS-03 | PI06561 | Verified | Set all spring cans to cold settings. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-12-23 | Bobby Williams | 2020-01-27 | Michael Law
MBS-03 | MBS-03 | PI06586 | Verified | Spread cotter pins on LP-14 support - south of LP drum. | A | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-10-02 | Bobby Williams | 2020-01-21 | Michael Law
MBS-03 | MBS-03 | PI06602 | Verified | Add support on line LP-13-E. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-10-07 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-03 | MBS-03 | PI07061 | Verified | Tag not installed on TE 1A-CNM-TE-8503A | C | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-10-07 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-03 | MBS-03 | PI07062 | Verified | Support LPS01PS02 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-08 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-03 | MBS-03 | PI07063 | Verified | PIT 1A-CNM-PIT-8504 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-03 | MBS-03 | PI07064 | Verified | TP 1A-CNM-TP-8508 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const |  |  | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07065 | Verified | Tag not installed on valve 1A-CNM-V-8508 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-10-01 | Alex Isaac
MBS-03 | MBS-03 | PI07066 | Verified | Shoe not welded to support per detail on support LPS03PS01 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-03 | MBS-03 | PI07067 | Verified | TE 1A-CNM-TE-8510 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const |  |  | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07068 | Verified | Rotate spectacle blind to closed position for chemical clean | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07069 | Verified | Tag not installed on valve 1A-CNM-V-8511 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-10-01 | Alex Isaac
MBS-03 | MBS-03 | PI07070 | Verified | TP 1A-CNM-TP-8511 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const |  |  | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07071 | Verified | Tag not installed on TE 1A-CNM-TE-8512B | C | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-28 | Bobby Williams | 2019-10-01 | Alex Isaac
MBS-03 | MBS-03 | PI07072 | Verified | Tag not installed on valve 1A-CNM-V-8512 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-07 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-03 | MBS-03 | PI07073 | Verified | Restore valve 1A-CNM-LV-8500A (AFTER CHEMICAL CLEAN) | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-12-02 | Bobby Williams | 2019-12-06 | Shane Copeland
MBS-03 | MBS-03 | PI07074 | Verified | Tag not installed on valve 1A-CNM-V-8524 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-10-01 | Alex Isaac
MBS-03 | MBS-03 | PI07075 | Verified | Tag not installed on TE 1A-CNM-TE-8517B | C | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-28 | Bobby Williams | 2019-10-01 | Alex Isaac
MBS-03 | MBS-03 | PI07076 | Verified | TE 1A-CNM-TE-8517A not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const |  |  | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07077 | Verified | TP 1A-CNM-TP-8516 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const |  |  | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07078 | Verified | Tag not installed on TE 1A-CNM-TE-8515 | C | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-28 | Bobby Williams | 2019-10-01 | Alex Isaac
MBS-03 | MBS-03 | PI07079 | Verified | TP 1A-CNM-TP-8514 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const |  |  | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07080 | Verified | Remove temporary support (ROPE) at elevation +100'-2.1/2" | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-03 | MBS-03 | PI07081 | Verified | LIT 1A-LPS-LIT-8602C not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-03 | MBS-03 | PI07082 | Verified | LIT 1A-LPS-LIT-8602B not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-03 | MBS-03 | PI07083 | Verified | LIT 1A-LPS-LIT-8602A not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-03 | MBS-03 | PI07084 | Verified | PIT 1A-LPS-PIT-8604A not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-03 | MBS-03 | PI07085 | Verified | PIT 1A-LPS-PIT-8604B not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-03 | MBS-03 | PI07086 | Verified | PI 1A-LPS-PI-8603 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-09 | Alex Isaac
MBS-03 | MBS-03 | PI07087 | Verified | PIT 1A-LPS-PIT-8604C not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-03 | MBS-03 | PI07088 | Verified | Tag not installed on valve 1A-MBL-MOV-8705 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-10-01 | Alex Isaac
MBS-03 | MBS-03 | PI07089 | Verified | TP 1A-LPS-TP-8703 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const |  |  | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07090 | Verified | Tag not installed on TE 1A-LPS-TE-8704 | C | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-12-31 | Gonzalo Pena | 2020-01-01 | Kelvin Cook
MBS-03 | MBS-03 | PI07091 | Verified | TP 1A-LPS-TP-8701 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const |  |  | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07092 | Verified | Loose clamp on support LPS14PS02 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07093 | Verified | Support LPS14PS05 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07094 | Verified | PIT 1A-LPS-PIT-8708 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const |  |  | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07095 | Verified | Remove hydro material from high point | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07096 | Verified | Grout not installed on support LPS15PS01 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-11-12 | Johnny Campbell | 2019-11-13 | Alex Isaac
MBS-03 | MBS-03 | PI07097 | Verified | Grout not installed on support LPS16PS01 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-11-12 | Johnny Campbell | 2019-11-13 | Alex Isaac
MBS-03 | MBS-03 | PI07098 | Verified | Grout not installed on support LPS17PS01 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-11-12 | Johnny Campbell | 2019-11-13 | Alex Isaac
MBS-03 | MBS-03 | PI07099 | Verified | Grout not installed on support LPS18PS05 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-11-12 | Johnny Campbell | 2019-11-13 | Alex Isaac
MBS-03 | MBS-03 | PI07100 | Verified | Grout not installed on support LPS18PS06 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-11-12 | Johnny Campbell | 2019-11-13 | Alex Isaac
MBS-03 | MBS-03 | PI07101 | Verified | Restore piping to blowdown tank (AFTER FLUSH) | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-12-02 | Bobby Williams | 2019-12-12 | Shane Copeland
MBS-03 | MBS-03 | PI07102 | Verified | Grout not installed on support LPS18PS01 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-11-12 | Johnny Campbell | 2019-11-13 | Alex Isaac
MBS-03 | MBS-03 | PI07103 | Verified | Grout not installed on support LPS18PS02 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-11-12 | Johnny Campbell | 2019-11-13 | Alex Isaac
MBS-03 | MBS-03 | PI07104 | Verified | Grout not installed on support LPS18PS03 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-11-12 | Johnny Campbell | 2019-11-13 | Alex Isaac
MBS-03 | MBS-03 | PI07105 | Verified | Guides not installed on support LPS20PS01 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07106 | Verified | Guides not installed on support LPS21PS01 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07107 | Verified | Guides not installed on support LPS22PS01 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07108 | Verified | Complete field run drains on top of HRSG 1A | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-02 | Bobby Williams | 2019-11-06 | Alex Isaac
MBS-03 | MBS-03 | PI07109 | Verified | Loose bolts at flange connection on valve 1A-CNM-TV-8506 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-11-16 | Alex Isaac
MBS-03 | MBS-03 | PI07110 | Verified | Loose/missing bolts, no gasket, at SRV 1A-CNM-SRV-8518 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-03 | MBS-03 | PI07111 | Verified | 1A-CRS-TE-8400 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-16 | Alex Isaac
MBS-03 | MBS-03 | PI07112 | Verified | Complete field run drains | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-26 | Alex Isaac | 2019-09-26 | Alex Isaac
MBS-03 | MBS-03 | PI07113 | Verified | 1A-HRS-TP-8416 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-16 | Alex Isaac
MBS-03 | MBS-03 | PI07114 | Verified | 1A-CRS-TE-8412 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-16 | Alex Isaac
MBS-03 | MBS-03 | PI07115 | Verified | 1A-CRS-TP-8411 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-16 | Alex Isaac
MBS-03 | MBS-03 | PI07116 | Verified | 1A-CRS-TE-8407 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-16 | Alex Isaac
MBS-03 | MBS-03 | PI07117 | Verified | 1A-CRS-TE-8408 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-16 | Alex Isaac
MBS-03 | MBS-03 | PI07118 | Verified | 1A-CRS-TE-8409 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-16 | Alex Isaac
MBS-03 | MBS-03 | PI07119 | Verified | 1A-CRS-TE-8410 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-16 | Alex Isaac
MBS-03 | MBS-03 | PI07120 | Verified | 1A-HRS-TP-8424 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-16 | Alex Isaac
MBS-03 | MBS-03 | PI07121 | Verified | 1A-HRS-TP-8423 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-16 | Alex Isaac
MBS-03 | MBS-03 | PI07122 | Verified | 1A-HRS-TP-8421 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-16 | Alex Isaac
MBS-03 | MBS-03 | PI07123 | Verified | 1A-HRS-TP-8422 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-16 | Alex Isaac
MBS-03 | MBS-03 | PI07124 | Verified | 1A-HRS-PIT-8428 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-03 | MBS-03 | PI07125 | Verified | Tag not installed on valve 1A-HRS-V-8430 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Alex Isaac | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07126 | Verified | Tag not installed on valve 1A-HRS-V-8432 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Alex Isaac | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07127 | Verified | Guides not installed on support RPS04PS01 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07128 | Verified | Guides not installed on support RPS05PS01 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07129 | Verified | Tag not installed on valve 1A-HRS-V-8427 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Alex Isaac | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07130 | Verified | Support RPS07PS01 not installed per detail | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07131 | Verified | Support RPS101PS01 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07132 | Verified | Support RPS101PS02 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07133 | Verified | Remove rigging from riser (UNDER PENETRATION) | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07134 | Verified | Restore valve 1A-FWS-TV-8418 (AFTER degrease) | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-12-02 | Bobby Williams | 2019-12-06 | Shane Copeland
MBS-03 | MBS-03 | PI07135 | Verified | Tag not installed on valve 1A-FWS-V-8417 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Alex Isaac | 2019-09-25 | Alex Isaac
MBS-03 | MBS-03 | PI07136 | Verified | Restore line to blowdown tank (AFTER degrease) | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-12-02 | Bobby Williams | 2019-12-12 | Shane Copeland
MBS-03 | MBS-03 | PI10001 | Verified | 1AMBLK0020 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-03 | MBS-03 | PI10002 | Verified | 1AMBLC0020 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-03 | MBS-03 | PI10003 | Verified | 1AMBLK0019 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-03 | MBS-03 | PI10004 | Verified | 1AMBLK0020 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-03 | MBS-03 | PI10261 | Verified | 1ACNMC0001 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10262 | Verified | 1ACNMX0002 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10263 | Verified | 1ACNMX0003 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10264 | Verified | 1ACNMX0004 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10265 | Verified | 1ACNMX0005 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10266 | Verified | 1ACNMX0006 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10267 | Verified | 1ACNMX0007 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10268 | Verified | 1ACNMX0008 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10269 | Verified | 1ACNMX0009 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10270 | Verified | 1ACNMX0010 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10271 | Verified | 1ACNMX0011 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10272 | Verified | 1ACNMX0012 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10273 | Verified | 1ACNMX0013 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10274 | Verified | 1ACNMX0014 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10275 | Verified | 1ACNMX0015 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10276 | Verified | 1ACNMX0016 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10277 | Verified | 1ACNMX0017 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10278 | Verified | 1ACNMX0018 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10306 | Verified | 1ALPSC0003 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10315 | Verified | 1ALPSC0018 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10318 | Verified | 1ALPSK0003 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10321 | Verified | 1ALPSK0006 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10328 | Verified | 1ALPSX0007 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10329 | Verified | 1ALPSX0008 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10330 | Verified | 1ALPSX0009 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10331 | Verified | 1ALPSX0010 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10332 | Verified | 1ALPSX0011 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10333 | Verified | 1ALPSX0012 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10334 | Verified | 1ALPSX0013 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10335 | Verified | 1ALPSX0014 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10336 | Verified | 1ALPSX0015 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10337 | Verified | 1ALPSX0016 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10338 | Verified | 1ALPSX0017 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10339 | Verified | 1ALPSX0018 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10340 | Verified | 1ALPSX0019 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10341 | Verified | 1ALPSX0020 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10342 | Verified | 1ALPSX0021 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10344 | Verified | 1ALPSX0029 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10372 | Verified | 1AMBLC0024 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10848 | Verified | 1ACNMX0002 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10849 | Verified | 1ACNMX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10850 | Verified | 1ACNMX0004 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10851 | Verified | 1ACNMX0005 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10852 | Verified | 1ACNMX0006 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10853 | Verified | 1ACNMX0007 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10854 | Verified | 1ACNMX0008 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10855 | Verified | 1ACNMX0009 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10856 | Verified | 1ACNMX0010 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10857 | Verified | 1ACNMX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10858 | Verified | 1ACNMX0012 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10859 | Verified | 1ACNMX0013 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10860 | Verified | 1ACNMX0014 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10861 | Verified | 1ACNMX0015 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10862 | Verified | 1ACNMX0016 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10863 | Verified | 1ACNMX0017 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10920 | Verified | 1ALPSX0007 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10921 | Verified | 1ALPSX0008 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10924 | Verified | 1ALPSX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10925 | Verified | 1ALPSX0012 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10926 | Verified | 1ALPSX0013 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10928 | Verified | 1ALPSX0015 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10929 | Verified | 1ALPSX0016 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10930 | Verified | 1ALPSX0017 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10932 | Verified | 1ALPSX0019 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10933 | Verified | 1ALPSX0020 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI10934 | Verified | 1ALPSX0021 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11484 | Verified | 1ACNMX0004 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11485 | Verified | 1ACNMX0005 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11486 | Verified | 1ACNMX0006 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11487 | Verified | 1ACNMX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11491 | Verified | 1ACNMX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11492 | Verified | 1ACNMX0012 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11493 | Verified | 1ACNMX0013 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11494 | Verified | 1ACNMX0014 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11495 | Verified | 1ACNMX0015 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11496 | Verified | 1ACNMX0016 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11497 | Verified | 1ACNMX0017 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11558 | Verified | 1ALPSX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11559 | Verified | 1ALPSX0008 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11562 | Verified | 1ALPSX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11568 | Verified | 1ALPSX0017 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11569 | Verified | 1ALPSX0018 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI11570 | Verified | 1ALPSX0019 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
MBS-03 | MBS-03 | PI12924 | Verified | Tag all instruments, use SS wiring. | C | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-12-14 | James Tanner | 2019-12-14 | Fred Michael
MBS-03 | MBS-03 | PI12925 | Verified | Move 1A-HTS-CAB-0108. | A | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const |  |  | 2019-11-15 | Gonzalo Pena
MBS-03 | MBS-03 | PI12926 | Verified | Add support for 1A-LPS-LG-8605. | B | P | Bobby Williams | McD | 2019-11-13 | Bobby Williams | Const | 2020-02-11 | Bobby Williams | 2020-02-17 | Shannon Scott
MBS-03 | MBS-03 | PI12927 | Verified | 1A-LPS-LG-8605 - rotate 90 deg. | B | P | Bobby Williams | McD | 2019-11-13 | Bobby Williams | Const | 2020-01-15 | Bobby Williams | 2020-02-17 | Shannon Scott
MBS-03 | MBS-03 | PI12928 | Verified | Tighten 1A-CNM-TE-8517A. | A | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-11-15 | James Tanner | 2019-11-19 | Shannon Scott
MBS-03 | MBS-03 | PI12929 | Verified | Tighten flex on 1A-CNM-TE-8503B. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-02 | Brad Stanford | 2019-12-15 | Shannon Scott
MBS-03 | MBS-03 | PI12930 | Verified | 1A-CNM-TV-8506 - nipple on regulator bent. | A | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-11-15 | James Tanner | 2019-11-19 | Shannon Scott
MBS-03 | MBS-03 | PI12931 | Verified | Install 1A-CNM-PIT-8504 and run tubing. | A | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-11-15 | James Tanner | 2019-12-17 | John Sullivan
MBS-03 | MBS-03 | PI12932 | Verified | 1A-LPS-LIY- 8608 - label. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-11-24 | Brad Stanford | 2019-12-08 | Mike Tabbert
MBS-03 | MBS-03 | PI12933 | Verified | 1A-LPS-LIY- 8608 - clean. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-11-24 | Brad Stanford | 2019-12-08 | Mike Tabbert
MBS-03 | MBS-03 | PI12934 | Verified | 1A-LPS-LIY- 8609 - missing condulet covers. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-18 | Mike Tabbert
MBS-03 | MBS-03 | PI12935 | Verified | 1A-LPS-LIY- 8609 - conduit needs support within 30" of box. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-18 | Mike Tabbert
MBS-03 | MBS-03 | PI12936 | Verified | 1A-LPS-LIY- 8609 - replace printed circuit board with new one. | B | E | Mike Tabbert | McD | 2019-11-13 | Mike Tabbert | Const |  |  | 2019-12-09 | Mike Tabbert
MBS-03 | MBS-03 | PI12937 | Verified | Missing condulet covers under grating - north side of LP drum. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-18 | Mike Tabbert
MBS-03 | MBS-03 | PI12938 | Verified | 1A-CNM-TV-8507 - conduit needs support. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-15 | Shannon Scott
MBS-03 | MBS-03 | PI12939 | Verified | 1A-CNM-TV-8505 - conduit needs support. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-15 | Shannon Scott
MBS-03 | MBS-03 | PI12940 | Verified | 1A-HTS-CAB-0203 - support cabinet & tube bundles. | C | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2020-03-09 | Tim Green | 2020-04-06 | Bernard Stasse
MBS-03 | MBS-03 | PI12941 | Verified | 1A-HTS-CAB-0203 - tighten flex. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-12-07 | Mark Ball | 2019-12-15 | Shannon Scott
MBS-03 | MBS-03 | PI12942 | Verified | Replace tube bundles ty-wrap with SS banding. | D | I | Michael Law | McD | 2019-11-13 | Michael Law | Const | 2020-02-27 | Fred Michael | 2020-04-07 | Bernard Stasse
MBS-03 | MBS-03 | PI12943 | Verified | 1A-LPS-LY-8208 - replace rusted bolt on back with SS bolt. | B | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-18 | Mike Tabbert
MBS-03 | MBS-03 | PI12944 | Verified | 1A-LPS-LY-8208 - add support. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const |  |  | 2019-12-20 | Mike Tabbert
MBS-03 | MBS-03 | PI13002 | Verified | 1ALPSK0006, From Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
MBS-03 | MBS-03 | PI13003 | Verified | 1ACNMX0002, To Termination | A | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const |  |  | 2019-12-04 | Mike Tabbert
MBS-03 | MBS-03 | PI13004 | Verified | 1ALPSK0006, To Termination | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const | 2019-11-15 | Dustin Futrell | 2019-11-15 | Mike Tabbert
MBS-03 | MBS-03 | PI14682 | Verified | 1ALPSC0003, To Termination | A | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-20 | Mike Tabbert
MBS-03 | MBS-03 | PI14683 | Verified | 1ALPSK0003, To Termination | A | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-20 | Mike Tabbert
MBS-03 | MBS-03 | PI16042 | Verified | Install spray nozzles 1A-FWS-DESC-8401 | B | P | Bobby Williams | McD | 2020-01-14 | Bobby Williams | Const | 2020-01-16 | Bobby Williams | 2020-01-27 | Michael Law
MBS-03 | MBS-03 | PI17839 | Verified | The LP drum bypass is running much more open on A than B. It may still be clogged. | C | M | William Mitchell | McD | 2020-03-16 | William Mitchell | Const | 2020-03-31 | William Mitchell | 2020-06-03 | Chase Courtade
MBS-04 | MBS-04 | PI02798 | Verified | 10DCSX0101, Terminate Cable | A | E | Sheri Fritz | ITS | 2019-07-25 | Sheri Fritz | Const | 2019-08-01 | Mike Tabbert | 2019-08-01 | Mike Tabbert
MBS-04 | MBS-04 | PI04660 | Verified | Complete tubing to all AOV's on the Gas Fired Duct Burner (20 PLACES). | A | I | Gonzalo Pena | McD | 2019-08-27 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-12 | Alex Isaac
MBS-04 | MBS-04 | PI04661 | Verified | 1A-MBS-PIT-8902A not installed. | A | I | Gonzalo Pena | McD | 2019-08-27 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-04 | MBS-04 | PI04662 | Verified | 1A-MBS-PIT-8902B not installed. | A | I | Gonzalo Pena | McD | 2019-08-27 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-04 | MBS-04 | PI04663 | Verified | 1A-MBS-PIT-8902C not installed. | A | I | Gonzalo Pena | McD | 2019-08-27 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-04 | MBS-04 | PI04664 | Verified | Grout not installed on support BPS04PS01. | C | C | Johnny Campbell | McD | 2019-08-27 | Johnny Campbell | Const |  |  | 2019-11-05 | Alex Isaac
MBS-04 | MBS-04 | PI06546 | Verified | Tag all valves with proper tag numbers, (1A-). Currently tagged 1X-. | C | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-10-07 | Bobby Williams | 2019-10-15 | Shannon Scott
MBS-04 | MBS-04 | PI06554 | Verified | Remove all plastic from piping (under HRSG). | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-11-06 | Bobby Williams | 2020-01-27 | Michael Law
MBS-04 | MBS-04 | PI06562 | Verified | Set all spring cans to cold settings. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-11-16 | Bobby Williams | 2020-01-27 | Michael Law
MBS-04 | MBS-04 | PI06588 | Verified | Clean up trash on level 4 (all levels). | A | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Shannon Scott
MBS-04 | MBS-04 | PI06589 | Verified | Valves 8140 (on all levels) - handle hits toe plate. | A | S | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-10-03 | Shannon Scott
MBS-04 | MBS-04 | PI06590 | Verified | Valve missing rubber handle cover - level 5. | C | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-10-07 | Bobby Williams | 2019-10-09 | Shannon Scott
MBS-04 | MBS-04 | PI06592 | Verified | Trim mid-rail for valve operation - level 2. | A | S | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Shannon Scott
MBS-04 | MBS-04 | PI06593 | Verified | Handle missing on burner view port - level 2. | B | M | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-11-16 | Bobby Williams | 2019-11-19 | Shannon Scott
MBS-04 | MBS-04 | PI06594 | Verified | Trim top handrail for valve operation - level 1. | A | S | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Shannon Scott
MBS-04 | MBS-04 | PI06595 | Verified | FE-8136 installed backwards - level 1. | A | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-28 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-04 | MBS-04 | PI06596 | Verified | Loose u-bolt on northwest corner of duct burner skid. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-09 | Shannon Scott
MBS-04 | MBS-04 | PI06597 | Verified | Remove shipping material - south end of duct burner skid. | A | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-10-08 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-04 | MBS-04 | PI06598 | Verified | Replace plug to GUAT on blower skid. | B | E | Dustin Futrell | McD | 2019-09-19 | Dustin Futrell | Const | 2019-09-27 | Fred Michael | 2019-09-27 | Fred Michael
MBS-04 | MBS-04 | PI06599 | Verified | Install permanent tags on all components on the blower skid. | C | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2020-02-24 | Bobby Williams | 2020-04-06 | Bernard Stasse
MBS-04 | MBS-04 | PI06600 | Verified | Need housekeeping on the blower skid. | B | M | Shane Crowe | McD | 2019-09-19 | Shane Crowe | Const | 2019-09-27 | Shane Crowe | 2020-01-27 | Michael Law
MBS-04 | MBS-04 | PI10006 | Verified | 1AMBBC0002 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10007 | Verified | 1AMBBC0003 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10008 | Verified | 1AMBBC0004 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10009 | Verified | 1AMBBC0080 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10010 | Verified | 1AMBBK0019 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10011 | Verified | 1AMBBK0020 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10012 | Verified | 1AMBBK0021 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10013 | Verified | 1AMBBK0022 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10014 | Verified | 1AMBBK0023 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10015 | Verified | 1AMBBK0024 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10042 | Verified | 1AMBBC0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10043 | Verified | 1AMBBC0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10044 | Verified | 1AMBBC0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10045 | Verified | 1AMBBC0080 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10046 | Verified | 1AMBBK0019 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10047 | Verified | 1AMBBK0020 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10048 | Verified | 1AMBBK0021 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10049 | Verified | 1AMBBK0022 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10050 | Verified | 1AMBBK0023 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10051 | Verified | 1AMBBK0024 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-04 | MBS-04 | PI10346 | Verified | 1AMBBC0001 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10347 | Verified | 1AMBBC0008 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10348 | Verified | 1AMBBC0081 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10349 | Verified | 1AMBBC0082 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10350 | Verified | 1AMBBC0083 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10351 | Verified | 1AMBBC0084 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10352 | Verified | 1AMBBK0001 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10353 | Verified | 1AMBBK0002 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10354 | Verified | 1AMBBK0003 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10355 | Verified | 1AMBBK0004 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10356 | Verified | 1AMBBK0005 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10357 | Verified | 1AMBBK0006 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10358 | Verified | 1AMBBK0007 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10359 | Verified | 1AMBBK0008 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10360 | Verified | 1AMBBK0009 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10361 | Verified | 1AMBBK0010 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10362 | Verified | 1AMBBK0011 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10363 | Verified | 1AMBBK0012 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10364 | Verified | 1AMBBK0013 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10365 | Verified | 1AMBBX0001 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10366 | Verified | 1AMBBX0002 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10367 | Verified | 1AMBBX0003 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10368 | Verified | 1AMBBX0004 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10369 | Verified | 1AMBBX0011 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10370 | Verified | 1AMBBX0012 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10938 | Verified | 1AMBBC0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10939 | Verified | 1AMBBC0008 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10940 | Verified | 1AMBBC0009 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10941 | Verified | 1AMBBC0010 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10942 | Verified | 1AMBBC0011 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10943 | Verified | 1AMBBC0012 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10944 | Verified | 1AMBBC0013 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10945 | Verified | 1AMBBC0014 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10946 | Verified | 1AMBBC0015 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10947 | Verified | 1AMBBC0016 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10948 | Verified | 1AMBBC0017 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10949 | Verified | 1AMBBC0018 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10950 | Verified | 1AMBBC0019 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10951 | Verified | 1AMBBC0020 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10952 | Verified | 1AMBBC0021 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10953 | Verified | 1AMBBC0022 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10954 | Verified | 1AMBBC0023 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10955 | Verified | 1AMBBC0024 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10956 | Verified | 1AMBBC0025 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10957 | Verified | 1AMBBC0026 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10958 | Verified | 1AMBBC0027 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10959 | Verified | 1AMBBC0028 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10960 | Verified | 1AMBBC0029 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10961 | Verified | 1AMBBC0030 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10962 | Verified | 1AMBBC0031 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10963 | Verified | 1AMBBC0032 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10964 | Verified | 1AMBBC0033 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10965 | Verified | 1AMBBC0034 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10966 | Verified | 1AMBBC0035 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10967 | Verified | 1AMBBC0036 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10968 | Verified | 1AMBBC0037 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10969 | Verified | 1AMBBC0038 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10970 | Verified | 1AMBBC0081 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10971 | Verified | 1AMBBC0084 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10972 | Verified | 1AMBBK0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10973 | Verified | 1AMBBK0002 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10974 | Verified | 1AMBBK0003 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10975 | Verified | 1AMBBK0004 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10976 | Verified | 1AMBBK0005 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10977 | Verified | 1AMBBK0006 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10978 | Verified | 1AMBBK0007 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10979 | Verified | 1AMBBK0008 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10980 | Verified | 1AMBBK0009 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10981 | Verified | 1AMBBK0010 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10982 | Verified | 1AMBBK0011 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10983 | Verified | 1AMBBK0012 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10984 | Verified | 1AMBBK0013 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10985 | Verified | 1AMBBK0015 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10986 | Verified | 1AMBBK0016 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10987 | Verified | 1AMBBK0017 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10988 | Verified | 1AMBBK0018 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10989 | Verified | 1AMBBX0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10990 | Verified | 1AMBBX0002 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10991 | Verified | 1AMBBX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10992 | Verified | 1AMBBX0004 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10993 | Verified | 1AMBBX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI10994 | Verified | 1AMBBX0012 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11576 | Verified | 1AMBBC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11577 | Verified | 1AMBBC0008 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11578 | Verified | 1AMBBC0009 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11579 | Verified | 1AMBBC0010 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11580 | Verified | 1AMBBC0011 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11581 | Verified | 1AMBBC0012 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11582 | Verified | 1AMBBC0013 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11583 | Verified | 1AMBBC0014 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11584 | Verified | 1AMBBC0015 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11585 | Verified | 1AMBBC0016 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11586 | Verified | 1AMBBC0017 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11587 | Verified | 1AMBBC0018 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11588 | Verified | 1AMBBC0019 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11589 | Verified | 1AMBBC0020 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11590 | Verified | 1AMBBC0021 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11591 | Verified | 1AMBBC0022 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11592 | Verified | 1AMBBC0023 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11593 | Verified | 1AMBBC0024 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11594 | Verified | 1AMBBC0025 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11595 | Verified | 1AMBBC0026 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11596 | Verified | 1AMBBC0027 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11597 | Verified | 1AMBBC0028 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11598 | Verified | 1AMBBC0029 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11599 | Verified | 1AMBBC0030 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11600 | Verified | 1AMBBC0031 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11601 | Verified | 1AMBBC0032 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11602 | Verified | 1AMBBC0033 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11603 | Verified | 1AMBBC0034 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11604 | Verified | 1AMBBC0035 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11605 | Verified | 1AMBBC0036 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11606 | Verified | 1AMBBC0037 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11607 | Verified | 1AMBBC0038 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11608 | Verified | 1AMBBC0081 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11609 | Verified | 1AMBBC0082 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11610 | Verified | 1AMBBC0083 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11611 | Verified | 1AMBBC0084 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11612 | Verified | 1AMBBK0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11613 | Verified | 1AMBBK0002 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11614 | Verified | 1AMBBK0003 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11615 | Verified | 1AMBBK0004 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11616 | Verified | 1AMBBK0005 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11617 | Verified | 1AMBBK0006 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11618 | Verified | 1AMBBK0007 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11619 | Verified | 1AMBBK0008 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11620 | Verified | 1AMBBK0009 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11621 | Verified | 1AMBBK0010 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11622 | Verified | 1AMBBK0011 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11623 | Verified | 1AMBBK0012 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11624 | Verified | 1AMBBK0013 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11625 | Verified | 1AMBBK0015 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11626 | Verified | 1AMBBK0016 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11627 | Verified | 1AMBBK0017 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11628 | Verified | 1AMBBK0018 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11629 | Verified | 1AMBBX0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11630 | Verified | 1AMBBX0002 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-01 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11631 | Verified | 1AMBBX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11632 | Verified | 1AMBBX0004 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11633 | Verified | 1AMBBX0005 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11634 | Verified | 1AMBBX0006 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11635 | Verified | 1AMBBX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11636 | Verified | 1AMBBX0008 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11637 | Verified | 1AMBBX0009 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11638 | Verified | 1AMBBX0010 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11639 | Verified | 1AMBBX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI11640 | Verified | 1AMBBX0012 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI12290 | Verified | 1AMBBK0019 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI12291 | Verified | 1AMBBK0020 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI12292 | Verified | 1AMBBK0021 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-08 | Mike Tabbert
MBS-04 | MBS-04 | PI12293 | Verified | 1AMBBK0022 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-04 | MBS-04 | PI12294 | Verified | 1AMBBK0023 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-04 | MBS-04 | PI12295 | Verified | 1AMBBK0024 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-14 | Mike Tabbert
MBS-04 | MBS-04 | PI12719 | Verified | Seal off conduits at the duct burner panel. | B | E | Chris Colvin | McD | 2019-11-04 | Chris Colvin | Const |  |  | 2020-02-10 | Fred Michael
MBS-04 | MBS-04 | PI12720 | Verified | Cold galv nipples at the duct burner panel. | C | E | Chris Colvin | McD | 2019-11-04 | Chris Colvin | Const | 2019-11-15 | Brad Stanford | 2019-12-18 | Mike Tabbert
MBS-04 | MBS-04 | PI12721 | Verified | Double nut u-bolts on pipe supports on the duct burner skid. | C | P | Bobby Williams | McD | 2019-11-04 | Bobby Williams | Const | 2020-01-09 | Bobby Williams | 2020-02-25 | Randy Carpenter
MBS-04 | MBS-04 | PI12722 | Verified | Repair grating on the duct burner skid at the panel. | C | S | Tim Gallegos | McD | 2019-11-04 | Tim Gallegos | Const | 2020-05-15 | Tim Gallegos | 2020-05-19 | Mike Tabbert
MBS-04 | MBS-04 | PI12723 | Verified | Redo the 2" conduit support on the duct burner skid. | D | E | Dustin Futrell | McD | 2019-11-04 | Dustin Futrell | Const | 2019-11-15 | Brad Stanford | 2019-11-21 | Randy Carpenter
MBS-04 | MBS-04 | PI12724 | Verified | 2" conduit on the duct burner skid needs low point drain. | D | E | Dustin Futrell | McD | 2019-11-04 | Dustin Futrell | Const | 2019-11-15 | Brad Stanford | 2019-11-21 | Randy Carpenter
MBS-04 | MBS-04 | PI12725 | Verified | Missing condulet covers on the duct burner skid and under the skid grating (front & back). | B | E | Dustin Futrell | McD | 2019-11-04 | Dustin Futrell | Const | 2019-11-15 | Brad Stanford | 2019-12-01 | Fred Michael
MBS-04 | MBS-04 | PI12726 | Verified | Tubing for 1A-MBB-PCV-8113 needs support on the duct burner skid. | B | I | Gonzalo Pena | McD | 2019-11-04 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-11-21 | Albert Burge
MBS-04 | MBS-04 | PI12727 | Verified | Duct burner skid panel 1A-MBB-CP-8100 - needs cleaning inside. | A | E | Dustin Futrell | McD | 2019-11-04 | Dustin Futrell | Const |  |  | 2019-11-14 | Mike Tabbert
MBS-04 | MBS-04 | PI12728 | Verified | Duct burner skid panel 1A-MBB-CP-8100 - has rusty hardware inside. | A | E | Dustin Futrell | McD | 2019-11-04 | Dustin Futrell | Const | 2019-11-13 | Brad Stanford | 2019-11-15 | Mike Tabbert
MBS-04 | MBS-04 | PI12729 | Verified | Duct burner skid panel 1A-MBB-CP-8100 - install panduit covers. | A | E | Dustin Futrell | McD | 2019-11-04 | Dustin Futrell | Const | 2019-11-13 | Brad Stanford | 2019-11-15 | Mike Tabbert
MBS-04 | MBS-04 | PI12730 | Verified | Duct burner skid panel 1A-MBB-CP-8100 - seal conduits. | B | E | Chris Colvin | McD | 2019-11-04 | Chris Colvin | Const | 2019-11-13 | Brad Stanford | 2019-12-18 | Mike Tabbert
MBS-04 | MBS-04 | PI12731 | Verified | Duct burner skid panel 1A-MBB-CP-8100 - label terminal blocks. | A | E | Dustin Futrell | McD | 2019-11-04 | Dustin Futrell | Const | 2019-11-13 | Brad Stanford | 2019-11-21 | Albert Burge
MBS-04 | MBS-04 | PI12732 | Verified | 1A-MBB-PIT-8112 missing plug on the duct burner skid. | A | I | Gonzalo Pena | McD | 2019-11-04 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-11-21 | Albert Burge
MBS-04 | MBS-04 | PI12733 | Verified | 1A-MBB-PIT-has 2 sets of wires on the duct burner skid. | A | E | Dustin Futrell | McD | 2019-11-04 | Dustin Futrell | Const | 2019-11-13 | Brad Stanford | 2019-11-21 | Albert Burge
MBS-04 | MBS-04 | PI12734 | Verified | 1A-MBB-PIT-8112 - clean cover threads on the duct burner skid. | A | I | Gonzalo Pena | McD | 2019-11-04 | Gonzalo Pena | Const |  |  | 2019-12-07 | Michael Law
MBS-04 | MBS-04 | PI12735 | Verified | Label the cable tray for the duct burner skid. | C | E | Dustin Futrell | McD | 2019-11-04 | Dustin Futrell | Const | 2019-11-15 | Brad Stanford | 2019-12-01 | Fred Michael
MBS-04 | MBS-04 | PI12736 | Verified | Ground the cable tray at the duct burner skid. | A | E | Dustin Futrell | McD | 2019-11-04 | Dustin Futrell | Const | 2019-11-11 | Brad Stanford | 2019-11-15 | Mike Tabbert
MBS-04 | MBS-04 | PI12737 | Verified | Label panel 1A-MBB-CP-8100 on the duct burner skid. | C | E | Chris Colvin | McD | 2019-11-04 | Chris Colvin | Const | 2019-11-13 | Brad Stanford | 2019-12-08 | Mike Tabbert
MBS-04 | MBS-04 | PI12738 | Verified | Install all fire eyes - all levels. | A | I | Gonzalo Pena | McD | 2019-11-04 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2019-11-21 | Albert Burge
MBS-04 | MBS-04 | PI12739 | Verified | Complete fire eye terminations after installed. | A | E | Dustin Futrell | McD | 2019-11-04 | Dustin Futrell | Const | 2019-11-13 | Brad Stanford | 2019-11-15 | Mike Tabbert
MBS-04 | MBS-04 | PI12740 | Verified | Cold galv all nipples for fire eys & ignitors. | B | E | Chris Colvin | McD | 2019-11-04 | Chris Colvin | Const | 2019-11-15 | Brad Stanford | 2019-12-18 | Mike Tabbert
MBS-04 | MBS-04 | PI12741 | Verified | Add cable tray support above vertical 90 deg. - first level. | B | E | Chris Colvin | McD | 2019-11-04 | Chris Colvin | Const | 2019-11-15 | Brad Stanford | 2019-12-18 | Mike Tabbert
MBS-04 | MBS-04 | PI12742 | Verified | Clean out 1A-MBB-JB-8002F. | B | E | Chris Colvin | McD | 2019-11-04 | Chris Colvin | Const | 2019-11-15 | Brad Stanford | 2019-12-08 | Mike Tabbert
MBS-04 | MBS-04 | PI12743 | Verified | Modify hand rail on duct burner platforms H&G, K&J and A&B. | B | S | Bobby Williams | McD | 2019-11-04 | Bobby Williams | Const | 2019-11-16 | Bobby Williams | 2019-12-18 | Mike Tabbert
MBS-04 | MBS-04 | PI12744 | Verified | Solenoid missing plate & red hat (10 each) K&J. | B | I | Gonzalo Pena | McD | 2019-11-04 | Gonzalo Pena | Const | 2019-11-19 | James Tanner | 2019-12-01 | Fred Michael
MBS-04 | MBS-04 | PI12745 | Verified | Handle missing from valve 1A-MBB-PI-8132 on the cooling air blower skie. | B | I | Gonzalo Pena | McD | 2019-11-04 | Gonzalo Pena | Const | 2019-11-14 | Gonzalo Pena | 2019-12-01 | Fred Michael
MBS-04 | MBS-04 | PI12746 | Verified | Covers need installed at cooling air blower skid. | B | E | Dustin Futrell | McD | 2019-11-04 | Dustin Futrell | Const | 2019-11-15 | Brad Stanford | 2019-12-01 | Fred Michael
MBS-04 | MBS-04 | PI13134 | Verified | Complete gas duct burner gas pipe pressure test. | A | P | Bobby Williams | McD | 2019-11-18 | Bobby Williams | Const | 2019-11-20 | Michael Law | 2019-11-20 | Michael Law
MBS-04 | MBS-04 | PI13136 | Verified | Complete skin TE installation. | A | I | Gonzalo Pena | McD | 2019-11-18 | Gonzalo Pena | Const | 2019-11-20 | Gonzalo Pena | 2019-11-20 | Michael Law
MBS-04 | MBS-04 | PI14523 | Verified | Install Catalyst | B | P | Bobby Williams | McD | 2019-12-07 | Bobby Williams | Const | 2020-02-10 | Bobby Williams | 2020-03-03 | Michael Law
MBS-04 | MBS-04 | PI17677 | Verified | 1A HRSG Seals - Bellows pipe penetration seals still have OEM plugs installed in the drain / vent. | B | P | Bobby Williams | McD | 2020-03-04 | Bobby Williams | Comm | 2020-03-09 | Bobby Williams | 2020-04-30 | John Watts
MBS-05 | MBS-05 | PI06547 | Verified | Tag all valves with proper tag numbers, (1B-). Currently tagged 1X-. | C | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-15 | Shannon Scott
MBS-05 | MBS-05 | PI06555 | Verified | Remove all plastic from piping (under HRSG). | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-11-06 | Bobby Williams | 2020-01-21 | Michael Law
MBS-05 | MBS-05 | PI06563 | Verified | Set all spring cans to cold settings. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-12-23 | Bobby Williams | 2020-01-27 | Michael Law
MBS-05 | MBS-05 | PI06963 | Verified | Grout all supports. | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2020-01-09 | Kelvin Cook
MBS-05 | MBS-05 | PI06964 | Verified | 1B-MBL-TE-8423A - flex not adequate for growth. Under HRSG. | A | E | Dustin Futrell | McD | 2019-09-24 | Dustin Futrell | Const |  |  | 2019-11-19 | Alex Isaac
MBS-05 | MBS-05 | PI06965 | Verified | 1B-MBL-LSL-8109 - flex not adequate for growth. Under HRSG. | A | E | Chris Colvin | McD | 2019-09-24 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-15 | Shannon Scott
MBS-05 | MBS-05 | PI06966 | Verified | Line at 1B-MBL-LSL-8109 needs added support. Under HRSG. | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-05 | MBS-05 | PI06967 | Verified | Hanger for line HP-19A is up against line above it. Under HRSG. | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-10-03 | Shannon Scott
MBS-05 | MBS-05 | PI06968 | Verified | Support HPS20-APS03 needs added welding. Under HRSG. | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-05 | MBS-05 | PI06969 | Verified | Hanger 19A-PS03 - tighten bottom nut. Under HRSG. | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-30 | Bobby Williams | 2019-10-03 | Shannon Scott
MBS-05 | MBS-05 | PI06970 | Verified | Open flange on bottom of HRSG - west side. | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2020-01-21 | Michael Law
MBS-05 | MBS-05 | PI06971 | Verified | Incomplete support at HP-40 at the IP drum. | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-05 | MBS-05 | PI06972 | Verified | Complete all trim piping supports on the HP drum. | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-17 | Alex Isaac
MBS-05 | MBS-05 | PI06973 | Verified | 1B-FWS-V-8005 - handwheel missing. Top of HRSG. | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-05 | MBS-05 | PI06974 | Verified | Remove dunnage at 1B-MSS-CHK-8134. South end HRSG mezz. Level. | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-01 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-05 | MBS-05 | PI06975 | Verified | Housekeeping need by all disciplines at top of HRSG. | B | C | Alan Huntsman | McD | 2019-09-24 | Alan Huntsman | Const | 2019-11-12 | Carlos Wallen | 2020-01-21 | Michael Law
MBS-05 | MBS-05 | PI07058 | Verified | Bellows not plumb. Under HRSG. | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-10-17 | Alex Isaac
MBS-05 | MBS-05 | PI08139 | Verified | Restore valve 1B-FWS-LV-8002A (AFTER Chemical Clean) | A | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-12-05 | Bobby Williams | 2019-12-06 | Shane Copeland
MBS-05 | MBS-05 | PI08140 | Verified | Support HPS01PS02 not installed | A | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-10-01 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-05 | MBS-05 | PI08141 | Verified | Restore valve 1B-FWS-LV-8002B (AFTER Chemical Clean) | A | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-12-05 | Bobby Williams | 2019-12-06 | Shane Copeland
MBS-05 | MBS-05 | PI08142 | Verified | 1B-FWS-TP-8010 not installed | A | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2019-11-18 | Alex Isaac
MBS-05 | MBS-05 | PI08143 | Verified | Line needs better support | B | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-11-06 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-05 | MBS-05 | PI08144 | Verified | 1B-FWS-TP-8012 not installed | A | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2019-11-18 | Alex Isaac
MBS-05 | MBS-05 | PI08145 | Verified | Tag not installed on valve 1B-MSS-V-8023 | C | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-12-07 | Bobby Williams | 2020-01-09 | Kelvin Cook
MBS-05 | MBS-05 | PI08146 | Verified | Line needs better support | B | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-05 | MBS-05 | PI08147 | Verified | 1B-MSS-PI-8006 not installed | A | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2019-11-18 | Alex Isaac
MBS-05 | MBS-05 | PI08148 | Verified | Tag not installed on valve 1B-MSS-V-8107 | C | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-17 | Alex Isaac
MBS-05 | MBS-05 | PI08149 | Verified | Tag not installed on valve 1B-MSS-V-8065 | C | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-17 | Alex Isaac
MBS-05 | MBS-05 | PI08150 | Verified | 1B-MSS-TP-8116 not installed | A | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2019-11-18 | Alex Isaac
MBS-05 | MBS-05 | PI08151 | Verified | 1B-MSS-TP-8111 not installed | A | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2019-11-18 | Alex Isaac
MBS-05 | MBS-05 | PI08152 | Verified | 1B-MSS-TE-8107 not installed | B | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const |  |  | 2019-11-21 | Ed Gober
MBS-05 | MBS-05 | PI08153 | Verified | 1B-MSS-TE-8108 not installed | B | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const |  |  | 2019-11-21 | Ed Gober
MBS-05 | MBS-05 | PI08154 | Verified | 1B-MSS-TE-8109 not installed | B | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const |  |  | 2019-11-21 | Ed Gober
MBS-05 | MBS-05 | PI08155 | Verified | 1B-MSS-TE-8110 not installed | B | I | Gonzalo Pena | McD | 2019-09-30 | Gonzalo Pena | Const |  |  | 2019-11-21 | Ed Gober
MBS-05 | MBS-05 | PI08156 | Verified | 1B-MSS-TP-8121 not installed | B | I | James Beech | McD | 2019-09-30 | James Beech | Const | 2020-02-03 | Bobby Williams | 2020-02-03 | Kelvin Cook
MBS-05 | MBS-05 | PI08157 | Verified | Complete all field run drains | A | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-12-03 | Bobby Williams | 2019-12-04 | Shane Copeland
MBS-05 | MBS-05 | PI08158 | Verified | Tag not installed on valve 1B-MSS-CHK-8134 | C | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-17 | Alex Isaac
MBS-05 | MBS-05 | PI08159 | Verified | Remove rigging at support HPS31PS05 | B | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-10-07 | Bobby Williams | 2019-10-09 | Alex Isaac
MBS-05 | MBS-05 | PI08160 | Verified | 1B-MSS-TP-8122 not installed | B | I | James Beech | McD | 2019-09-30 | James Beech | Const | 2020-02-03 | Bobby Williams | 2020-02-03 | Kelvin Cook
MBS-05 | MBS-05 | PI08161 | Verified | 1B-MSS-TP-8123 not installed | B | I | James Beech | McD | 2019-09-30 | James Beech | Const | 2020-02-03 | Bobby Williams | 2020-02-03 | Kelvin Cook
MBS-05 | MBS-05 | PI08162 | Verified | 1B-MSS-TP-8124 not installed | B | I | James Beech | McD | 2019-09-30 | James Beech | Const | 2020-02-03 | Bobby Williams | 2020-02-03 | Kelvin Cook
MBS-05 | MBS-05 | PI08163 | Verified | Restore line to blowdown tank (AFTER degrease) | B | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-12-05 | Bobby Williams | 2019-12-12 | Shane Copeland
MBS-05 | MBS-05 | PI08164 | Verified | Tag not installed on valve 1B-MSS-V-8128 | C | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-17 | Alex Isaac
MBS-05 | MBS-05 | PI08165 | Verified | Tag not installed on valve 1B-MSS-PV-8129 | C | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-17 | Alex Isaac
MBS-05 | MBS-05 | PI08167 | Verified | Tag not installed on valve 1B-MBL-V-8114 | C | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-17 | Alex Isaac
MBS-05 | MBS-05 | PI08168 | Verified | Tag not installed on valve 1B-MBL-V-8125 | C | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-10-10 | Bobby Williams | 2019-10-17 | Alex Isaac
MBS-05 | MBS-05 | PI08169 | Verified | Restore line to blowdown tank (AFTER degrease) | B | P | Bobby Williams | McD | 2019-09-30 | Bobby Williams | Const | 2019-12-05 | Bobby Williams | 2019-12-12 | Shane Copeland
MBS-05 | MBS-05 | PI10032 | Verified | 1BMBLC0008 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10033 | Verified | 1BMBLK0004 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10034 | Verified | 1BMBLK0008 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10039 | Verified | 1BMSSK0004 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10040 | Verified | 1BMSSK0005 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10041 | Verified | 1BMSSK0006 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10071 | Verified | 1BMBLC0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10072 | Verified | 1BMBLC0008 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10073 | Verified | 1BMBLC0009 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10079 | Verified | 1BMBLK0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10080 | Verified | 1BMBLK0006 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10081 | Verified | 1BMBLK0008 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10082 | Verified | 1BMBLK0009 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10088 | Verified | 1BMSSC0015 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10089 | Verified | 1BMSSC0017 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10090 | Verified | 1BMSSK0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10091 | Verified | 1BMSSK0005 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10092 | Verified | 1BMSSK0006 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10093 | Verified | 1BMSSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI10094 | Verified | 1BMSSX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-05 | MBS-05 | PI13196 | Verified | Install 1B-MSS-PIT-8129. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const |  |  | 2019-12-03 | James Tanner
MBS-05 | MBS-05 | PI13197 | Verified | Install 1B-MSS-TE-8107. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const | 2020-02-10 | James Tanner | 2020-03-03 | Michael Law
MBS-05 | MBS-05 | PI13198 | Verified | Install 1B-MSS-TE-8108. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const |  |  | 2019-12-03 | James Tanner
MBS-05 | MBS-05 | PI13199 | Verified | Install 1B-MSS-TE-8109. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const |  |  | 2019-12-03 | James Tanner
MBS-05 | MBS-05 | PI13200 | Verified | Install 1B-MSS-TE-8110. | A | I | Gonzalo Pena | McD | 2019-11-20 | Gonzalo Pena | Const |  |  | 2019-12-03 | James Tanner
MBS-05 | MBS-05 | PI13264 | Verified | Clean outside of all instrument cabinets and inside if needed. | C | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2020-02-13 | James Tanner | 2020-02-17 | Shannon Scott
MBS-05 | MBS-05 | PI13265 | Verified | Heat shrink all boots. | B | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const |  |  | 2019-12-14 | Fred Michael
MBS-05 | MBS-05 | PI13266 | Verified | Tighten all flex. | B | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-01 | Fred Michael | 2019-12-09 | Albert Burge
MBS-05 | MBS-05 | PI13267 | Verified | Install kick plates at all grating penetrations. | C | S | Tim Gallegos | McD | 2019-11-22 | Tim Gallegos | Const | 2020-05-15 | Tim Gallegos | 2020-07-10 | Dave Goldak
MBS-05 | MBS-05 | PI13268 | Verified | Tag all drum level junction boxes. | C | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2020-04-28 | Matt Gilmore | 2020-04-29 | Mike Tabbert
MBS-05 | MBS-05 | PI13309 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, Cable Tray, Vertical tray at southeast corner needs hold down clamps, finish divider. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-01 | Brad Stanford | 2019-12-07 | Mike Tabbert
MBS-05 | MBS-05 | PI13310 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, Vertical tray at southeast corner needs grounding complete. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-01 | Brad Stanford | 2019-12-07 | Mike Tabbert
MBS-05 | MBS-05 | PI13311 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, Vertical tray at southeast needs cable tray lables. | B | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-01 | Brad Stanford | 2019-12-18 | Mike Tabbert
MBS-05 | MBS-05 | PI13312 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, All horizontal tray at top of HRSG needs grounding complete. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-01 | Brad Stanford | 2019-12-07 | Mike Tabbert
MBS-05 | MBS-05 | PI13313 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, All horizontal tray at top of HRSG needs divider complete. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-01 | Brad Stanford | 2019-12-07 | Mike Tabbert
MBS-05 | MBS-05 | PI13314 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, All horizontal tray at top of HRSG needs lables complete. | B | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-01 | Brad Stanford | 2019-12-07 | Mike Tabbert
MBS-05 | MBS-05 | PI13315 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, All horizontal tray at top of HRSG needs hold down clamps complete, all threaded rod cut off to a consistent length. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-12-08 | Mike Tabbert
MBS-05 | MBS-05 | PI13316 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, Cable Tray needs support at offset east side. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-01 | Brad Stanford | 2019-12-07 | Mike Tabbert
MBS-05 | MBS-05 | PI13317 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, Cable Tray needs support north side of vertical offset east side. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-07 | Mike Tabbert
MBS-05 | MBS-05 | PI13318 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, Cable tray needs support horizontal offset that transitions under catwalk east side, cables are also going over top of divder and must be fixed. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-01 | Brad Stanford | 2019-12-08 | Mike Tabbert
MBS-05 | MBS-05 | PI13319 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, Cable tray needs three supports at horizontal 90 degree elbow northwest corner. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-26 | Brad Stanford | 2019-12-07 | Mike Tabbert
MBS-05 | MBS-05 | PI13320 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, Cable Tray needs support horizontal offset north side. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-07 | Mike Tabbert
MBS-05 | MBS-05 | PI13321 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, Cable Tray needs support 90 degree horizontal elbow northwest corner. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-07 | Mike Tabbert
MBS-05 | MBS-05 | PI13322 | Verified | 1BTK121051, 1BTK121031, 1BTK121033, 1BTK121014, 1BTK121102, Cable Tray, tie trays together west side below 1B-NJSPNL-0003. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-08 | Mike Tabbert
MBS-05 | MBS-05 | PI13398 | Verified | 1B-MBS-JB-8003 - label termination blocks. | B | E | Chris Colvin | McD | 2019-11-23 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-09 | Albert Burge
MBS-05 | MBS-05 | PI13399 | Verified | 1B-MBS-JB-8004 - label termination blocks. | B | E | Chris Colvin | McD | 2019-11-23 | Chris Colvin | Const | 2020-03-10 | Chris Colvin | 2020-03-16 | Albert Burge
MBS-05 | MBS-05 | PI13400 | Verified | 1B-MSS-LIT-8009A, B, C - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-23 | Gonzalo Pena | Const | 2019-12-21 | Gonzalo Pena | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI13401 | Verified | 1B-MSS-LIT-8009A, B, C - complete instrument enclosure installation. | A | I | Gonzalo Pena | McD | 2019-11-23 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI13402 | Verified | 1B-FWS-TE-8005 missing tag. | C | I | Gonzalo Pena | McD | 2019-11-23 | Gonzalo Pena | Const | 2020-01-03 | Gonzalo Pena | 2020-01-15 | Albert Burge
MBS-05 | MBS-05 | PI13403 | Verified | 1B-MSS-PIT-8007A & B - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-23 | Gonzalo Pena | Const | 2019-11-26 | Gonzalo Pena | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI13404 | Verified | 1B-MSS-LE-8011 - cut/modify handrail for access. | A | S | Bobby Williams | McD | 2019-11-23 | Bobby Williams | Const | 2019-12-03 | Bobby Williams | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI13405 | Verified | 1B-MSS-LE-8011 - run conduit. | A | E | Chris Colvin | McD | 2019-11-23 | Chris Colvin | Const | 2019-11-26 | Brad Stanford | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI13406 | Verified | 1B-MSS-LIY-8011 - check wires / shields. | A | E | Chris Colvin | McD | 2019-11-23 | Chris Colvin | Const | 2019-11-26 | Brad Stanford | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI13407 | Verified | 1B-MSS-LIY-8011 - clean panel | A | E | Chris Colvin | McD | 2019-11-23 | Chris Colvin | Const | 2019-11-26 | Brad Stanford | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI13408 | Verified | 1B-MSS-LIY-8011 - missing label. | C | E | Chris Colvin | McD | 2019-11-23 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-16 | Albert Burge
MBS-05 | MBS-05 | PI13409 | Verified | 1B-MSS-TE-8004A - flex too short. | A | E | Chris Colvin | McD | 2019-11-23 | Chris Colvin | Const | 2019-11-26 | Brad Stanford | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI13410 | Verified | 1B-MSS-TE-8004B - flex too short. | A | E | Chris Colvin | McD | 2019-11-23 | Chris Colvin | Const | 2019-11-26 | Brad Stanford | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI13411 | Verified | 1B-MSS-TE-8005A - flex too short. | A | E | Chris Colvin | McD | 2019-11-23 | Chris Colvin | Const | 2019-11-26 | Brad Stanford | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI13412 | Verified | 1B-MSS-TE-8005B - flex too short. | A | E | Chris Colvin | McD | 2019-11-23 | Chris Colvin | Const | 2019-11-26 | Brad Stanford | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI13413 | Verified | 1B-MSS-TE-8004A missing tag. | C | I | Gonzalo Pena | McD | 2019-11-23 | Gonzalo Pena | Const | 2020-01-03 | Gonzalo Pena | 2020-01-15 | Albert Burge
MBS-05 | MBS-05 | PI13414 | Verified | 1B-MSS-PV-8129 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-23 | Gonzalo Pena | Const | 2019-11-26 | Gonzalo Pena | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI13415 | Verified | 1B-MSS-TE-8126A, B, C - flex too short. | A | E | Chris Colvin | McD | 2019-11-23 | Chris Colvin | Const | 2019-11-26 | Brad Stanford | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI13416 | Verified | 1B-MSS-TE-8126A missing tag. | C | I | Gonzalo Pena | McD | 2019-11-23 | Gonzalo Pena | Const | 2019-12-31 | Gonzalo Pena | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI14359 | Verified | 1B-MSS-MOV-8137 actuator needs to be rotated 90 degrees to plant east. Once scaffold is taken down for first fire we will not be able to access the controls if needed during operations. | A | P | Bobby Williams | McD | 2019-12-05 | Bobby Williams | Const | 2019-12-06 | Bobby Williams | 2020-01-16 | Michael Law
MBS-05 | MBS-05 | PI14641 | Verified | Re-route six umbilicals that are in contact with 1B-MSS-LE-8011. | A | I | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Const | 2019-12-09 | James Tanner | 2020-01-01 | Albert Burge
MBS-05 | MBS-05 | PI14642 | Verified | Hold down clamp missing southeast corner, first support after vertical outside 90 degree elbow on horizontal tray. | C | E | Chris Colvin | McD | 2019-12-08 | Chris Colvin | Const | 2020-04-21 | Matt Gilmore | 2020-04-29 | Mike Tabbert
MBS-05 | MBS-05 | PI15849 | Verified | Retube the HP Water Drum Level transmitters 1B-MSS-LIT-8003A. | A | I | Gonzalo Pena | McD | 2020-01-10 | Gonzalo Pena | Comm | 2020-02-10 | James Tanner | 2020-02-18 | Albert Burge
MBS-05 | MBS-05 | PI15850 | Verified | Retube the HP Water Drum Level transmitters 1B-MSS-LIT-8003B. | A | I | Gonzalo Pena | McD | 2020-01-10 | Gonzalo Pena | Comm | 2020-02-10 | James Tanner | 2020-02-18 | Albert Burge
MBS-05 | MBS-05 | PI15851 | Verified | Retube the HP Water Drum Level transmitters 1B-MSS-LIT-8003C. | A | I | Gonzalo Pena | McD | 2020-01-10 | Gonzalo Pena | Comm | 2020-02-10 | James Tanner | 2020-02-18 | Albert Burge
MBS-05 | MBS-05 | PI16041 | Verified | Install spray nozzles 1B-FWS-DESC-8100 | B | P | Bobby Williams | McD | 2020-01-14 | Bobby Williams | Const | 2020-01-16 | Bobby Williams | 2020-01-21 | Michael Law
MBS-05 | MBS-05 | PI16677 | Verified | 1B-MSS-V-8140 & 1B-MSS-V-8141 - 1B HP Superheater No. 1 and HP Superheater No. 2 crossover piping vent valves, 1B-MSS-V-8141 and 1B-MSS-V-8140, are leaking by. | B | M | Bobby Williams | McD | 2020-02-07 | Bobby Williams | Comm | 2020-03-27 | William Mitchell | 2020-04-06 | Bernard Stasse
MBS-05 | MBS-05 | PI16678 | Verified | 1B-MSS-PIT-8007A - There's a steam leak at the weld of the sensing tubing going to the transmitter. Currently, the valve is out of service because steam was filling 1B-HTS-CAB-0207. | B | I | Gonzalo Pena | McD | 2020-02-07 | Gonzalo Pena | Comm | 2020-02-12 | James Tanner | 2020-02-17 | Shannon Scott
MBS-05 | MBS-05 | PI17859 | Verified | 1B-MSS-TI-8126C 1B HP Steam Outlet Temp reads 20 degs F lower than other TE's | B | E | Albert Burge | McD | 2020-03-16 | Albert Burge | Comm | 2020-03-19 | Albert Burge | 2020-06-02 | Keith Pollock
MBS-05 | MBS-05 | PI18683 | Verified | 1B HRSG HP Steam Generator system nameplate is incorrect per Nooter Eriksen drawing 170300-GA-001, Rev. C. Nameplate should read: Steam Capacity 1,250,230 LBS/HR | C | S | Tim Gallegos | McD | 2020-06-24 | Tim Gallegos | Const | 2020-08-24 | Tim Gallegos | 2021-01-15 | Dave Goldak
MBS-06 | MBS-06 | PI04736 | Verified | Restore check valve 1B-FWS-CHK-8201 (AFTER FLUSH) | B | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2019-12-06 | Bobby Williams | 2019-12-12 | Shane Copeland
MBS-06 | MBS-06 | PI04737 | Verified | Weld at olet to 170337-RP-101 not made | A | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-06 | MBS-06 | PI04738 | Verified | Restore valve 1B-FWS-LV-8207A (AFTER FLUSH) | A | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2019-12-04 | Bobby Williams | 2019-12-05 | Shane Copeland
MBS-06 | MBS-06 | PI04739 | Verified | Flow element not installed on 1B-FWS-FE-8207 (AFTER FLUSH) | A | M | William Mitchell | McD | 2019-09-04 | William Mitchell | Const | 2019-12-20 | Bobby Williams | 2019-12-20 | Michael Law
MBS-06 | MBS-06 | PI04740 | Verified | 1B-FWS-TE-8204 missing tag | C | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Alex Isaac
MBS-06 | MBS-06 | PI04741 | Verified | 1B-FWS-TP-8203 not installed | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Alex Isaac
MBS-06 | MBS-06 | PI04742 | Verified | Valve 1B-FWS-V-8206 missing tag | C | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2019-12-07 | Bobby Williams | 2020-01-09 | Kelvin Cook
MBS-06 | MBS-06 | PI04743 | Verified | 1B-FWS-PIT-8206 not installed | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-06 | MBS-06 | PI04744 | Verified | 1B-FWS-FIT-8207 not installed | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-06 | MBS-06 | PI04745 | Verified | Replace damaged flex hose on valve 1B-FWS-AOV-8207B | C | E | Chris Colvin | McD | 2019-09-04 | Chris Colvin | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
MBS-06 | MBS-06 | PI04746 | Verified | 1B-IPS-LIT-8202C not installed | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-06 | MBS-06 | PI04747 | Verified | 1B-IPS-LIT-8202B not installed | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-06 | MBS-06 | PI04748 | Verified | 1B-IPS-LIT-8202A not installed | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-06 | MBS-06 | PI04749 | Verified | 1B-IPS-PIT-8204A not installed | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-06 | MBS-06 | PI04750 | Verified | 1B-IPS-PIT-8204B not installed | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-06 | MBS-06 | PI04751 | Verified | 1B-IPS-PI-8203 not installed | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-11-06 | Gonzalo Pena | 2019-11-18 | Alex Isaac
MBS-06 | MBS-06 | PI04752 | Verified | 1B-IPS-PIT-8204C not installed | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-06 | MBS-06 | PI04753 | Verified | Grout not installed on support IPS04APS02 | C | C | Johnny Campbell | McD | 2019-09-04 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-07 | Ethan Byrd
MBS-06 | MBS-06 | PI04754 | Verified | 1B-IPS-TE-8302 missing tag | C | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Alex Isaac
MBS-06 | MBS-06 | PI04755 | Verified | Install FE 1A-IPS-FE-8312 (INSTALL AFTER FLUSH) | B | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2019-12-06 | Shane Copeland | 2019-12-13 | Shane Copeland
MBS-06 | MBS-06 | PI04756 | Verified | Valve 1B-IPS-PV-8303 needs restoration, (RESTORE AFTER Steam Blow) | A | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2020-02-06 | Bobby Williams | 2020-02-06 | Kelvin Cook
MBS-06 | MBS-06 | PI04757 | Verified | 1B-IPS-PIT-8303 not installed | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-06 | MBS-06 | PI04758 | Verified | INSTALL SPOOL IP-07-C-01 (AFTER IB-IPS-FE-8312 INSTALLATION) | B | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2020-01-31 | Bobby Williams | 2020-01-31 | Kelvin Cook
MBS-06 | MBS-06 | PI04759 | Verified | INSTALL SPOOL IP-07-D-01 (AFTER IB-IPS-FE-8312 INSTALLATION) | B | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2020-01-31 | Bobby Williams | 2020-01-31 | Kelvin Cook
MBS-06 | MBS-06 | PI04760 | Verified | Grout not installed on support IPS10PS01 | C | C | Johnny Campbell | McD | 2019-09-04 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-07 | Ethan Byrd
MBS-06 | MBS-06 | PI04761 | Verified | Grout not installed on support IPS11PS04 | C | C | Johnny Campbell | McD | 2019-09-04 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-07 | Ethan Byrd
MBS-06 | MBS-06 | PI04762 | Verified | Grout not installed on support IPS11PS05 | C | C | Johnny Campbell | McD | 2019-09-04 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-07 | Ethan Byrd
MBS-06 | MBS-06 | PI04763 | Verified | Restore line to blowdown tank (FILL POINT FOR HYDRO) | B | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2019-12-05 | Bobby Williams | 2019-12-09 | Shane Copeland
MBS-06 | MBS-06 | PI04764 | Verified | Grout not installed on support IPS11PS02 | C | C | Johnny Campbell | McD | 2019-09-04 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-07 | Ethan Byrd
MBS-06 | MBS-06 | PI04765 | Verified | Loose nuts on strut support IPS15PS01 | C | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2019-09-19 | Bobby Williams | 2019-09-27 | Alex Isaac
MBS-06 | MBS-06 | PI04766 | Verified | Support IPS15PS06 not installed | B | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2019-09-06 | Bobby Williams | 2019-09-12 | Alex Isaac
MBS-06 | MBS-06 | PI04767 | Verified | Weld not made at connection to BOP piping | A | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-06 | MBS-06 | PI04768 | Verified | Valve 1B-MBL-MOV-8260 missing tag | C | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2019-09-06 | Bobby Williams | 2019-09-12 | Alex Isaac
MBS-06 | MBS-06 | PI06548 | Verified | Tag all valves with proper tag numbers, (1B-). Currently tagged 1X-. | C | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-12-05 | Bobby Williams | 2019-12-15 | Shannon Scott
MBS-06 | MBS-06 | PI06556 | Verified | Remove all plastic from piping (under HRSG). | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-11-06 | Bobby Williams | 2020-01-21 | Michael Law
MBS-06 | MBS-06 | PI06564 | Verified | Set all spring cans to cold settings. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-12-23 | Bobby Williams | 2020-01-27 | Michael Law
MBS-06 | MBS-06 | PI06576 | Verified | Line at IP drum needs additional support - east end of drum. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-10-03 | Shannon Scott
MBS-06 | MBS-06 | PI06578 | Verified | IP-101 - needs added support - south side of IP drum. | A | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Shannon Scott
MBS-06 | MBS-06 | PI06580 | Verified | Loose nut on support at valve 1B-IPS-CHK-8308 - south side of drum. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-10-03 | Shannon Scott
MBS-06 | MBS-06 | PI06581 | Verified | Cold galv. IP drum trim supports. | C | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-10-03 | Shannon Scott
MBS-06 | MBS-06 | PI10016 | Verified | 1BFWSK0015 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10017 | Verified | 1BIPSC0004 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10018 | Verified | 1BIPSX0002 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10019 | Verified | 1BIPSX0004 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10020 | Verified | 1BIPSX0005 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10021 | Verified | 1BIPSX0007 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10022 | Verified | 1BIPSX0008 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10023 | Verified | 1BIPSX0009 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10024 | Verified | 1BIPSX0010 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10025 | Verified | 1BIPSX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10026 | Verified | 1BIPSX0012 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10027 | Verified | 1BIPSX0013 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10035 | Verified | 1BMBLK0011 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10036 | Verified | 1BMBLK0012 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10037 | Verified | 1BMBLK0015 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10052 | Verified | 1BFWSC0031 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10053 | Verified | 1BFWSK0015 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10054 | Verified | 1BIPSC0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10055 | Verified | 1BIPSX0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-12-12 | Jared Stimpson | 2019-12-20 | Mike Tabbert
MBS-06 | MBS-06 | PI10056 | Verified | 1BIPSX0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10057 | Verified | 1BIPSX0005 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10058 | Verified | 1BIPSX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10059 | Verified | 1BIPSX0008 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10060 | Verified | 1BIPSX0009 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10061 | Verified | 1BIPSX0010 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10062 | Verified | 1BIPSX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10063 | Verified | 1BIPSX0012 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10064 | Verified | 1BIPSX0013 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10074 | Verified | 1BMBLC0011 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10075 | Verified | 1BMBLC0012 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10076 | Verified | 1BMBLC0015 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10077 | Verified | 1BMBLC0016 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10083 | Verified | 1BMBLK0011 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10084 | Verified | 1BMBLK0012 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI10085 | Verified | 1BMBLK0015 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-06 | MBS-06 | PI13269 | Verified | Clean outside of all instrument cabinets and inside if needed. | C | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2020-02-13 | James Tanner | 2020-02-17 | Shannon Scott
MBS-06 | MBS-06 | PI13270 | Verified | Heat shrink all boots. | B | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | Gonzalo Pena | 2020-01-13 | Fred Michael
MBS-06 | MBS-06 | PI13271 | Verified | Tighten all flex. | B | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2020-01-01 | Albert Burge
MBS-06 | MBS-06 | PI13272 | Verified | Install kick plates at all grating penetrations. | C | S | Tim Gallegos | McD | 2019-11-22 | Tim Gallegos | Const | 2020-06-11 | Tim Gallegos | 2020-07-10 | Dave Goldak
MBS-06 | MBS-06 | PI13273 | Verified | Tag all drum level junction boxes. | C | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2020-04-28 | Matt Gilmore | 2020-04-29 | Mike Tabbert
MBS-06 | MBS-06 | PI13274 | Verified | 1B-IPS-LG-8205 - missing plug. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-11-26 | Gonzalo Pena | 2020-01-13 | Fred Michael
MBS-06 | MBS-06 | PI13275 | Verified | 1B-HTS-CAB-0104 needs bracing / support. | C | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2020-02-18 | James Tanner | 2020-04-06 | Bernard Stasse
MBS-06 | MBS-06 | PI13276 | Verified | 1B-IPS-PI-8203 not installed. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-11-23 | Michael Law | 2020-01-15 | Albert Burge
MBS-06 | MBS-06 | PI13277 | Verified | 1B-IPS-LIT-8202C - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-11-26 | Gonzalo Pena | 2020-01-13 | Fred Michael
MBS-06 | MBS-06 | PI13278 | Verified | 1B-IPS-TE-8200A - rework flex (too short). | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-26 | Brad Stanford | 2020-01-13 | Fred Michael
MBS-06 | MBS-06 | PI13279 | Verified | 1B-IPS-TE-8201 not installed. S.T. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | Gonzalo Pena | 2020-01-13 | Fred Michael
MBS-06 | MBS-06 | PI13280 | Verified | 1B-MBS-PI-0111 - clean gauge glass. | B | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-20 | Shannon Scott
MBS-06 | MBS-06 | PI13281 | Verified | 1B-IPS-PIT-8303 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-11-26 | Gonzalo Pena | 2020-01-01 | Albert Burge
MBS-06 | MBS-06 | PI13282 | Verified | 1B-IPS-LIT-8201A - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-11-26 | Gonzalo Pena | 2020-01-01 | Albert Burge
MBS-06 | MBS-06 | PI13283 | Verified | 1B-IPS-LIT-8201B - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-11-26 | Gonzalo Pena | 2020-01-01 | Albert Burge
MBS-06 | MBS-06 | PI13284 | Verified | 1B-IPS-JB-8208 - back plate rusted / clean inside. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-26 | Brad Stanford | 2019-12-05 | Mike Tabbert
MBS-06 | MBS-06 | PI13285 | Verified | 1B-IPS-PIT-8204B - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-11-26 | Gonzalo Pena | 2020-01-01 | Albert Burge
MBS-06 | MBS-06 | PI13286 | Verified | 1B-HTS-CAB-0203 needs bracing / support. | C | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2020-02-18 | James Tanner | 2020-04-06 | Bernard Stasse
MBS-06 | MBS-06 | PI13287 | Verified | 1B-IPS-LIY-8208 - back plate rusted / clean. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-26 | Brad Stanford | 2020-01-01 | Albert Burge
MBS-06 | MBS-06 | PI13288 | Verified | 1B-FWS-FIT-8207 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-01 | Albert Burge
MBS-06 | MBS-06 | PI13289 | Verified | 1B-FWS-PIT-8206 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-01 | Albert Burge
MBS-06 | MBS-06 | PI13290 | Verified | 1B-MBL-LSH-8305 missing tag. | C | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-13 | Fred Michael
MBS-06 | MBS-06 | PI13342 | Verified | 1BIPSC0004, From Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-12-04 | Mike Tabbert
MBS-06 | MBS-06 | PI13343 | Verified | 1BIPSK0003, From Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-06 | MBS-06 | PI13344 | Verified | 1BIPSX0001, From Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-05 | Mike Tabbert
MBS-06 | MBS-06 | PI13345 | Verified | 1BIPSX0002, From Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-06 | MBS-06 | PI13346 | Verified | 1BIPSX0007, From Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-06 | MBS-06 | PI13347 | Verified | 1BIPSX0008, From Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-06 | MBS-06 | PI13348 | Verified | 1BIPSX0010, From Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-06 | MBS-06 | PI13349 | Verified | 1BIPSX0011, From Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-06 | MBS-06 | PI13350 | Verified | 1BFWSC0031, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-06 | MBS-06 | PI13351 | Verified | 1BFWSX0028, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-06 | MBS-06 | PI13352 | Verified | 1BFWSX0029, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-06 | MBS-06 | PI13354 | Verified | 1BIPSC0004, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-06 | MBS-06 | PI13355 | Verified | 1BIPSK0003, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-06 | MBS-06 | PI13356 | Verified | 1BIPSX0001, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-06 | MBS-06 | PI13357 | Verified | 1BIPSX0002, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-05 | Christie Harris | 2019-12-05 | Mike Tabbert
MBS-06 | MBS-06 | PI13358 | Verified | 1BIPSX0005, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-05 | Christie Harris | 2019-12-05 | Mike Tabbert
MBS-06 | MBS-06 | PI13359 | Verified | 1BIPSX0007, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-05 | Christie Harris | 2019-12-05 | Mike Tabbert
MBS-06 | MBS-06 | PI13360 | Verified | 1BIPSX0008, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-06 | MBS-06 | PI13361 | Verified | 1BIPSX0009, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-06 | MBS-06 | PI13362 | Verified | 1BIPSX0010, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-06 | MBS-06 | PI13363 | Verified | 1BIPSX0011, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-06 | MBS-06 | PI13364 | Verified | 1BIPSX0016, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-06 | MBS-06 | PI13365 | Verified | 1BIPSX0017, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-06 | MBS-06 | PI13366 | Verified | 1BMBLC0011, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-06 | MBS-06 | PI13367 | Verified | 1BMBLC0012, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-06 | MBS-06 | PI13368 | Verified | 1BMBLC0015, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-06 | MBS-06 | PI13369 | Verified | 1BMBLC0016, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-06 | MBS-06 | PI13370 | Verified | 1BMBLK0011, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-06 | MBS-06 | PI13545 | Verified | 1B-IPS-PV-8303 - install after steam blows. | A | I | Bobby Williams | McD | 2019-11-25 | Bobby Williams | Const |  |  | 2020-01-14 | Michael Law
MBS-06 | MBS-06 | PI16675 | Verified | 1B-IPS-PIT-8204A - There's a steam leak coming from the insulation at the transmitter root valve (1B-IPS-V-8251). | B | I | Bobby Williams | McD | 2020-02-07 | Bobby Williams | Comm | 2020-02-11 | Bobby Williams | 2020-04-06 | Bernard Stasse
MBS-06 | MBS-06 | PI17860 | Verified | 1B-IPS-TI-8200A 1B IP Drum Mid Wall Temp reads 31 deg F with unit running | B | E | Albert Burge | McD | 2020-03-16 | Albert Burge | Comm | 2020-03-19 | Albert Burge | 2020-03-26 | Keith Pollock
MBS-07 | MBS-07 | PI06549 | Verified | Tag all valves with proper tag numbers, (1B-). Currently tagged 1X-. | C | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2019-12-15 | Shannon Scott
MBS-07 | MBS-07 | PI06557 | Verified | Remove all plastic from piping (under HRSG). | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-11-06 | Bobby Williams | 2020-01-22 | Michael Law
MBS-07 | MBS-07 | PI06565 | Verified | Set all spring cans to cold settings. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-12-20 | Bobby Williams | 2020-01-27 | Michael Law
MBS-07 | MBS-07 | PI06582 | Verified | Install 1B-CNM-V-8522 - north side of LP drum. | A | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI06583 | Verified | Loose u-bolt at LP-13B - LP drum platform. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-10-03 | Shannon Scott
MBS-07 | MBS-07 | PI06584 | Verified | Tubing on 1B-LPS-PV-8708 is too close to hanger - south of LP drum. | A | I | Gonzalo Pena | McD | 2019-09-19 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-10-03 | Shannon Scott
MBS-07 | MBS-07 | PI06585 | Verified | Spread cotter pins on LP-14 support - south of LP drum. | A | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2020-01-22 | Michael Law
MBS-07 | MBS-07 | PI07137 | Verified | Tag not installed at TE 1B-CNM-TE-8503B | C | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-07 | Ethan Byrd
MBS-07 | MBS-07 | PI07138 | Verified | Support LPS01PS02 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-30 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07139 | Verified | PIT 1B-CNM-PIT-8504 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-07 | MBS-07 | PI07140 | Verified | TP 1B-CNM-TP-8508 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07141 | Verified | No tag installed on valve 1B-CNM-V-8508 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-07 | Ethan Byrd
MBS-07 | MBS-07 | PI07142 | Verified | TE 1B-CNM-TE-8510 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07143 | Verified | Shoe not welded to support per detail on support LPS03PS01 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07144 | Verified | Rotate spectacle blind to closed position for chemical clean | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07145 | Verified | No tag installed on valve 1B-CNM-V-8511 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-07 | Ethan Byrd
MBS-07 | MBS-07 | PI07146 | Verified | TP 1B-CNM-TP-8511 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07147 | Verified | No tag installed on valve 1B-CNM-V-8512 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-07 | Ethan Byrd
MBS-07 | MBS-07 | PI07148 | Verified | Restore valve 1B-CNM-LV-8500A (AFTER Chemical Clean) | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-12-04 | Bobby Williams | 2019-12-05 | Shane Copeland
MBS-07 | MBS-07 | PI07149 | Verified | Weld not made east side of valve 1B-CNM-V-8520 | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07150 | Verified | Tag not installed on TE 1B-CNM-TE-8517B | C | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-07 | Ethan Byrd
MBS-07 | MBS-07 | PI07151 | Verified | Tag not installed on TE 1B-CNM-TE-8517A | C | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-07 | Ethan Byrd
MBS-07 | MBS-07 | PI07152 | Verified | TP 1B-CNM-TP-8516 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07153 | Verified | SRV 1B-CNM-SRV-8518 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07154 | Verified | Tag not installed on TE 1B-CNM-TE-8515 | C | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-07 | Ethan Byrd
MBS-07 | MBS-07 | PI07155 | Verified | TP 1B-CNM-TP-8514 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07156 | Verified | Valve 1B-CNM-V-8522 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-14 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07157 | Verified | LIT 1B-LPS-LIT-8602C not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-07 | MBS-07 | PI07158 | Verified | LIT 1B-LPS-LIT-8602B not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-07 | MBS-07 | PI07159 | Verified | Remove temporary support (rope) at elevation +100'-8.1/4" | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-01 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07160 | Verified | LIT 1B-LPS-LIT-8602A not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-07 | MBS-07 | PI07161 | Verified | PIT 1B-LPS-PIT-8604A not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-07 | MBS-07 | PI07162 | Verified | PIT 1B-LPS-PIT-8604B not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-07 | MBS-07 | PI07163 | Verified | PI 1B-LPS-PI-8603 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07164 | Verified | PIT 1B-LPS-PIT-8604C not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-07 | MBS-07 | PI07165 | Verified | Support LPS13PS02 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-10-07 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07166 | Verified | No tag installed on valve 1B-MBL-MOV-8705 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-07 | Ethan Byrd
MBS-07 | MBS-07 | PI07167 | Verified | TP 1B-LPS-TP-8703 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07168 | Verified | TE 1B-LPS-TE-8704 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07169 | Verified | TP 1B-LPS-TP-8701 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07170 | Verified | TE 1B-LPS-TE-8702 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07171 | Verified | SRV 1B-LPS-SRV-8707 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07172 | Verified | No tag installed on valve 1B-LPS-MOV-8714 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-07 | Ethan Byrd
MBS-07 | MBS-07 | PI07173 | Verified | Spray Galv support LPS14PS04 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-30 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07174 | Verified | PIT 1B-LPS-PIT-8708 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MBS-07 | MBS-07 | PI07175 | Verified | Grout not installed on support LPS15PS01 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-03 | Ethan Byrd
MBS-07 | MBS-07 | PI07176 | Verified | Grout not installed on support LPS16PS01 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-03 | Ethan Byrd
MBS-07 | MBS-07 | PI07177 | Verified | Grout not installed on support LPS17PS01 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-03 | Ethan Byrd
MBS-07 | MBS-07 | PI07178 | Verified | Restore piping to blowdown tank (AFTER FLUSH) | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-12-04 | Bobby Williams | 2019-12-12 | Shane Copeland
MBS-07 | MBS-07 | PI07179 | Verified | Grout not installed on support LPS18PS05 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-03 | Ethan Byrd
MBS-07 | MBS-07 | PI07180 | Verified | Grout not installed on support LPS18PS06 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-03 | Ethan Byrd
MBS-07 | MBS-07 | PI07181 | Verified | Grout not installed on support LPS18PS01 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-03 | Ethan Byrd
MBS-07 | MBS-07 | PI07182 | Verified | Grout not installed on support LPS18PS02 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-03 | Ethan Byrd
MBS-07 | MBS-07 | PI07183 | Verified | Grout not installed on support LPS18PS03 | C | C | Johnny Campbell | McD | 2019-09-24 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2020-01-03 | Ethan Byrd
MBS-07 | MBS-07 | PI07184 | Verified | Complete field run drains on top of HRSG 1B | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2019-12-04 | Shane Copeland
MBS-07 | MBS-07 | PI07185 | Verified | Remove temporary support (rope) at elevation +97'-11.1/8" | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-30 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07186 | Verified | 1B-CRS-TE-8400 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07187 | Verified | Tag not installed on valve 1B-CRS-V-0019 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-07 | Ethan Byrd
MBS-07 | MBS-07 | PI07188 | Verified | Tag not installed on valve 1B-CRS-AOV-0020 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-09 | Kelvin Cook
MBS-07 | MBS-07 | PI07189 | Verified | 1B-HRS-TP-8416 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07190 | Verified | 1B-HRS-TE-8417A not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07191 | Verified | 1B-HRS-TE-8417B not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07192 | Verified | 1B-CRS-TP-8411 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07193 | Verified | 1B-CRS-TE-8412 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07194 | Verified | 1B-CRS-TE-8407 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07195 | Verified | 1B-CRS-TE-8408 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07196 | Verified | 1B-CRS-TE-8409 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07197 | Verified | 1B-CRS-TE-8410 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07198 | Verified | Remove debris from pipe directly under drain pot | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07199 | Verified | Support RPS02APS10 not set per detail | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-09-26 | Alex Isaac
MBS-07 | MBS-07 | PI07200 | Verified | Tag not installed on valve 1B-CRS-V-8433 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-09 | Kelvin Cook
MBS-07 | MBS-07 | PI07201 | Verified | Tag not installed on valve 1B-CRS-V-8434 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-09 | Kelvin Cook
MBS-07 | MBS-07 | PI07202 | Verified | 1B-HRS-TP-8424 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const |  |  | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07203 | Verified | 1B-HRS-TI-8426 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07204 | Verified | 1B-HRS-TE-8427A not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07205 | Verified | 1B-HRS-TP-8423 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07206 | Verified | 1B-HRS-TP-8421 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07207 | Verified | 1B-HRS-TP-8422 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07208 | Verified | 1B-HRS-TE-8427B not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-25 | Gonzalo Pena | 2019-09-25 | Alex Isaac
MBS-07 | MBS-07 | PI07209 | Verified | 1B-HRS-PIT-8428 not installed | A | I | Gonzalo Pena | McD | 2019-09-24 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-10-01 | Alex Isaac
MBS-07 | MBS-07 | PI07210 | Verified | Tag not installed on valve 1B-HRS-V-8432 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-09 | Kelvin Cook
MBS-07 | MBS-07 | PI07211 | Verified | Complete field run drains | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-09-26 | Alex Isaac
MBS-07 | MBS-07 | PI07212 | Verified | Weld not made to IP-01 continuation | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07213 | Verified | Support RPS101PS01 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07214 | Verified | Support RPS101PS02 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07215 | Verified | Weld at support RPS101PS03 not made | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07216 | Verified | Support RPS101PS03 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07217 | Verified | Support RPS101PS04 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07218 | Verified | Support RPS101PS05 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07219 | Verified | Support RPS101PS06 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07220 | Verified | Support RPS101PS07 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07221 | Verified | Spool RP-101-05 not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07222 | Verified | Restore valve 1B-FWS-TV-8418 (AFTER degrease) | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-12-05 | Bobby Williams | 2019-12-05 | Shane Copeland
MBS-07 | MBS-07 | PI07223 | Verified | Line not installed | A | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-09-25 | Bobby Williams | 2019-11-18 | Alex Isaac
MBS-07 | MBS-07 | PI07224 | Verified | Tag not installed on valve 1B-MBL-V-8422 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-09 | Kelvin Cook
MBS-07 | MBS-07 | PI07225 | Verified | Tag not installed on valve 1B-MBL-MOV-8423 | C | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-09 | Kelvin Cook
MBS-07 | MBS-07 | PI07226 | Verified | Restore line to blowdown tank (AFTER degrease) | B | P | Bobby Williams | McD | 2019-09-24 | Bobby Williams | Const | 2019-12-05 | Bobby Williams | 2019-12-12 | Shane Copeland
MBS-07 | MBS-07 | PI10028 | Verified | 1BLPSK0003 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-07 | MBS-07 | PI10038 | Verified | 1BMBLK0020 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-07 | MBS-07 | PI10065 | Verified | 1BLPSC0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-12-12 | Jared Stimpson | 2019-12-20 | Mike Tabbert
MBS-07 | MBS-07 | PI10066 | Verified | 1BLPSK0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-12-12 | Jared Stimpson | 2019-12-20 | Mike Tabbert
MBS-07 | MBS-07 | PI10078 | Verified | 1BMBLC0020 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-07 | MBS-07 | PI10086 | Verified | 1BMBLK0018 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-07 | MBS-07 | PI10087 | Verified | 1BMBLK0020 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-07 | MBS-07 | PI13291 | Verified | Clean outside of all instrument cabinets and inside if needed. | C | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2020-02-13 | James Tanner | 2020-02-17 | Shannon Scott
MBS-07 | MBS-07 | PI13292 | Verified | Heat shrink all boots. | B | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-15 | Albert Burge
MBS-07 | MBS-07 | PI13293 | Verified | Tighten all flex. | B | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2020-01-01 | Albert Burge
MBS-07 | MBS-07 | PI13294 | Verified | Install kick plates at all grating penetrations. | C | S | Tim Gallegos | McD | 2019-11-22 | Tim Gallegos | Const | 2020-05-15 | Tim Gallegos | 2020-07-10 | Dave Goldak
MBS-07 | MBS-07 | PI13295 | Verified | 1B-HTS-CAB-0106 & tube bundle needs bracing / support. | C | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2020-02-13 | James Tanner | 2020-02-17 | Shannon Scott
MBS-07 | MBS-07 | PI13296 | Verified | 1B-LPS-LIY-8605 - re-work conduit for access. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2020-01-15 | Albert Burge
MBS-07 | MBS-07 | PI13297 | Verified | 1B-LPS-LIT-8602A - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-13 | Fred Michael
MBS-07 | MBS-07 | PI13298 | Verified | 1B-CNM-PIT-8504 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-13 | Fred Michael
MBS-07 | MBS-07 | PI13299 | Verified | 1B-HTS-CAB-0107 needs bracing / support. | C | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2020-01-06 | Gonzalo Pena | 2020-01-13 | Fred Michael
MBS-07 | MBS-07 | PI13300 | Verified | 1B-LPS-LIT-8602B - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-13 | Fred Michael
MBS-07 | MBS-07 | PI13301 | Verified | 1B-LPS-LIT-8602C - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-01 | Albert Burge
MBS-07 | MBS-07 | PI13302 | Verified | 1B-LPS-PIT-8604C - tube bundle needs separation from pipe. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2019-12-15 | Shannon Scott
MBS-07 | MBS-07 | PI13303 | Verified | 1B-LPS-PI-8603 not installed. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-13 | Fred Michael
MBS-07 | MBS-07 | PI13304 | Verified | Rework insulation on the west manway of the LP Drum for access to flange. | C | Q | Sheri Fritz | PCI | 2019-11-22 | Sheri Fritz | Const | 2020-03-07 | Albert Burge | 2020-03-07 | Albert Burge
MBS-07 | MBS-07 | PI13305 | Verified | 1B-LPS-PIT-8708 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-01 | Albert Burge
MBS-07 | MBS-07 | PI13306 | Verified | 1B-LPS-PV-8708 - air supply tubing missing. | A | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-01 | Albert Burge
MBS-07 | MBS-07 | PI13307 | Verified | 1B-MBL-LSH-8905 needs tag. | C | I | Gonzalo Pena | McD | 2019-11-22 | Gonzalo Pena | Const | 2019-12-04 | James Tanner | 2020-01-01 | Albert Burge
MBS-07 | MBS-07 | PI13308 | Verified | Tag all drum level junction boxes. | C | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-05 | Brad Stanford | 2019-12-08 | Mike Tabbert
MBS-07 | MBS-07 | PI13323 | Verified | 1BCNMX0004, From Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-07 | MBS-07 | PI13324 | Verified | 1BLPSK0006, From Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-05 | Christie Harris | 2019-12-05 | Chris Caywood
MBS-07 | MBS-07 | PI13325 | Verified | 1BLPSX0016, From Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-07 | MBS-07 | PI13326 | Verified | 1BLPSX0029, From Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-07 | MBS-07 | PI13327 | Verified | 1BLPSX0030, From Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-07 | MBS-07 | PI13328 | Verified | 1BCNMX0002, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-12-05 | Mike Tabbert
MBS-07 | MBS-07 | PI13329 | Verified | 1BCNMX0003, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-07 | MBS-07 | PI13330 | Verified | 1BCNMX0008, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-05 | Christie Harris | 2019-12-05 | Chris Caywood
MBS-07 | MBS-07 | PI13331 | Verified | 1BLPSC0003, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-07 | MBS-07 | PI13332 | Verified | 1BLPSK0006, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-07 | MBS-07 | PI13333 | Verified | 1BLPSX0013, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-07 | MBS-07 | PI13334 | Verified | 1BLPSX0014, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-07 | MBS-07 | PI13335 | Verified | 1BLPSX0015, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-07 | MBS-07 | PI13336 | Verified | 1BLPSX0016, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-07 | MBS-07 | PI13337 | Verified | 1BLPSX0020, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-05 | Christie Harris | 2019-12-05 | Chris Caywood
MBS-07 | MBS-07 | PI13338 | Verified | 1BLPSX0029, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-07 | MBS-07 | PI13339 | Verified | 1BLPSX0030, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-11-26 | Chris Caywood
MBS-07 | MBS-07 | PI13340 | Verified | 1BMBLC0020, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-05 | Christie Harris | 2019-12-05 | Chris Caywood
MBS-07 | MBS-07 | PI13341 | Verified | 1BMBLK0018, To Termination | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-11-24 | Dustin Futrell | 2019-12-04 | Mike Tabbert
MBS-07 | MBS-07 | PI16043 | Verified | Install spray nozzles 1B-FWS-DESC-8401 | B | P | Bobby Williams | McD | 2020-01-14 | Bobby Williams | Const | 2020-01-16 | Bobby Williams | 2020-01-27 | Michael Law
MBS-07 | MBS-07 | PI17861 | Verified | 1B-LPS-TI-8601A 1B LP Drum Inner Wall Temp reads 30 deg F off from 1B-LPS-TI-8601B | B | E | Albert Burge | McD | 2020-03-16 | Albert Burge | Comm | 2020-03-19 | Albert Burge | 2020-03-26 | Keith Pollock
MBS-08 | MBS-08 | PI04769 | Verified | Complete tubing to all AOV's on the Gas Fired Duct Burner (20 PLACES) | A | I | Gonzalo Pena | McD | 2019-09-04 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-05 | Alex Isaac
MBS-08 | MBS-08 | PI04770 | Verified | Guides not installed on support BPS02PS04 | A | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const | 2019-09-06 | Bobby Williams | 2019-09-12 | Alex Isaac
MBS-08 | MBS-08 | PI04771 | Verified | Line not installed | A | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const |  |  | 2019-09-18 | Alex Isaac
MBS-08 | MBS-08 | PI04772 | Verified | Line not installed | A | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const |  |  | 2019-09-18 | Alex Isaac
MBS-08 | MBS-08 | PI04773 | Verified | Line not installed | A | P | Bobby Williams | McD | 2019-09-04 | Bobby Williams | Const |  |  | 2019-09-18 | Alex Isaac
MBS-08 | MBS-08 | PI06550 | Verified | Tag all valves with proper tag numbers, (1B-). Currently tagged 1X-. | C | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2019-12-15 | Shannon Scott
MBS-08 | MBS-08 | PI06558 | Verified | Remove all plastic from piping (under HRSG). | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-11-06 | Bobby Williams | 2020-01-27 | Michael Law
MBS-08 | MBS-08 | PI06566 | Verified | Set all spring cans to cold settings. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-11-26 | Bobby Williams | 2020-01-15 | Michael Law
MBS-08 | MBS-08 | PI06567 | Verified | 1B-MBS-PI-8133 - needle broken - cooling air blower skid. | A | I | Gonzalo Pena | McD | 2019-09-19 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-03 | Shannon Scott
MBS-08 | MBS-08 | PI06568 | Verified | Remove scaffold on 1st level. | B | C | Jerry Smith | McD | 2019-09-19 | Jerry Smith | Const | 2019-11-11 | Jerry Smith | 2020-01-15 | Michael Law
MBS-08 | MBS-08 | PI06569 | Verified | Loose u-bolt on scanner air riser - 1st level. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-10-03 | Shannon Scott
MBS-08 | MBS-08 | PI06570 | Verified | Missing ignitor - 1st level. | A | I | Gonzalo Pena | McD | 2019-09-19 | Gonzalo Pena | Const | 2019-11-08 | James Tanner | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI06571 | Verified | Remove scaffold on 2nd level. | B | C | Jerry Smith | McD | 2019-09-19 | Jerry Smith | Const | 2019-11-11 | Jerry Smith | 2020-01-15 | Michael Law
MBS-08 | MBS-08 | PI06572 | Verified | Loose u-bolts on scanner air riser - 4th level. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-26 | Bobby Williams | 2019-10-03 | Shannon Scott
MBS-08 | MBS-08 | PI06573 | Verified | Trim mid-rail for valve operation - all levels. | A | S | Tim Gallegos | McD | 2019-09-19 | Tim Gallegos | Const | 2019-09-26 | Bobby Williams | 2019-10-03 | Shannon Scott
MBS-08 | MBS-08 | PI06574 | Verified | Valve 8140G (all "G" valves - all levels) - handle hits toe plate. | A | S | Tim Gallegos | McD | 2019-09-19 | Tim Gallegos | Const | 2019-09-23 | Bobby Williams | 2019-09-25 | Shannon Scott
MBS-08 | MBS-08 | PI06575 | Verified | Loose u-bolts on scanner air riser - 5th level. | B | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-23 | Bobby Williams | 2019-09-25 | Shannon Scott
MBS-08 | MBS-08 | PI06587 | Verified | Support missing on gas header riser (dead leg) - level 3. | A | P | Bobby Williams | McD | 2019-09-19 | Bobby Williams | Const | 2019-09-23 | Bobby Williams | 2019-10-01 | Alex Isaac
MBS-08 | MBS-08 | PI10029 | Verified | 1BMBBK0001 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-08 | MBS-08 | PI10030 | Verified | 1BMBBK0013 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-08 | MBS-08 | PI10031 | Verified | 1BMBBK0014 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-08 | MBS-08 | PI10067 | Verified | 1BMBBC0081 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-08 | MBS-08 | PI10068 | Verified | 1BMBBK0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-08 | MBS-08 | PI10069 | Verified | 1BMBBK0013 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-08 | MBS-08 | PI10070 | Verified | 1BMBBK0014 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MBS-08 | MBS-08 | PI11082 | Verified | 1BCRSX0007 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11083 | Verified | 1BCRSX0010 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11174 | Verified | 1BMBBC0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11175 | Verified | 1BMBBC0002 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11176 | Verified | 1BMBBC0003 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11177 | Verified | 1BMBBC0004 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11178 | Verified | 1BMBBC0008 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11179 | Verified | 1BMBBC0009 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11180 | Verified | 1BMBBC0010 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11181 | Verified | 1BMBBC0011 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11182 | Verified | 1BMBBC0012 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11183 | Verified | 1BMBBC0013 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11184 | Verified | 1BMBBC0014 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11185 | Verified | 1BMBBC0015 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11186 | Verified | 1BMBBC0016 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11187 | Verified | 1BMBBC0017 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11188 | Verified | 1BMBBC0018 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11189 | Verified | 1BMBBC0019 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11190 | Verified | 1BMBBC0020 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11191 | Verified | 1BMBBC0021 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11192 | Verified | 1BMBBC0022 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11193 | Verified | 1BMBBC0023 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11194 | Verified | 1BMBBC0024 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11195 | Verified | 1BMBBC0025 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11196 | Verified | 1BMBBC0026 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11197 | Verified | 1BMBBC0027 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11198 | Verified | 1BMBBC0028 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11199 | Verified | 1BMBBC0029 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11200 | Verified | 1BMBBC0030 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11201 | Verified | 1BMBBC0031 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11202 | Verified | 1BMBBC0032 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11203 | Verified | 1BMBBC0033 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11204 | Verified | 1BMBBC0034 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11205 | Verified | 1BMBBC0035 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11206 | Verified | 1BMBBC0036 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11207 | Verified | 1BMBBC0037 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11208 | Verified | 1BMBBC0038 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11209 | Verified | 1BMBBC0079 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11210 | Verified | 1BMBBC0080 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11211 | Verified | 1BMBBC0082 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11212 | Verified | 1BMBBC0083 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11213 | Verified | 1BMBBC0084 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11214 | Verified | 1BMBBK0002 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
MBS-08 | MBS-08 | PI11215 | Verified | 1BMBBK0003 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11216 | Verified | 1BMBBK0004 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11217 | Verified | 1BMBBK0005 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11218 | Verified | 1BMBBK0006 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11219 | Verified | 1BMBBK0007 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11220 | Verified | 1BMBBK0008 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11221 | Verified | 1BMBBK0009 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11222 | Verified | 1BMBBK0010 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11223 | Verified | 1BMBBK0011 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11224 | Verified | 1BMBBK0012 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11225 | Verified | 1BMBBK0015 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11226 | Verified | 1BMBBK0016 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11227 | Verified | 1BMBBK0017 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11228 | Verified | 1BMBBK0018 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11229 | Verified | 1BMBBK0019 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11230 | Verified | 1BMBBK0020 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11231 | Verified | 1BMBBK0021 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11232 | Verified | 1BMBBK0022 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11233 | Verified | 1BMBBK0023 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11234 | Verified | 1BMBBK0024 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11235 | Verified | 1BMBBX0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11236 | Verified | 1BMBBX0002 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11237 | Verified | 1BMBBX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11238 | Verified | 1BMBBX0004 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11239 | Verified | 1BMBBX0005 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11240 | Verified | 1BMBBX0006 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11241 | Verified | 1BMBBX0007 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11242 | Verified | 1BMBBX0008 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11243 | Verified | 1BMBBX0009 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11244 | Verified | 1BMBBX0010 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11245 | Verified | 1BMBBX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11246 | Verified | 1BMBBX0012 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11257 | Verified | 1BMBSC0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11258 | Verified | 1BMBSC0003 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11259 | Verified | 1BMBSC0004 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11260 | Verified | 1BMBSK0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11261 | Verified | 1BMBSX0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11262 | Verified | 1BMBSX0002 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11263 | Verified | 1BMBSX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11264 | Verified | 1BMBSX0004 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11265 | Verified | 1BMBSX0005 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11266 | Verified | 1BMBSX0006 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11267 | Verified | 1BMBSX0007 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11268 | Verified | 1BMBSX0008 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11269 | Verified | 1BMBSX0009 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11270 | Verified | 1BMBSX0010 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11271 | Verified | 1BMBSX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11272 | Verified | 1BMBSX0012 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11273 | Verified | 1BMBSX0013 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11274 | Verified | 1BMBSX0014 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
MBS-08 | MBS-08 | PI11275 | Verified | 1BMBSX0015 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
MBS-08 | MBS-08 | PI11276 | Verified | 1BMBSX0016 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11277 | Verified | 1BMBSX0017 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11278 | Verified | 1BMBSX0018 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11279 | Verified | 1BMBSX0019 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11319 | Verified | 1BMSSX0059 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11729 | Verified | 1BCRSX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11730 | Verified | 1BCRSX0010 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11821 | Verified | 1BMBBC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11822 | Verified | 1BMBBC0002 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11823 | Verified | 1BMBBC0003 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
MBS-08 | MBS-08 | PI11824 | Verified | 1BMBBC0004 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
MBS-08 | MBS-08 | PI11825 | Verified | 1BMBBC0008 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11826 | Verified | 1BMBBC0009 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11827 | Verified | 1BMBBC0010 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11828 | Verified | 1BMBBC0011 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11829 | Verified | 1BMBBC0012 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11830 | Verified | 1BMBBC0013 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11831 | Verified | 1BMBBC0014 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11832 | Verified | 1BMBBC0015 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11833 | Verified | 1BMBBC0016 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11834 | Verified | 1BMBBC0017 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11835 | Verified | 1BMBBC0018 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11836 | Verified | 1BMBBC0019 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11837 | Verified | 1BMBBC0020 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11838 | Verified | 1BMBBC0021 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11839 | Verified | 1BMBBC0022 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11840 | Verified | 1BMBBC0023 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11841 | Verified | 1BMBBC0024 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11842 | Verified | 1BMBBC0025 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11843 | Verified | 1BMBBC0026 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11844 | Verified | 1BMBBC0027 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11845 | Verified | 1BMBBC0028 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11846 | Verified | 1BMBBC0029 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11847 | Verified | 1BMBBC0030 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11848 | Verified | 1BMBBC0031 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
MBS-08 | MBS-08 | PI11849 | Verified | 1BMBBC0032 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11850 | Verified | 1BMBBC0033 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11851 | Verified | 1BMBBC0034 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11852 | Verified | 1BMBBC0035 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11853 | Verified | 1BMBBC0036 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11854 | Verified | 1BMBBC0037 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11855 | Verified | 1BMBBC0038 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11856 | Verified | 1BMBBC0079 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11857 | Verified | 1BMBBC0080 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11858 | Verified | 1BMBBC0082 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11859 | Verified | 1BMBBC0083 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11860 | Verified | 1BMBBC0084 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11861 | Verified | 1BMBBK0002 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11862 | Verified | 1BMBBK0003 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11863 | Verified | 1BMBBK0004 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11864 | Verified | 1BMBBK0005 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11865 | Verified | 1BMBBK0006 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11866 | Verified | 1BMBBK0007 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11867 | Verified | 1BMBBK0008 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11868 | Verified | 1BMBBK0009 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11869 | Verified | 1BMBBK0010 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11870 | Verified | 1BMBBK0011 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11871 | Verified | 1BMBBK0012 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11872 | Verified | 1BMBBK0015 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11873 | Verified | 1BMBBK0016 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11874 | Verified | 1BMBBK0017 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11875 | Verified | 1BMBBK0018 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11876 | Verified | 1BMBBK0019 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11877 | Verified | 1BMBBK0020 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11878 | Verified | 1BMBBK0021 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11879 | Verified | 1BMBBK0022 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11880 | Verified | 1BMBBK0023 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11881 | Verified | 1BMBBK0024 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11882 | Verified | 1BMBBX0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11883 | Verified | 1BMBBX0002 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11884 | Verified | 1BMBBX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11885 | Verified | 1BMBBX0004 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11886 | Verified | 1BMBBX0005 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11887 | Verified | 1BMBBX0006 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11888 | Verified | 1BMBBX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11889 | Verified | 1BMBBX0008 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11890 | Verified | 1BMBBX0009 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11891 | Verified | 1BMBBX0010 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11892 | Verified | 1BMBBX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11893 | Verified | 1BMBBX0012 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11904 | Verified | 1BMBSC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11905 | Verified | 1BMBSC0003 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11906 | Verified | 1BMBSC0004 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11907 | Verified | 1BMBSK0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11908 | Verified | 1BMBSX0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11909 | Verified | 1BMBSX0002 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11910 | Verified | 1BMBSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11911 | Verified | 1BMBSX0004 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11912 | Verified | 1BMBSX0005 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11913 | Verified | 1BMBSX0006 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11914 | Verified | 1BMBSX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11915 | Verified | 1BMBSX0008 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11916 | Verified | 1BMBSX0009 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11917 | Verified | 1BMBSX0010 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11918 | Verified | 1BMBSX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11919 | Verified | 1BMBSX0012 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11920 | Verified | 1BMBSX0013 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11921 | Verified | 1BMBSX0014 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
MBS-08 | MBS-08 | PI11922 | Verified | 1BMBSX0015 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
MBS-08 | MBS-08 | PI11923 | Verified | 1BMBSX0016 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11924 | Verified | 1BMBSX0017 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11925 | Verified | 1BMBSX0018 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11926 | Verified | 1BMBSX0019 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI11966 | Verified | 1BMSSX0059 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI12206 | Verified | 1BMBBK0001 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI12207 | Verified | 1BMBBK0013 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
MBS-08 | MBS-08 | PI12208 | Verified | 1BMBBK0014 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
MBS-08 | MBS-08 | PI12396 | Verified | 1BMBBC0081 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI12397 | Verified | 1BMBBK0001 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-20 | Mike Tabbert
MBS-08 | MBS-08 | PI12398 | Verified | 1BMBBK0013 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI12399 | Verified | 1BMBBK0014 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI13110 | Verified | BLW-M-8100A/B remake motor terms. Bolts too long | A | E | Dustin Futrell | McD | 2019-11-16 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI13111 | Verified | Blower skid - 2" condut missing plug | A | E | Dustin Futrell | McD | 2019-11-16 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI13112 | Verified | 8100B Blower unit need ground on flex | A | E | Dustin Futrell | McD | 2019-11-16 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI13113 | Verified | Duct burner skid - 2" drain plug t install on conduit. Need support near the conduit end | A | E | Dustin Futrell | McD | 2019-11-16 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI13114 | Verified | 1B-MBB-CP-8100 to clean inside panel | A | E | Dustin Futrell | McD | 2019-11-16 | Dustin Futrell | Const | 2019-11-18 | Brad Stanford | 2019-11-23 | Fred Michael
MBS-08 | MBS-08 | PI13115 | Verified | 1B-MBB-CP-8100 seal all conduits | B | E | Chris Colvin | McD | 2019-11-16 | Chris Colvin | Const | 2019-11-18 | Brad Stanford | 2019-12-18 | Mike Tabbert
MBS-08 | MBS-08 | PI13116 | Verified | Duct burner skid - pour all seal offs, to be sealed after commissioning | B | E | Chris Colvin | McD | 2019-11-16 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-02 | Mike Tabbert
MBS-08 | MBS-08 | PI13117 | Verified | 1B-MBB-CP-8100 conduits to panel to secure to the grating and tighten up fittings | A | E | Dustin Futrell | McD | 2019-11-16 | Dustin Futrell | Const | 2019-11-18 | Brad Stanford | 2019-11-23 | Fred Michael
MBS-08 | MBS-08 | PI13118 | Verified | 1B-MBB-CP-8100 condulet covers not installed | B | E | Chris Colvin | McD | 2019-11-16 | Chris Colvin | Const | 2019-11-18 | Brad Stanford | 2019-12-08 | Mike Tabbert
MBS-08 | MBS-08 | PI13120 | Verified | AOV-8120D missing solenoid valve | A | I | Gonzalo Pena | McD | 2019-11-16 | Gonzalo Pena | Const | 2019-11-23 | Gonzalo Pena | 2020-01-13 | Fred Michael
MBS-08 | MBS-08 | PI13121 | Verified | Rusty nipples need cold gal coating on JB-8002D/E/G | B | E | Dustin Futrell | McD | 2019-11-16 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI13122 | Verified | Complete ground work on all JB's | A | E | Dustin Futrell | McD | 2019-11-16 | Dustin Futrell | Const |  |  | 2019-11-18 | Mike Tabbert
MBS-08 | MBS-08 | PI13126 | Verified | FY-8118F and H, FY-8120F and H to complete solenod wiring. Replace condulet covers | A | E | Dustin Futrell | McD | 2019-11-16 | Dustin Futrell | Const |  |  | 2019-11-19 | Albert Burge
MBS-08 | MBS-08 | PI13127 | Verified | Wrong size CGB at H igniter | A | E | Chris Colvin | McD | 2019-11-16 | Chris Colvin | Const | 2019-11-21 | Dustin Futrell | 2020-01-01 | Albert Burge
MBS-08 | MBS-08 | PI13128 | Verified | 8900 JB need additional support on conduit 2/in 30" off box | C | E | Chris Colvin | McD | 2019-11-16 | Chris Colvin | Const | 2020-04-29 | Matt Gilmore | 2020-04-30 | Mike Tabbert
MBS-08 | MBS-08 | PI13129 | Verified | Complete wiring on JB-8900 | A | E | Dustin Futrell | McD | 2019-11-16 | Dustin Futrell | Const |  |  | 2019-11-19 | Fred Michael
MBS-08 | MBS-08 | PI13130 | Verified | Adjust damper limit switch target | A | M | Bobby Williams | McD | 2019-11-16 | Bobby Williams | Const | 2019-11-23 | Bobby Williams | 2020-01-01 | Albert Burge
MBS-08 | MBS-08 | PI13131 | Verified | 8900 Damper conduit cover missing | A | E | Dustin Futrell | McD | 2019-11-16 | Dustin Futrell | Const |  |  | 2019-11-19 | Fred Michael
MBS-08 | MBS-08 | PI13132 | Verified | Terminate grounds in JB-8900. | A | E | Dustin Futrell | McD | 2019-11-18 | Dustin Futrell | Const |  |  | 2019-11-19 | Fred Michael
MBS-08 | MBS-08 | PI13133 | Verified | Tag JB-8900. | C | E | Chris Colvin | McD | 2019-11-18 | Chris Colvin | Const | 2020-04-29 | Matt Gilmore | 2020-04-30 | Mike Tabbert
MBS-08 | MBS-08 | PI13135 | Verified | Complete gas duct burner gas pipe pressure test. | A | P | Bobby Williams | McD | 2019-11-18 | Bobby Williams | Const |  |  | 2019-11-22 | Michael Law
MBS-08 | MBS-08 | PI13137 | Verified | Complete skid TE installation. | A | I | Gonzalo Pena | McD | 2019-11-18 | Gonzalo Pena | Const | 2019-11-20 | Gonzalo Pena | 2019-11-20 | Michael Law
MBS-08 | MBS-08 | PI13138 | Verified | Need to dress up expanded metal screen (safety hazard) | C | P | Bobby Williams | McD | 2019-11-18 | Bobby Williams | Const | 2019-12-20 | Bobby Williams | 2019-12-23 | Michael Law
MBS-08 | MBS-08 | PI14524 | Verified | Install Catalyst | B | P | Bobby Williams | McD | 2019-12-07 | Bobby Williams | Const | 2020-02-07 | Bobby Williams | 2020-02-07 | Kelvin Cook
MBS-08 | MBS-08 | PI16039 | Open | Need to address the 4 hotspots for HRSG 1B Identified by Entergy | B | M | Bobby Williams | McD | 2020-01-14 | Bobby Williams | Const
MBS-08 | MBS-08 | PI17678 | Verified | 1B HRSG Seals - Bellows pipe penetration seals still have OEM plugs installed in the drain / vent. | B | P | Bobby Williams | McD | 2020-03-04 | Bobby Williams | Comm | 2020-03-09 | Bobby Williams | 2020-04-30 | John Watts
MHS-01 | MHS-01 | PI08200 | Verified | 5 ton crane - run conduit, install junction box & disconnect switch. | B | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2020-03-10 | Chris Colvin | 2020-03-11 | Mike Tabbert
MHS-01 | MHS-01 | PI08201 | Verified | 5 ton crane - pull & terminate un-schedule cables. | B | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2020-03-10 | Chris Colvin | 2020-03-11 | Mike Tabbert
MHS-01 | MHS-01 | PI08202 | Verified | Small jib crane - complete tie in of hoist cables to junction box. | B | E | Chris Colvin | McD | 2019-09-30 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-11 | Mike Tabbert
MHS-01 | MHS-01 | PI17141 | Verified | Need LOAD RATING sticker on center structural beam above Filter Press | C | S | Sheri Fritz | McD | 2020-02-22 | Sheri Fritz | Comm | 2020-05-19 | Bobby Williams | 2020-08-17 | Dave Goldak
MHS-01 | MHS-01 | PI17766 | Verified | 5 ton hoist on unit B air inlet need parts from MHPS | C | E | Chris Colvin | McD | 2020-03-11 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2020-04-21 | Mike Tabbert
MHS-01 | MHS-01 | PI18528 | Verified | Unit 1B, Light fixture needs to be moved on filter deck in order for hoist to rotate 360 degrees | C | E | Chris Colvin | McD | 2020-06-12 | Chris Colvin | Const | 2020-06-17 | Chris Colvin | 2020-07-10 | Mike Tabbert
MHS-01 | MHS-01 | PI18529 | Verified | Unit 1B, Tie disconnect stand to hand rail for more support filter deck hoist. | C | E | Chris Colvin | McD | 2020-06-12 | Chris Colvin | Const | 2020-06-17 | Chris Colvin | 2020-07-10 | Mike Tabbert
MHS-01 | MHS-01 | PI18530 | Verified | Unit 1B, Upper Filter deck hoist, cut tie raps from trolly chain to allow use. | C | M | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-22 | Tim Gallegos | 2020-07-10 | Mike Tabbert
MHS-01 | MHS-01 | PI18531 | Verified | Unit 1B, CTG hoist west side, hand wheel chain to long, load chain needs to be lubed, chain gets hung up in in hook. Need to run hook to lowest point to see if chain is to long. | C | M | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-07-02 | Tim Gallegos | 2021-02-01 | Dave Goldak
MHS-01 | MHS-01 | PI18532 | Verified | Unit 1A, CTG hoist west side, hand wheel chain to long, load chain needs to be lubed, chain gets hung up in in hook. Need to run hook to lowest point to see if chain is to long. | C | M | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-30 | Tim Gallegos | 2021-02-01 | Dave Goldak
MHS-01 | MHS-01 | PI18533 | Verified | Unit 1A, Filter deck hoist missing LR cover. | C | E | Chris Colvin | McD | 2020-06-12 | Chris Colvin | Const | 2020-08-14 | Chris Colvin | 2020-08-24 | Mike Tabbert
MHS-01 | MHS-01 | PI18534 | Verified | Unit 1A, Filter deck hoist shorten hand wheel chain | C | M | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-30 | Tim Gallegos | 2021-02-01 | Dave Goldak
MHS-01 | MHS-01 | PI18535 | Verified | Unit 1A and Unit 1B filter deck hoist, lube the 360 degree roller. | C | M | Tim Gallegos | McD | 2020-06-12 | Tim Gallegos | Const | 2020-06-30 | Tim Gallegos | 2021-02-01 | Dave Goldak
MHS-01 | MHS-01 | PI18536 | Verified | Unit 1A , remove rope from hoist swivel. | C | E | Chris Colvin | McD | 2020-06-12 | Chris Colvin | Const | 2020-06-17 | Chris Colvin | 2020-07-10 | Mike Tabbert
MHS-01 | MHS-01 | PI18537 | Verified | Unit 1A-A, BFP hoist missing end cap on ground bar. | B | E | Chris Colvin | McD | 2020-06-12 | Chris Colvin | Const | 2020-06-23 | Chris Colvin | 2020-07-10 | Mike Tabbert
MHS-01 | MHS-01 | PI18538 | Verified | Unit 1A-B, BFP Missing collector arm, and collector bar clips. | B | E | Chris Colvin | McD | 2020-06-12 | Chris Colvin | Const | 2020-07-10 | Mike Tabbert | 2020-07-10 | Mike Tabbert
MHS-01 | MHS-01 | PI18539 | Verified | Unit 1A, BFP remove scaffold that is not needed. | C | E | Chris Colvin | McD | 2020-06-12 | Chris Colvin | Const | 2020-06-26 | Chris Colvin | 2020-06-26 | Jason Ezell
MHS-01 | MHS-01 | PI18540 | Verified | Unit 1A and 1B BFP, Momorail does not seem to extend out far enough to get motor completely out of enclosure. | D | M | Charles Worthington | McD | 2020-06-12 | Charles Worthington | Const | 2020-07-24 | Jason Ezell | 2020-07-24 | John Watts
MSS-01 | MSS-01 | PI06605 | Verified | Install FE 1A-MSS-FE-8139 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-02-06 | Kelvin Cook
MSS-01 | MSS-01 | PI06606 | Verified | Install permanent TW 1A-MSS-TW-0020 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06607 | Verified | Gamma plug not installed at field weld 0010-02-1 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06608 | Verified | Support 1A-MSS-PD-HGR-0501 not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI06609 | Verified | Gamma plug not installed on East side of valve 1A-MSS-MOV-0050 (FW 0010-03-1) | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06610 | Verified | Replace sacrificial TW with permanent TW 1A-MSS-TW-0031 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-07 | Ethan Byrd | 2020-01-14 | Ethan Byrd
MSS-01 | MSS-01 | PI06611 | Verified | Install permanent TW 1A-MSS-TW-0040 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06612 | Verified | Gamma plug not installed at field weld 0020-01-1 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06621 | Verified | Install FE 1A-MSS-FE-0081 (AFTER STEAM BLOW) | B | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06622 | Verified | Weld incomplete on support 1A-MSS-PD-HGR-0013, loose clamp, cold-galv weld | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06623 | Verified | Valve 1A-MSS-V-0088 not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const |  |  | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06624 | Verified | Support 1A-MSS-PD-HGR-0015 not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const |  |  | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06625 | Verified | Loose clamp on support 1A-MSS-PD-HGR-0014, cold-galv welds | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06626 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06627 | Verified | INSTALL SPOOL PS-1A-MSS-P41-0010-02-151-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-02-03 | Kelvin Cook
MSS-01 | MSS-01 | PI06628 | Verified | INSTALL SPOOL PS-1A-MSS-P41-0010-03-151-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-02-03 | Kelvin Cook
MSS-01 | MSS-01 | PI06629 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const |  |  | 2019-10-03 | Alex Isaac
MSS-01 | MSS-01 | PI06630 | Verified | Line not complete | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06631 | Verified | Tag not installed on valve 1A-MSS-V-0020 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06632 | Verified | Tag not installed on valve 1A-MSS-V-0021 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06633 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06634 | Verified | Tag not installed on valve 1A-MSS-V-0040 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06635 | Verified | Tag not installed on valve 1A-MSS-V-0041 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06636 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06637 | Verified | INSTALL SPOOL PS-1A-MSS-P41-0040-03-151-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-02-06 | Kelvin Cook
MSS-01 | MSS-01 | PI06638 | Verified | INSTALL SPOOL PS-1A-MSS-P41-0040-04-151-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-02-06 | Kelvin Cook
MSS-01 | MSS-01 | PI06639 | Verified | Tag not installed on valve 1A-MSS-V-0044 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | Albert Burge | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06640 | Verified | Tag not installed on valve 1A-MSS-V-0045 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06641 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06642 | Verified | Tag not installed on valve 1A-MSS-V-0048 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06643 | Verified | Tag not installed on valve 1A-MSS-V-0049 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06644 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06645 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06646 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06647 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06648 | Verified | Support 1B-MSS-PD-HGR-0538 not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06649 | Verified | Set correct elevation on clamp per detail on support 1B-MSS-PD-HGR-0535 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06650 | Verified | Gamma plug not installed at FW 0010-01-3 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06651 | Verified | Support 1B-MSS-PD-HGR-0510 not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI06652 | Verified | Gamma plug not installed at FW 0010-01-2 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06653 | Verified | Support 1B-MSS-PD-HGR-0509 not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06654 | Verified | Set correct offset on strut per detail on support 1B-MSS-PD-HGR-0507 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06655 | Verified | Support 1B-MSS-PD-HGR-0508 not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06656 | Verified | Set support 1B-MSS-PD-HGR-0534 to correct detail | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06657 | Verified | Loose clamp on support 1B-MSS-PD-HGR-0529 | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06658 | Verified | Install FE 1B-MSS-FE-8139 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-02-06 | Kelvin Cook
MSS-01 | MSS-01 | PI06659 | Verified | Gamma plug not installed at FW 0010-03-2 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06660 | Verified | Gamma plug not installed on West side of valve 1B-MSS-MOV-0050 (FW 0010-04-2) | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06661 | Verified | Loose clamp on support 1B-MSS-PD-HGR-0525 | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06662 | Verified | Install sacrificial TW 1B-MSS-TW-0031 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06663 | Verified | Guides not installed on support 1B-MSS-PD-HGR-0527 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const |  |  | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06664 | Verified | Install permanent TW 1B-MSS-TW-0020 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06665 | Verified | Install permanent TW 1B-MSS-TW-0040 | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06666 | Verified | Guides not installed on support 1B-MSS-PD-HGR-0025 | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-12-05 | James Beech | 2019-12-09 | Shane Copeland
MSS-01 | MSS-01 | PI06667 | Verified | Guides not installed on support 1B-MSS-PD-HGR-0026, loose clamp | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-12-05 | James Beech | 2019-12-09 | Shane Copeland
MSS-01 | MSS-01 | PI06668 | Verified | Support 1B-MSS-PD-HGR-0032 not on centerline of steel | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI06669 | Verified | Support 1B-MSS-PD-HGR-0033 not on centerline of steel | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI06670 | Verified | Guides not installed on support 1B-MSS-PD-HGR-0050, loose clamp | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI06671 | Verified | Support 1B-MSS-PD-HGR-0049 not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI06672 | Verified | Support 1B-MSS-PD-HGR-0046 not installed per detail | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI06673 | Verified | Stops not installed on support 1B-MSS-PD-HGR-0043 | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI06674 | Verified | Loose clamp on support 1B-MSS-PD-HGR-0038 | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI06675 | Verified | Install FE 1B-MSS-FE-0081 (AFTER CHEMICAL CLEAN) | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-12-08 | James Beech | 2019-12-10 | Shane Copeland
MSS-01 | MSS-01 | PI06676 | Verified | Loose nuts on support 1B-MSS-PD-HGR-0051 | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI06677 | Verified | Rotate operator on valve 1B-MSS-V-0088 for accessibility | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06678 | Verified | Support 1B-MSS-PD-HGR-0053 not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06679 | Verified | Loose clamp on support 1B-MSS-PD-HGR-0052 | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI06680 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06681 | Verified | INSTALL SPOOL PS-1B-MSS-P41-0010-02-151-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-02-06 | Kelvin Cook
MSS-01 | MSS-01 | PI06682 | Verified | INSTALL SPOOL PS-1B-MSS-P41-0010-03-151-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-02-06 | Kelvin Cook
MSS-01 | MSS-01 | PI06683 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06684 | Verified | Tag not installed on valve 1B-MSS-V-0020 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06685 | Verified | Tag not installed on valve 1B-MSS-V-0021 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06686 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06687 | Verified | Tag not installed on valve 1B-MSS-V-0033 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06688 | Verified | Tag not installed on valve 1B-MSS-V-0034 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06689 | Verified | Tag not installed on valve 1B-MSS-V-0040 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06690 | Verified | Tag not installed on valve 1B-MSS-V-0041 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06691 | Verified | Tag not installed on valve 1B-MSS-V-0042 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06692 | Verified | Tag not installed on valve 1B-MSS-V-0043 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06693 | Verified | INSTALL SPOOL PS-1B-MSS-P41-0040-03-151-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-02-06 | Kelvin Cook
MSS-01 | MSS-01 | PI06694 | Verified | INSTALL SPOOL PS-1B-MSS-P41-0040-04-151-1 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-02-06 | Kelvin Cook
MSS-01 | MSS-01 | PI06695 | Verified | Tag not installed on valve 1B-MSS-V-0044 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06696 | Verified | Tag not installed on valve 1B-MSS-V-0045 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06697 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06698 | Verified | Tag not installed on valve 1B-MSS-V-0048 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06699 | Verified | Tag not installed on valve 1B-MSS-V-0049 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06700 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06701 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06702 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06703 | Verified | Line not installed | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-01 | Alex Isaac
MSS-01 | MSS-01 | PI06704 | Verified | Replace sacrificial TW with permanent TW 1C-MSS-TW-0015 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-07 | Ethan Byrd | 2020-01-14 | Ethan Byrd
MSS-01 | MSS-01 | PI06705 | Verified | Replace sacrificial TW with permanent TW 1C-MSS-TW-9013 (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-07 | Ethan Byrd | 2020-01-08 | Ethan Byrd
MSS-01 | MSS-01 | PI06706 | Verified | Nozzle 1C-MSS-NOZ-0020 not installed (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2020-02-06 | Kelvin Cook
MSS-01 | MSS-01 | PI06707 | Verified | Support 1C-MSS-PD-HGR-0523 not complete | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06708 | Verified | Replace sacrificial TW with permanent TW 1C-MSS-TW-0025A (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-07 | Ethan Byrd | 2020-01-08 | Ethan Byrd
MSS-01 | MSS-01 | PI06709 | Verified | Replace sacrificial TW with permanent TW 1C-MSS-TW-0025B (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-07 | Ethan Byrd | 2020-01-08 | Ethan Byrd
MSS-01 | MSS-01 | PI06710 | Verified | Replace sacrificial TW with permanent TW 1C-MSS-TW-0028A (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-07 | Ethan Byrd | 2020-01-08 | Ethan Byrd
MSS-01 | MSS-01 | PI06711 | Verified | Replace sacrificial TW with permanent TW 1C-MSS-TW-0028B (AFTER STEAM BLOW) | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-01-07 | Ethan Byrd | 2020-01-08 | Ethan Byrd
MSS-01 | MSS-01 | PI06712 | Verified | Remove temporary tagging | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
MSS-01 | MSS-01 | PI06713 | Verified | Shorten all-thread/tighten clevis on support 1C-MSS-PD-HGR-0022 | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI06714 | Verified | Tag not installed on valve 1C-MSS-V-0043 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06715 | Verified | Loose clamp on support 1C-MSS-PD-HGR-0117 | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI06716 | Verified | Support 1C-MSS-PD-HGR-0116 not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06717 | Verified | Support 1C-MSS-PD-HGR-0070 not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06718 | Verified | Support 1C-MSS-PD-HGR-0120 not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06719 | Verified | Weld 0016-01-4 not made | A | P | Damon Turner | McD | 2019-09-21 | Damon Turner | Const |  |  | 2019-10-05 | Alex Isaac
MSS-01 | MSS-01 | PI06720 | Verified | Tag not installed on valve 1C-MSS-V-9010A | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06721 | Verified | Tag not installed on valve 1C-MSS-V-9011A | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06722 | Verified | 1C-MSS-PIT-9010A not installed | A | I | Gonzalo Pena | McD | 2019-09-21 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MSS-01 | MSS-01 | PI06723 | Verified | 1C-MSS-PIT-9010B not installed | A | I | Gonzalo Pena | McD | 2019-09-21 | Gonzalo Pena | Const | 2019-09-26 | Gonzalo Pena | 2019-09-27 | Alex Isaac
MSS-01 | MSS-01 | PI06724 | Verified | 1C-MSS-PP-0023 not installed | A | I | Gonzalo Pena | McD | 2019-09-21 | Gonzalo Pena | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06725 | Verified | Tag not installed on valve 1C-MSS-V-0030 | C | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI06726 | Verified | Support 1C-MSS-PD-HGR-0119 not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06727 | Verified | Support 1C-MSS-PD-HGR-0118 not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const |  |  | 2019-10-09 | Alex Isaac
MSS-01 | MSS-01 | PI06728 | Verified | remove rigging from pipe | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-23 | Kelvin Cook
MSS-01 | MSS-01 | PI06729 | Verified | Pipe supports 1B-MSS-PD-HGR-0096 & 0114 are not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-09-27 | Damon Turner | 2019-11-23 | Kelvin Cook
MSS-01 | MSS-01 | PI06730 | Verified | Pipe support 1A-MSS-PD-HGr-0081 is not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-23 | Kelvin Cook
MSS-01 | MSS-01 | PI06731 | Verified | Pipe support 1C-MSS-PD-HGR-0520 eyebolt requires full thread engagement 2 or more thread | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-23 | Kelvin Cook
MSS-01 | MSS-01 | PI06732 | Verified | pipe support 1C-MSS-PD-HGr-0521 3 bolt clamp not plumb | B | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-23 | Kelvin Cook
MSS-01 | MSS-01 | PI06733 | Verified | pipe support 1C-MSS-PD-HGR-0523 | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-11-23 | Kelvin Cook
MSS-01 | MSS-01 | PI06734 | Verified | loose pipe clamp on ISO 1C-SDS-PD-P41-0017-01 | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-23 | Kelvin Cook
MSS-01 | MSS-01 | PI06735 | Verified | Valve 1C-SDS-V-9613B connection to TP-DC-27 & TP-DC-28 and connection to TP-DC-26 is not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-23 | Kelvin Cook
MSS-01 | MSS-01 | PI06736 | Verified | lines SCVL2-A & SCVL2-B are not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-18 | Michael Law | 2019-12-06 | Kelvin Cook
MSS-01 | MSS-01 | PI06737 | Verified | Valve 1C-SDS-V-9613A connection to TP-DC-12 & TP-DC-13 and connection to TP-DC-11 is not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-23 | Kelvin Cook
MSS-01 | MSS-01 | PI06738 | Verified | From valve 1C-SDS-V-9613A to the TP connection MSV-9000A/DC-11 is not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-12-06 | Kelvin Cook
MSS-01 | MSS-01 | PI06739 | Verified | Set support proper 1C-SDS-PD-HGR-0849 | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-12-06 | Kelvin Cook
MSS-01 | MSS-01 | PI06740 | Verified | Flex Too short for thermal growth 1C-SDS-MOV-9610A & 9612A & 9614A | A | E | Chris Colvin | McD | 2019-09-21 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-19 | Kelvin Cook
MSS-01 | MSS-01 | PI06741 | Verified | Support 1C-MSS-PD-HGR-0061 not installed | A | P | James Beech | McD | 2019-09-21 | James Beech | Const | 2019-11-11 | James Beech | 2019-11-24 | Alex Isaac
MSS-01 | MSS-01 | PI07059 | Verified | Set all spring cans to cold settings. | A | P | James Beech | McD | 2019-09-24 | James Beech | Const | 2019-12-20 | Bobby Williams | 2020-01-15 | Michael Law
MSS-01 | MSS-01 | PI07060 | Verified | Tag all valves. | C | P | James Beech | McD | 2019-09-24 | James Beech | Const | 2019-10-10 | James Beech | 2019-11-02 | Alex Isaac
MSS-01 | MSS-01 | PI10095 | Verified | 1AMSSC0014 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10096 | Verified | 1AMSSK0004 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10097 | Verified | 1AMSSK0005 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10098 | Verified | 1AMSSK0006 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10099 | Verified | 1AMSSX0009 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10100 | Verified | 1AMSSX0010 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10101 | Verified | 1AMSSX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10102 | Verified | 1AMSSX0012 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10103 | Verified | 1AMSSX0013 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10104 | Verified | 1AMSSX0014 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-25 | Mike Tabbert | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10105 | Verified | 1AMSSX0015 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10106 | Verified | 1AMSSX0024 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10107 | Verified | 1AMSSX0025 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-25 | Mike Tabbert | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10108 | Verified | 1AMSSX0028 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10109 | Verified | 1AMSSX0029 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10110 | Verified | 1AMSSX0030 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10111 | Verified | 1AMSSX0031 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10112 | Verified | 1AMSSX0039 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10113 | Verified | 1AMSSX0046 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10117 | Verified | 1BMSSC0002 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10118 | Verified | 1BMSSX0009 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10119 | Verified | 1BMSSX0010 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10120 | Verified | 1BMSSX0011 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10121 | Verified | 1BMSSX0014 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10122 | Verified | 1BMSSX0015 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10123 | Verified | 1BMSSX0024 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10124 | Verified | 1BMSSX0025 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10125 | Verified | 1BMSSX0030 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10126 | Verified | 1BMSSX0031 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10127 | Verified | 1BMSSX0037 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10128 | Verified | 1BMSSX0039 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10129 | Verified | 1BMSSX0041 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10130 | Verified | 1BMSSX0043 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10131 | Verified | 1BMSSX0052 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10132 | Verified | 1BMSSX0061 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10133 | Verified | 1BMSSX0062 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10144 | Verified | 1AMSSC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10145 | Verified | 1AMSSC0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10146 | Verified | 1AMSSC0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10147 | Verified | 1AMSSC0010 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10148 | Verified | 1AMSSC0011 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10149 | Verified | 1AMSSC0014 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10150 | Verified | 1AMSSC0015 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10151 | Verified | 1AMSSC0016 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10152 | Verified | 1AMSSC0017 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10153 | Verified | 1AMSSK0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10154 | Verified | 1AMSSK0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10155 | Verified | 1AMSSK0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10156 | Verified | 1AMSSK0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10157 | Verified | 1AMSSK0005 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10158 | Verified | 1AMSSK0006 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10159 | Verified | 1AMSSX0009 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10160 | Verified | 1AMSSX0010 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10161 | Verified | 1AMSSX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10162 | Verified | 1AMSSX0012 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10163 | Verified | 1AMSSX0013 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10164 | Verified | 1AMSSX0014 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10165 | Verified | 1AMSSX0015 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10166 | Verified | 1AMSSX0024 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10167 | Verified | 1AMSSX0025 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10168 | Verified | 1AMSSX0028 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10169 | Verified | 1AMSSX0029 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10170 | Verified | 1AMSSX0030 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10171 | Verified | 1AMSSX0031 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10172 | Verified | 1AMSSX0039 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10173 | Verified | 1AMSSX0041 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10174 | Verified | 1AMSSX0042 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10175 | Verified | 1AMSSX0043 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10176 | Verified | 1AMSSX0046 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10188 | Verified | 1BMSSC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10189 | Verified | 1BMSSC0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10190 | Verified | 1BMSSC0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10191 | Verified | 1BMSSC0010 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10192 | Verified | 1BMSSC0011 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10193 | Verified | 1BMSSX0009 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10194 | Verified | 1BMSSX0010 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10195 | Verified | 1BMSSX0011 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10196 | Verified | 1BMSSX0014 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10197 | Verified | 1BMSSX0015 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10198 | Verified | 1BMSSX0024 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10199 | Verified | 1BMSSX0025 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10200 | Verified | 1BMSSX0030 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10201 | Verified | 1BMSSX0031 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10202 | Verified | 1BMSSX0037 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10203 | Verified | 1BMSSX0038 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10204 | Verified | 1BMSSX0039 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10205 | Verified | 1BMSSX0040 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10206 | Verified | 1BMSSX0041 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10207 | Verified | 1BMSSX0042 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10208 | Verified | 1BMSSX0043 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10209 | Verified | 1BMSSX0044 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10210 | Verified | 1BMSSX0045 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10211 | Verified | 1BMSSX0046 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10212 | Verified | 1BMSSX0049 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10213 | Verified | 1BMSSX0050 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10214 | Verified | 1BMSSX0052 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10215 | Verified | 1BMSSX0053 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10216 | Verified | 1BMSSX0057 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10217 | Verified | 1BMSSX0061 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI10218 | Verified | 1BMSSX0062 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MSS-01 | MSS-01 | PI12163 | Verified | 1AMSSX0014 From Term | A | E | Chris Colvin | McD | 2019-10-25 | Chris Colvin | Const | 2019-10-28 | Dustin Futrell | 2019-12-06 | Mike Tabbert
MSS-01 | MSS-01 | PI12432 | Verified | 1BMSSX0014 To Term | A | E | Chris Colvin | McD | 2019-10-25 | Chris Colvin | Const | 2019-10-28 | Dustin Futrell | 2019-12-06 | Mike Tabbert
MSS-01 | MSS-01 | PI12945 | Verified | 1A-MSS-MOV-8014 - trim support that is gouging insulation. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-11 | Shannon Savoy
MSS-01 | MSS-01 | PI12946 | Verified | 1A-MSS-MOV-8014 - tighten support clamps. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-11 | Shannon Scott
MSS-01 | MSS-01 | PI13078 | Verified | Remove flush trim and install final trim and actuator on valve 1A-MSS-AOV-0086 (AFTER STEAM BLOW) | A | P | James Beech | CCI | 2019-11-15 | James Beech | Const | 2019-12-17 | James Beech | 2019-12-17 | Shane Copeland
MSS-01 | MSS-01 | PI13079 | Verified | Install Spray Nozzles on valve 1B-MSS-PV-0030 | A | P | James Beech | CCI | 2019-11-15 | James Beech | Const |  |  | 2020-01-09 | James Beech
MSS-01 | MSS-01 | PI13080 | Verified | Remove hydro trim and install final trim and actuator on valve 1A-MSS-TV-0087 (AFTER STEAM BLOW) | A | P | James Beech | CCI | 2019-11-15 | James Beech | Const | 2019-12-17 | James Beech | 2019-12-17 | Shane Copeland
MSS-01 | MSS-01 | PI13083 | Verified | Remove flush trim and install final trim and actuator on valve 1B-MSS-AOV-0086 (AFTER STEAM BLOW) | A | P | James Beech | CCI | 2019-11-15 | James Beech | Const | 2019-12-17 | James Beech | 2019-12-17 | Shane Copeland
MSS-01 | MSS-01 | PI13084 | Verified | Install blow-kit in valve 1B-MSS-PV-0030 (BEFORE STEAM BLOW) | A | P | James Beech | CCI | 2019-11-15 | James Beech | Const |  |  | 2019-11-25 | Michael Law
MSS-01 | MSS-01 | PI13085 | Verified | Remove hydro trim and install final trim and actuator on valve 1B-MSS-TV-0087 (AFTER STEAM BLOW) | A | P | James Beech | CCI | 2019-11-15 | James Beech | Const | 2019-12-17 | James Beech | 2019-12-17 | Shane Copeland
MSS-01 | MSS-01 | PI13100 | Verified | Install internals in valve 1A-MSS-CHK-8134 (AFTER STEAM BLOW) | A | P | Bobby Williams | CWX | 2019-11-15 | Bobby Williams | Const | 2020-02-02 | Bobby Williams | 2020-02-03 | Kelvin Cook
MSS-01 | MSS-01 | PI13101 | Verified | Install internals in valve 1B-MSS-CHK-8134 (AFTER STEAM BLOW) | A | P | Bobby Williams | CWX | 2019-11-15 | Bobby Williams | Const | 2020-02-02 | Bobby Williams | 2020-02-03 | Kelvin Cook
MSS-01 | MSS-01 | PI12896 | Verified | Install 1A-MSS-TE-8005A (cut insulation). | A | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-12-03 | James Tanner | 2019-12-19 | Albert Burge
MSS-01 | MSS-01 | PI12897 | Verified | Run conduit to 1A-MSS-TE-8005A. | A | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-08 | Mike Tabbert
MSS-01 | MSS-01 | PI12898 | Verified | Install 1A-MSS-TE-8005B (cut insulation). | A | I | Gonzalo Pena | McD | 2019-11-13 | Gonzalo Pena | Const | 2019-12-03 | James Tanner | 2019-12-19 | Albert Burge
MSS-01 | MSS-01 | PI12899 | Verified | Run conduit to 1A-MSS-TE-8005B. | A | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2019-11-27 | Brad Stanford | 2019-12-08 | Mike Tabbert
MSS-01 | MSS-01 | PI13232 | Verified | Pipe Support Number: 1A-MSS-PD-HGR-0503: Ref. Iso. LK-1A-MSS-PD-P40-0010-02: Loose Jam Nut below Load Coupling at Spring. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-05 | James Beech | 2020-01-09 | Kelvin Cook
MSS-01 | MSS-01 | PI13233 | Verified | Pipe Support Number: 1B-MSS-PD-HGR-0510: Ref. Iso. LK-1B-MSS-PD-P40-0010-01: Hanger Rod Is Disconnected above the Turnbuckle. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-05 | James Beech | 2019-12-12 | Gary Pickeral
MSS-01 | MSS-01 | PI13234 | Verified | Pipe Support Number: 1B-MSS-PD-HGR-0508: Ref. Iso. LK-1B-MSS-PD-P40-0010-02: Hanger is not Offset 6 1/2" as Designed. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-08 | James Beech | 2020-01-06 | Ethan Byrd
MSS-01 | MSS-01 | PI13235 | Verified | Pipe Support Number: 1B-MSS-PD-HGR-0509: Ref. Iso. LK-1B-MSS-PD-P40-0010-02: Loose Jam Nut Above Turnbuckle | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-05 | James Beech | 2020-01-06 | Ethan Byrd
MSS-01 | MSS-01 | PI13236 | Verified | Pipe Support Number: 1B-MSS-PD-HGR-0515: Ref. Iso. LK-1B-MSS-PD-P40-0020-01; Shock Absorvber, Installed Extension = 5 1/2". However, 6 1/4" Extension is Required. Therefore, Compress 3/4" minumum, Extend Threaded Paddle an equal amount and Re-Pin. | B | P | James Beech | McD | 2019-11-20 | James Beech | Const | 2019-12-05 | James Beech | 2019-12-19 | Gary Pickeral
MSS-01 | MSS-01 | PI13509 | Verified | Remove Steam Blow Pipe | B | P | James Beech | McD | 2019-11-24 | James Beech | Const | 2020-02-07 | James Beech | 2020-02-07 | Kelvin Cook
MSS-01 | MSS-01 | PI13882 | Verified | 1A-MSS-FIT-8139 - complete tubing. STG ground level. | A | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Const | 2020-02-12 | James Tanner | 2020-02-19 | Albert Burge
MSS-01 | MSS-01 | PI13883 | Verified | 1A-MSS-FIT-0081 - complete tubing. STG ground level. | A | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Const | 2020-01-03 | Gonzalo Pena | 2020-01-09 | Albert Burge
MSS-01 | MSS-01 | PI13884 | Verified | 1B-MSS-FIT-0081 - complete tubing. STG ground level. | A | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Const | 2020-01-03 | Gonzalo Pena | 2020-01-09 | Albert Burge
MSS-01 | MSS-01 | PI13885 | Verified | Level up & weld support for 1A-HTS-CAB-0302. STG ground level. | B | E | Chris Colvin | McD | 2019-12-03 | Chris Colvin | Const | 2019-12-09 | Brad Stanford | 2020-01-08 | Mike Tabbert
MSS-01 | MSS-01 | PI13886 | Verified | 1C-MSS-AOV-0040 - complete tubing. STG mezz. | A | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Const | 2019-12-06 | James Tanner | 2019-12-19 | Albert Burge
MSS-01 | MSS-01 | PI13887 | Verified | Missing condulet cover at 1C-MSS-TE-0040. STG mezz. | B | E | Chris Colvin | McD | 2019-12-03 | Chris Colvin | Const |  |  | 2019-12-17 | Fred Michael
MSS-01 | MSS-01 | PI13888 | Verified | 1C-MSS-AOV-0030 - complete tubing. STG mezz. | A | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Const |  |  | 2019-12-20 | Michael Law
MSS-01 | MSS-01 | PI13889 | Verified | 1B-MSS-AOV-0040- replace damaged regulator / solenoid. | A | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Const | 2019-12-07 | James Tanner | 2019-12-19 | Albert Burge
MSS-01 | MSS-01 | PI13890 | Verified | Install 1A-MSS-MOV-1052. | A | P | James Beech | McD | 2019-12-03 | James Beech | Const | 2019-12-09 | James Beech | 2019-12-10 | Mike Tabbert
MSS-01 | MSS-01 | PI13891 | Verified | Install 1B-MSS-MOV-1052. | A | P | James Beech | McD | 2019-12-03 | James Beech | Const | 2019-12-09 | James Beech | 2019-12-10 | Mike Tabbert
MSS-01 | MSS-01 | PI13892 | Verified | 1A-MSS-MOV-0050 - redo terminations in MOV termination box. | A | E | Chris Colvin | McD | 2019-12-03 | Chris Colvin | Const | 2019-12-05 | Brad Stanford | 2019-12-10 | Mike Tabbert
MSS-01 | MSS-01 | PI13893 | Verified | 1B-MSS-MOV-0050 - one wire nicked in MOV termination box. | A | E | Chris Colvin | McD | 2019-12-03 | Chris Colvin | Const | 2019-12-10 | Chris Colvin | 2019-12-14 | Mike Tabbert
MSS-01 | MSS-01 | PI13894 | Verified | 1A-MSS-FE-0081 - plug spare taps. | A | P | James Beech | McD | 2019-12-03 | James Beech | Const | 2019-12-08 | James Beech | 2019-12-19 | Albert Burge
MSS-01 | MSS-01 | PI13895 | Verified | 1B-MSS-FE-0081 - plug spare taps. | A | P | James Beech | McD | 2019-12-03 | James Beech | Const | 2019-12-08 | James Beech | 2019-12-19 | Albert Burge
MSS-01 | MSS-01 | PI14035 | Verified | 1AMSSX0036, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
MSS-01 | MSS-01 | PI14036 | Verified | 1AMSSX0037, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
MSS-01 | MSS-01 | PI14037 | Verified | 1AMSSX0039, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
MSS-01 | MSS-01 | PI14038 | Verified | 1AMSSX0045, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
MSS-01 | MSS-01 | PI14039 | Verified | 1BMSSX0009, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
MSS-01 | MSS-01 | PI14040 | Verified | 1BMSSX0027, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
MSS-01 | MSS-01 | PI14041 | Verified | 1BMSSX0039, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
MSS-01 | MSS-01 | PI14042 | Verified | 1BMSSX0041, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14043 | Verified | 1CMSSX0002, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14044 | Verified | 1AMSSC0003, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
MSS-01 | MSS-01 | PI14045 | Verified | 1AMSSC0011, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-10 | Chris Colvin | 2019-12-14 | Mike Tabbert
MSS-01 | MSS-01 | PI14046 | Verified | 1AMSSK0002, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-14 | Mike Tabbert | 2019-12-18 | Mike Tabbert
MSS-01 | MSS-01 | PI14047 | Verified | 1AMSSX0004, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Alonso Guarisma | 2019-12-16 | Mike Tabbert
MSS-01 | MSS-01 | PI14048 | Verified | 1AMSSX0009, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14049 | Verified | 1AMSSX0036, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14050 | Verified | 1AMSSX0037, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
MSS-01 | MSS-01 | PI14051 | Verified | 1AMSSX0039, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
MSS-01 | MSS-01 | PI14052 | Verified | 1AMSSX0045, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-10 | Chris Colvin | 2019-12-18 | Mike Tabbert
MSS-01 | MSS-01 | PI14053 | Verified | 1AMSSX0046, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
MSS-01 | MSS-01 | PI14054 | Verified | 1BMSSC0003, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
MSS-01 | MSS-01 | PI14055 | Verified | 1BMSSC0011, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-10 | Chris Colvin | 2019-12-14 | Mike Tabbert
MSS-01 | MSS-01 | PI14056 | Verified | 1BMSSK0002, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-10 | Chris Colvin | 2019-12-18 | Mike Tabbert
MSS-01 | MSS-01 | PI14057 | Verified | 1BMSSX0027, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
MSS-01 | MSS-01 | PI14058 | Verified | 1BMSSX0038, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14059 | Verified | 1BMSSX0039, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
MSS-01 | MSS-01 | PI14060 | Verified | 1BMSSX0041, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14061 | Verified | 1BMSSX0045, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-18 | Mike Tabbert
MSS-01 | MSS-01 | PI14062 | Verified | 1BMSSX0046, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
MSS-01 | MSS-01 | PI14063 | Verified | 1CMSSX0002, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14066 | Verified | 1CSDSC0005, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14073 | Verified | 1CSDSC0015, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14074 | Verified | 1CSDSC0016, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14075 | Verified | 1CSDSC0017, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14078 | Verified | 1CSDSC0020, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14079 | Verified | 1CSDSC0021, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14080 | Verified | 1CSDSC0022, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14081 | Verified | 1CSDSC0023, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14082 | Verified | 1CSDSC0025, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14083 | Verified | 1CSDSC0027, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14089 | Verified | 1CSDSK0002, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14090 | Verified | 1CSDSK0003, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14091 | Verified | 1CSDSK0004, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14092 | Verified | 1CSDSK0005, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14093 | Verified | 1CSDSK0006, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14094 | Verified | 1CSDSK0007, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14064 | Verified | 1CSDSC0001, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14065 | Verified | 1CSDSC0003, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
MSS-01 | MSS-01 | PI14681 | Verified | 1BMSSX0037, To Termination | A | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-18 | Mike Tabbert
MSS-01 | MSS-01 | PI14705 | Verified | 1C-MSS-PIT-9010A-GROUND WIRE IS LOOSE ON FLEX. | A | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const | 2019-12-12 | John Sullivan | 2019-12-12 | John Sullivan
MSS-01 | MSS-01 | PI14706 | Verified | 1C-MSS-PIT-9010B-GROUND WIRE IS LOOSE ON FLEX. | A | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const | 2019-12-12 | John Sullivan | 2019-12-12 | John Sullivan
MSS-01 | MSS-01 | PI14707 | Verified | 1A-HTS-CAB-0302-FLEX CONNECTORS ARE LOOSE(NE CORNER OF STG) | C | E | Chris Colvin | McD | 2019-12-11 | Chris Colvin | Const | 2020-04-16 | Matt Gilmore | 2020-04-20 | Michael Law
MSS-01 | MSS-01 | PI14708 | Verified | 1C-HTS-CAB-0202-NEEDS TO BE CLEANED OUT GOOD. | B | I | James Tanner | McD | 2019-12-11 | James Tanner | Const | 2019-12-13 | Gonzalo Pena | 2019-12-14 | John Sullivan
MSS-01 | MSS-01 | PI14709 | Verified | 1A-MSS-FIT-8139- COVER IS VERY HARD TO REMOVE. NEEDS SOME ATTENTION. | C | I | James Beech | McD | 2019-12-11 | James Beech | Const | 2020-04-06 | Michael Law | 2020-04-06 | Michael Law
MSS-01 | MSS-01 | PI14710 | Verified | 1A-MSS-FIT-0081-NEED TO INSTALL INSTRUMENT I.D. TAG | C | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-13 | John Sullivan
MSS-01 | MSS-01 | PI14711 | Verified | 1B-MSS-FIT-0081-NEED TO INSTALL INSTRUMENT I.D. TAG | C | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-13 | John Sullivan
MSS-01 | MSS-01 | PI14713 | Verified | 1B-MSS-PD-P41-0016-01: 1B-MSS-HGR-0096 was located on 12/7/19. Verify the installed spring can is correct. | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-13 | Bobby Williams | 2019-12-15 | Kelvin Cook
MSS-01 | MSS-01 | PI14714 | Verified | 1B-MSS-PD-P41-0052-02: 1B-MSS-HGR-0131 was located on 12/7/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-15 | Bobby Williams | 2019-12-15 | Kelvin Cook
MSS-01 | MSS-01 | PI14726 | Verified | 1B-MSS-PD-P41-0036-01: 1B-MSS-HGR-0115 was located on 12/9/19 and needs to be installed. | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-15 | Bobby Williams | 2019-12-15 | Kelvin Cook
MSS-01 | MSS-01 | PI14819 | Verified | 1A-MSS-PIT-0030-WHITE WIRE IN TRANSMITTER HAS A NICK ON IT.(1A-HTS-CAB-0313) | A | E | James Tanner | McD | 2019-12-15 | James Tanner | Const | 2019-12-16 | Jared Stimpson | 2019-12-17 | John Sullivan
MSS-01 | MSS-01 | PI14820 | Verified | NEED TO INSTALL I.D. TAG ON 1A-MSS-PIT-0030(1A-HTS-CAB-0313) | C | I | James Tanner | McD | 2019-12-15 | James Tanner | Const |  |  | 2019-12-17 | John Sullivan
MSS-01 | MSS-01 | PI14821 | Verified | NEED TO INSTALL TUBE BUNDLE FOR 1A-MSS-PIT-0030(1A-HTS-CAB-0313) | A | I | James Tanner | McD | 2019-12-15 | James Tanner | Const |  |  | 2019-12-21 | John Sullivan
MSS-01 | MSS-01 | PI15837 | Verified | Install Condensing Pot (2 each) 1A-MSS-FIT-8139 | B | P | James Beech | McD | 2020-01-09 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
MSS-01 | MSS-01 | PI15838 | Verified | Install Condensing Pot (2 each) 1B-MSS-FIT-8139 | B | P | James Beech | McD | 2020-01-09 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
MSS-01 | MSS-01 | PI16031 | Verified | Install Final Trim on valve 1B-MSS-PV-0030 | A | P | James Beech | McD | 2020-01-14 | James Beech | Const | 2020-02-02 | James Beech | 2020-02-03 | Kelvin Cook
MSS-01 | MSS-01 | PI16033 | Verified | Install Final Trim on valve 1C-LPS-PV-0020 | A | P | James Beech | McD | 2020-01-14 | James Beech |  |  |  | 2020-01-14 | Michael Law
MSS-01 | MSS-01 | PI16037 | Verified | Install Final Trim on valve 1C-STS-MSV-9000A | A | P | Shane Crowe | McD | 2020-01-14 | Shane Crowe | Const | 2020-02-03 | Shane Crowe | 2020-02-03 | Kelvin Cook
MSS-01 | MSS-01 | PI16038 | Verified | Install Final Trim on valve 1C-STS-MSV-9000B | A | P | Shane Crowe | McD | 2020-01-14 | Shane Crowe | Const | 2020-02-03 | Shane Crowe | 2020-02-03 | Kelvin Cook
MSS-01 | MSS-01 | PI16692 | Verified | 1B-MSS-V-8140 & 1B-MSS-V-8141 - 1B HP Superheater No. 1 and HP Superheater No. 2 crossover piping vent valves, are leaking by. | B | P | Bobby Williams | McD | 2020-02-10 | Bobby Williams | Comm | 2020-02-13 | Bobby Williams | 2020-04-06 | Bernard Stasse
MSS-01 | MSS-01 | PI17197 | Verified | 1B-MSS-PIT-0030 Tube leak repair | A | I | Gonzalo Pena | McD | 2020-02-25 | Gonzalo Pena | Const | 2020-03-04 | Tim Green | 2020-03-07 | Albert Burge
MSS-01 | MSS-01 | PI17198 | Verified | 1B-HRS-PIT-0030 Tube leak repair | A | I | Gonzalo Pena | McD | 2020-02-25 | Gonzalo Pena | Const | 2020-03-04 | Tim Green | 2020-03-07 | Albert Burge
MSS-01 | MSS-01 | PI17448 | Verified | 1B-MSS-PIT-0030 is leaking and needs to be repaired. It is welded, needs to be cut and swaged. | B | I | James Beech | McD | 2020-03-02 | James Beech | Comm | 2020-03-07 | Albert Burge | 2020-03-07 | Albert Burge
MSS-01 | MSS-01 | PI17835 | Verified | HP steam to aux steam spray does not control in AUTO | C | I | Mike Wilferd | McD | 2020-03-16 | Mike Wilferd | Const | 2020-04-30 | Alan Joiner | 2020-06-03 | Chase Courtade
MWS-01 | MWS-01 | PI04603 | Verified | Install stilling well for 10-MWS-LIT-600 at back wastewater sump | A | I | Gonzalo Pena | McD | 2019-08-24 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
MWS-01 | MWS-01 | PI04604 | Verified | Install stilling well for 10-MWS-LIT-700 at filtered Water clearwell sump | A | I | Gonzalo Pena | McD | 2019-08-24 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
MWS-01 | MWS-01 | PI06032 | Verified | LK-10-MWS-PD-P40-0043-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06033 | Verified | LK-10-MWS-PD-P40-0044-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06034 | Verified | LK-10-MWS-PD-P40-0120-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06035 | Verified | LK-10-MWS-PD-P40-0120-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06036 | Verified | LK-10-MWS-PD-P40-0125-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06037 | Verified | LK-10-MWS-PD-P40-0550-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06038 | Verified | LK-10-MWS-PD-P40-0550-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06039 | Verified | LK-10-MWS-PD-P40-1010-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06040 | Verified | LK-10-MWS-PD-P40-1010-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06041 | Verified | LK-10-MWS-PD-P40-1010-03 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06042 | Verified | LK-10-MWS-PD-P40-1010-04 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06043 | Verified | LK-10-MWS-PD-P40-1010-05 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06044 | Verified | LK-10-MWS-PD-P40-1010-06 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06045 | Verified | LK-10-MWS-PD-P40-1014-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06046 | Verified | LK-10-MWS-PD-P40-1014-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06047 | Verified | LK-10-MWS-PD-P40-1410-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06048 | Verified | LK-10-MWS-PD-P40-1418-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06049 | Verified | LK-10-MWS-PD-P40-1420-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06050 | Verified | LK-10-MWS-PD-P41-0010-03 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06051 | Verified | LK-10-MWS-PD-P41-0043-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06052 | Verified | LK-10-MWS-PD-P41-0043-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06053 | Verified | LK-10-MWS-PD-P41-0043-03 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06054 | Verified | LK-10-MWS-PD-P41-0044-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06055 | Verified | LK-10-MWS-PD-P41-0044-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06056 | Verified | LK-10-MWS-PD-P41-0044-03 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06057 | Verified | LK-10-MWS-PD-P41-0047-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06058 | Verified | LK-10-MWS-PD-P41-0047-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06059 | Verified | LK-10-MWS-PD-P41-0110-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06060 | Verified | LK-10-MWS-PD-P41-0120-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06061 | Verified | LK-10-MWS-PD-P41-0125-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06062 | Verified | LK-10-MWS-PD-P41-0135-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06063 | Verified | LK-10-MWS-PD-P41-0230-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06064 | Verified | LK-10-MWS-PD-P41-0230-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06065 | Verified | LK-10-MWS-PD-P41-0230-03 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06066 | Verified | LK-10-MWS-PD-P41-0230-04 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06067 | Verified | LK-10-MWS-PD-P41-0271-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06068 | Verified | LK-10-MWS-PD-P41-0271-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06069 | Verified | LK-10-MWS-PD-P41-0273-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06070 | Verified | LK-10-MWS-PD-P41-0275-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06071 | Verified | LK-10-MWS-PD-P41-0550-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06072 | Verified | LK-10-MWS-PD-P41-1013-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06073 | Verified | LK-10-MWS-PD-P41-1333-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06074 | Verified | LK-10-MWS-PD-P41-1333-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06075 | Verified | LK-10-MWS-PD-P41-1400-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06076 | Verified | LK-10-MWS-PD-P41-1400-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06077 | Verified | LK-10-MWS-PD-P41-1400-03 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06078 | Verified | LK-10-MWS-PD-P41-1400-04 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06079 | Verified | LK-10-MWS-PD-P41-1402-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06080 | Verified | LK-10-MWS-PD-P41-1402-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06081 | Verified | LK-10-MWS-PD-P41-1404-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06082 | Verified | LK-10-MWS-PD-P41-1404-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06083 | Verified | LK-10-MWS-PD-P41-1404-03 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06084 | Verified | LK-10-MWS-PD-P41-1404-04 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06085 | Verified | LK-10-MWS-PD-P41-1406-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06086 | Verified | LK-10-MWS-PD-P41-1406-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06087 | Verified | LK-10-MWS-PD-P41-1406-03 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06088 | Verified | LK-10-MWS-PD-P41-1408-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06089 | Verified | LK-10-MWS-PD-P41-1408-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06090 | Verified | LK-10-MWS-PD-P41-1408-03 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06091 | Verified | LK-10-MWS-PD-P41-1408-04 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06092 | Verified | LK-10-MWS-PD-P41-1408-05 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06093 | Verified | LK-10-MWS-PD-P41-1408-06 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI06094 | Verified | LK-10-MWS-PD-P41-1408-07 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Michael Law
MWS-01 | MWS-01 | PI07245 | Verified | Grout all equipment. | A | C | Johnny Campbell | McD | 2019-09-26 | Johnny Campbell | Const | 2019-10-22 | Johnny Campbell | 2019-11-13 | Joshua Sturgeon
MWS-01 | MWS-01 | PI07246 | Verified | Grout all supports. | C | C | Johnny Campbell | McD | 2019-09-26 | Johnny Campbell | Const | 2019-10-22 | Johnny Campbell | 2019-11-13 | Joshua Sturgeon
MWS-01 | MWS-01 | PI07247 | Verified | Provide additonal plate / guard for the clarifier disc filter motors 10-MWS-M-0510A & B. | A | M | Shane Crowe | McD | 2019-09-26 | Shane Crowe | Const | 2019-10-01 | Joshua Sturgeon | 2019-10-03 | Shannon Scott
MWS-01 | MWS-01 | PI07248 | Verified | Complete all disc filter anchor bolting. | A | M | Shane Crowe | McD | 2019-09-26 | Shane Crowe | Const | 2019-10-01 | Joshua Sturgeon | 2019-10-01 | Joshua Sturgeon
MWS-01 | MWS-01 | PI07249 | Verified | On the south side of the disc filters there are two flange connections in contact with each other. | B | P | Kelvin Cook | McD | 2019-09-26 | Kelvin Cook | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07250 | Verified | Instal valve chain operators at valves 10-MWS-V-0024, 0025, 0026 the disc filters. | B | P | James Beech | McD | 2019-09-26 | James Beech | Const | 2019-12-09 | James Beech | 2019-12-11 | Shannon Scott
MWS-01 | MWS-01 | PI07251 | Verified | Clean up carbon contamination on the disc filters. | C | X | Jerry Smith | McD | 2019-09-26 | Jerry Smith | Const | 2020-03-18 | Johnny Campbell | 2020-04-08 | Bernard Stasse
MWS-01 | MWS-01 | PI07252 | Verified | Install safety gate on the clarifier disc filter platform. | B | S | Bobby Williams | McD | 2019-09-26 | Bobby Williams | Const | 2019-10-04 | Bobby Williams | 2019-10-15 | Shannon Scott
MWS-01 | MWS-01 | PI07253 | Verified | Install coupling guard on pumps 10-MWS-P-0600A & B. | A | M | Shane Crowe | McD | 2019-09-26 | Shane Crowe | Const | 2019-09-27 | Shane Crowe | 2019-10-03 | Shannon Scott
MWS-01 | MWS-01 | PI07254 | Verified | Tag all valves. | C | P | James Beech | McD | 2019-09-26 | James Beech | Const | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
MWS-01 | MWS-01 | PI07255 | Verified | Landing pad for the clarifier disc filter ladder needs to be extended out. | C | C | Jorge Alexander | McD | 2019-09-26 | Jorge Alexander | Const | 2019-11-21 | Johnny Campbell | 2019-12-11 | Shannon Scott
MWS-01 | MWS-01 | PI07256 | Verified | Complete anchor bolts on 10-MWS-P-0100A & B. | A | M | Shane Crowe | McD | 2019-09-26 | Shane Crowe | Const | 2019-09-27 | Shane Crowe | 2019-10-03 | Joshua Sturgeon
MWS-01 | MWS-01 | PI07257 | Verified | Install coupling guard on pumps 10-MWS-P-0100A & B. | A | M | Shane Crowe | McD | 2019-09-26 | Shane Crowe | Const | 2019-10-03 | Shane Crowe | 2019-10-15 | Shannon Scott
MWS-01 | MWS-01 | PI07258 | Verified | Rotate drain valves on 10-MWS-P-0100A & B. Cannot fully open. | A | P | James Beech | McD | 2019-09-26 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-11-07 | J.L. Bickham
MWS-01 | MWS-01 | PI07259 | Verified | Install coupling guard on 10-MWS-P-0400A & B. | A | M | Shane Crowe | McD | 2019-09-26 | Shane Crowe | Const | 2019-10-03 | Shane Crowe | 2019-10-15 | Shannon Scott
MWS-01 | MWS-01 | PI07260 | Verified | Verify tagging on sludge transfer equip., valves, instruments (A vs B tags). | B | M | Joshua Sturgeon | McD | 2019-09-26 | Joshua Sturgeon | Const | 2019-10-18 | Joshua Sturgeon | 2019-10-18 | Joshua Sturgeon
MWS-01 | MWS-01 | PI07261 | Verified | 10-MWS-PI-0131A at the sand recirc. Pump gets plugged during operations. | D | I | Michael Law | McD | 2019-09-26 | Michael Law | Const | 2019-11-08 | James Tanner | 2020-01-13 | Fred Michael
MWS-01 | MWS-01 | PI07262 | Verified | Flange at 10-MWS-V-0130 at sludge tank missing bolts. | A | P | James Beech | McD | 2019-09-26 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-11-07 | J.L. Bickham
MWS-01 | MWS-01 | PI07263 | Verified | Complete all clean & closures. | A | M | Shane Crowe | McD | 2019-09-26 | Shane Crowe | Const | 2019-11-11 | Shane Crowe | 2019-11-11 | Joshua Sturgeon
MWS-01 | MWS-01 | PI07264 | Verified | Complete 10-MWS-T-0400 trim. | A | P | James Beech | McD | 2019-09-26 | James Beech | Const | 2019-11-06 | James Beech | 2019-11-13 | Joshua Sturgeon
MWS-01 | MWS-01 | PI07265 | Verified | Complete 10-MWS-T-0400 trim. | A | P | James Beech | McD | 2019-09-26 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-11-13 | Joshua Sturgeon
MWS-01 | MWS-01 | PI07266 | Verified | Grind down & plug unused conduit at ladder on the clarifier caustic platform. | C | E | Dustin Futrell | McD | 2019-09-26 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI07267 | Verified | 10-MWS-CP-0230 - clarifier caustic panel door locking tab broken. | C | E | Mike Tabbert | McD | 2019-09-26 | Mike Tabbert | Const | 2020-01-13 | Shannon Scott | 2020-01-13 | Shannon Scott
MWS-01 | MWS-01 | PI07268 | Verified | 10-MWS-HOP-0310 - top housing bent. | B | M | Joshua Sturgeon | McD | 2019-09-26 | Joshua Sturgeon | Const | 2019-10-18 | Joshua Sturgeon | 2019-10-24 | Shannon Scott
MWS-01 | MWS-01 | PI07269 | Verified | Complete polymer heater 10-MWS-H-0310 installation. | A | M | Shane Crowe | McD | 2019-09-26 | Shane Crowe | Const | 2019-10-01 | Joshua Sturgeon | 2019-10-01 | Joshua Sturgeon
MWS-01 | MWS-01 | PI07270 | Verified | Clean & locate drain in the polymer mixing tank containment sump. | A | C | Johnny Campbell | McD | 2019-09-26 | Johnny Campbell | Const | 2019-10-10 | Johnny Campbell | 2019-10-15 | Shannon Scott
MWS-01 | MWS-01 | PI07271 | Verified | Sodium hypochlorite storage tank ladder missing gate at top. | D | S | Michael Law | McD | 2019-09-26 | Michael Law | Const | 2020-05-11 | Michael Law | 2020-12-03 | Dave Goldak
MWS-01 | MWS-01 | PI07272 | Verified | Clarifier coagulant storage tank ladder missing gate at top. | D | S | Michael Law | McD | 2019-09-26 | Michael Law | Const | 2020-05-11 | Michael Law | 2020-12-03 | Dave Goldak
MWS-01 | MWS-01 | PI07273 | Verified | Complete installation of sodium hypochlorite tank guides. | B | M | Shane Crowe | McD | 2019-09-26 | Shane Crowe | Const | 2019-11-11 | Shane Crowe | 2019-11-13 | Shannon Scott
MWS-01 | MWS-01 | PI07274 | Verified | Tighten anchor bolts on the clarifer coagulant tank. | B | M | Shane Crowe | McD | 2019-09-26 | Shane Crowe | Const | 2019-09-27 | Shane Crowe | 2019-11-07 | J.L. Bickham
MWS-01 | MWS-01 | PI07275 | Verified | Seal unused bolt holes in the clarifier coagulant tank containment. | A | C | Johnny Campbell | McD | 2019-09-26 | Johnny Campbell | Const | 2019-10-03 | Johnny Campbell | 2019-11-13 | Joshua Sturgeon
MWS-01 | MWS-01 | PI07276 | Verified | Housekeeping / cleanup needed in all tank containments. | C | C | Jorge Alexander | McD | 2019-09-26 | Jorge Alexander | Const |  |  | 2020-01-30 | Albert Burge
MWS-01 | MWS-01 | PI07277 | Verified | Header between clarifier & disc filter - verify lack of vents. | D | P | Michael Law | McD | 2019-09-26 | Michael Law | Const | 2020-04-02 | Michael Law | 2020-04-07 | Bernard Stasse
MWS-01 | MWS-01 | PI07278 | Verified | ISO 10-CWS-PD-P40-0100-01 Instrument 10-CWS-AE-0013 & 10-CWS-AE-0014 are not installed | A | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-10-03 | Kelvin Cook
MWS-01 | MWS-01 | PI07279 | Verified | ISO 10-CWS-PD-P40-0100-01 flange connection to instrument 10-CWS-FE-0012 needs 2 gaskets and missing 1 bolt | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07280 | Verified | ISO 10-CWS-PD-P41-0100-03 install bird screen | B | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-12-17 | Bobby Williams | 2019-12-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07281 | Verified | ISO 10-MWS-PD-P40-0010-03 Valve 10-MWS-FV-0016 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07282 | Verified | ISO 10-MWS-PD-P40-0025-01 missing handle on valve 10-MWS-V-0025 | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07283 | Verified | ISO 10-MWS-PD-P40-0026-01 flange to connection to 10-MWS-V-0026 missing cap screws | B | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07284 | Verified | ISO 10-MWS-PD-P40-0026-01 missing handle on valve 10-MWS-V-0026 | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07285 | Verified | ISO 10-MWS-PD-P40-0026-01 spool 0026-1 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07286 | Verified | ISO 10-MWS-PD-P40-0030-01 flange connection to 10-MWS-V-0034 missing cap screws | B | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07287 | Verified | ISO 10-MWS-PD-P40-0030-01 flange connection to 10-MWS-FLT-0500A/T missing cap screws | B | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07288 | Verified | ISO 10-MWS-PD-P40-0030-01 roate valve 10-MWS-V-0034 | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07289 | Verified | ISO 10-MWS-PD-P40-0030-01 missing valve handle on valve 10-MWS-V-0036 | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07290 | Verified | ISO 10-MWS-PD-P40-0041-01 missing handle at valve 10-MWS-V-0807 & 10-MWS-V-0023A | A | P | Damon Turner | McD | 2019-09-27 | Damon Turner | Const | 2019-09-30 | Damon Turner | 2019-09-30 | Kelvin Cook
MWS-01 | MWS-01 | PI07291 | Verified | ISO 10-MWS-PD-P40-0041-01 pipe support 10-MWS-PD-HGR-0023 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07292 | Verified | ISO 10-MWS-PD-P40-0041-01 missing cap screws at both valve 10-MWS-V-0807 & 10-MWS-V-0023A | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07293 | Verified | ISO 10-MWS-PD-P40-0041-01 connection to 10-MWS-CLR-0100/T70 is not completed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07294 | Verified | ISO 10-MWS-PD-P40-0042-01 pipe support 10-MWS-PD-HGR-0025 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07295 | Verified | ISO 10-MWS-PD-P40-0042-01 missing valve handle on 10-MWS-V-0023B | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07296 | Verified | ISO 10-MWS-PD-P40-0042-01 missing 4 caps screws on 10-MWS-V-0023B | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07297 | Verified | ISO 10-MWS-PD-P40-0043-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07298 | Verified | ISO 10-MWS-PD-P40-0043-02 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07299 | Verified | ISO 10-MWS-PD-P40-0043-03 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07300 | Verified | ISO 10-MWS-PD-P40-0044-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07301 | Verified | ISO 10-MWS-PD-P40-0044-02 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07302 | Verified | ISO 10-MWS-PD-P40-0044-03 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07303 | Verified | ISO 10-MWS-PD-P40-0047-03 missing cap screws at flange connection to valve 10-MWS-V-0046 | B | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07304 | Verified | ISO 10-MWS-PD-P40-0047-03 replace gasket at the UG connection | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07305 | Verified | ISO 10-MWS-PD-P40-0047-04 missing cap screws at flange connection to valve 10-MWS-V-0046 | B | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07306 | Verified | ISO 10-MWS-PD-P40-0047-04 adjust bolts properly and all correct length on 10-MWS-PV-0045 | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07307 | Verified | ISO 10-MWS-PD-P40-0070-01 at the UG connection anti seize bolts | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07308 | Verified | ISO 10-MWS-PD-P40-0100-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07309 | Verified | ISO 10-MWS-PD-P40-0104-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07310 | Verified | ISO 10-MWS-PD-P40-0108-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07311 | Verified | ISO 10-MWS-PD-P40-0110-01 pipe support 10-MWS-PD-HGR-0012 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07312 | Verified | ISO 10-MWS-PD-P40-0110-01 valves 10-MWS-V-0100A & 0111B are not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07313 | Verified | ISO 10-MWS-PD-P40-0110-02 add shim to pipe supports 10-MWS-PD-HGR-0014 & 0015 & 0016 | B | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07314 | Verified | ISO 10-MWS-PD-P40-0110-02 pipe supports 10-MWS-PD-HGR-0013 has no ubolt installed | B | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07315 | Verified | ISO 10-MWS-PD-P40-0110-02 instrument 10-MWS-FE-0113 is not installed | B | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07316 | Verified | ISO 10-MWS-PD-P40-0110-02 instrument 10-MWS-FE-0113 is not installed | B | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07317 | Verified | ISO 10-MWS-PD-P40-0110-02 wrong space at instrument 10-MWS-FE-0113 | B | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07318 | Verified | ISO 10-MWS-PD-P40-0110-03 pipe spool 0110-1 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07319 | Verified | ISO 10-MWS-PD-P40-0120-01 pipe support 10-MWS-PD-HGR-0038 & 10-MWS-PD-HGR-0037 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07320 | Verified | ISO 10-MWS-PD-P40-0120-02 pipe spool 0120-3 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07321 | Verified | ISO 10-MWS-PD-P40-0120-02 Install Washers at connection to 10-MWS-T-0400/T-18 fiber glass | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07322 | Verified | ISO 10-MWS-PD-P40-0125-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07323 | Verified | ISO 10-MWS-PD-P40-0130-01 missing cap screws and missing valve handle on 10-MWS-V-0130 | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07324 | Verified | ISO 10-MWS-PD-P40-0130-01 per spec install washers fiber glass tank to CS flange | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07327 | Verified | ISO 10-MWS-PD-P40-0150-01 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07328 | Verified | ISO 10-MWS-PD-P40-0180-01 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07329 | Verified | ISO 10-MWS-PD-P40-0186-01 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-31 | James Beech | 2019-11-04 | Kelvin Cook
MWS-01 | MWS-01 | PI07330 | Verified | ISO 10-MWS-PD-P40-0340-01 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-11-04 | James Beech | 2019-11-08 | Kelvin Cook
MWS-01 | MWS-01 | PI07331 | Verified | ISO 10-MWS-PD-P40-0450-01 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-11-04 | James Beech | 2019-11-08 | Kelvin Cook
MWS-01 | MWS-01 | PI07332 | Verified | ISO 10-MWS-PD-P40-0450-02 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-31 | James Beech | 2019-11-04 | Kelvin Cook
MWS-01 | MWS-01 | PI07333 | Verified | ISO 10-MWS-PD-P40-0803-01 use anit siege all botls at flanges connection to 10-MWS-V-0803 | B | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07334 | Verified | ISO 10-MWS-PD-P40-0804-01 use anit siege all botls at flanges connection to 10-MWS-V-0804 | B | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07335 | Verified | ISO 10-MWS-PD-P40-0806-01 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07336 | Verified | ISO 10-MWS-PD-P41-0010-03 instrument 10-MWS-PP-0118 is not installed | A | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-10-02 | Gonzalo Pena | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07337 | Verified | ISO 10-MWS-PD-P41-0041-01 quick connect 10-MWS-QC-0805 is not installed | B | P | Shannon Scott | McD | 2019-09-27 | Shannon Scott | Const | 2020-02-21 | Shannon Scott | 2020-02-21 | Michael Law
MWS-01 | MWS-01 | PI07338 | Verified | ISO 10-MWS-PD-P41-0041-02 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07339 | Verified | ISO 10-MWS-PD-P41-0042-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07340 | Verified | ISO 10-MWS-PD-P41-0043-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07341 | Verified | ISO 10-MWS-PD-P41-0043-02 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07342 | Verified | ISO 10-MWS-PD-P41-0043-03 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07343 | Verified | ISO 10-MWS-PD-P41-0044-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07344 | Verified | ISO 10-MWS-PD-P41-0044-02 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07345 | Verified | ISO 10-MWS-PD-P41-0044-03 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07346 | Verified | ISO 10-MWS-PD-P41-0110-01 instrument 10-MWS-PI-0112 is not installed | A | I | Gonzalo Pena | McD | 2019-09-27 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07347 | Verified | ISO 10-MWS-PD-P41-0110-01 valve 10-MWS-V-0112 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07348 | Verified | ISO 10-MWS-PD-P41-0120-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-03 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07349 | Verified | ISO 10-MWS-PD-P41-0135-01 per spec install washer at flange connection to fiber glass tank | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07350 | Verified | ISO 10-MWS-PD-P41-0155-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07351 | Verified | ISO 10-MWS-PD-P41-0160-01 pipe support 10-MWS-PD-HGr-0112 & 0088 are not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07352 | Verified | ISO 10-MWS-PD-P41-0165-01 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07353 | Verified | ISO 10-MWS-PD-P41-0170-01 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-31 | James Beech | 2019-11-04 | Kelvin Cook
MWS-01 | MWS-01 | PI07354 | Verified | ISO 10-MWS-PD-P41-0170-02 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-31 | James Beech | 2019-11-04 | Kelvin Cook
MWS-01 | MWS-01 | PI07355 | Verified | ISO 10-MWS-PD-P41-0185-01 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07356 | Verified | ISO 10-MWS-PD-P41-0190-01 valve 10-MWS-CHK-0192 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-11-13 | Kelvin Cook
MWS-01 | MWS-01 | PI07357 | Verified | ISO 10-MWS-PD-P41-0190-01 pipe support 10-MWS-PD-HGR-0116 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-11-12 | James Beech | 2019-11-13 | Kelvin Cook
MWS-01 | MWS-01 | PI07358 | Verified | ISO 10-MWS-PD-P41-0200-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-31 | James Beech | 2019-11-04 | Kelvin Cook
MWS-01 | MWS-01 | PI07359 | Verified | ISO 10-MWS-PD-P41-0200-02 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-31 | James Beech | 2019-11-04 | Kelvin Cook
MWS-01 | MWS-01 | PI07360 | Verified | ISO 10-MWS-PD-P41-0220-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07361 | Verified | ISO 10-MWS-PD-P41-0225-01 is not installled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07362 | Verified | ISO 10-MWS-PD-P41-0226-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07363 | Verified | ISO 10-MWS-PD-P41-0227-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07364 | Verified | ISO 10-MWS-PD-P41-0228-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-11-04 | James Beech | 2019-11-08 | Kelvin Cook
MWS-01 | MWS-01 | PI07365 | Verified | ISO 10-MWS-PD-P41-0229-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
MWS-01 | MWS-01 | PI07366 | Verified | ISO 10-MWS-PD-P41-0230-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07367 | Verified | ISO 10-MWS-PD-P41-0230-02 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07368 | Verified | ISO 10-MWS-PD-P41-0230-03 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07369 | Verified | ISO 10-MWS-PD-P41-0230-04 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-11 | James Beech | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07370 | Verified | ISO 10-MWS-PD-P41-0240-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07371 | Verified | ISO 10-MWS-PD-P41-0250-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07372 | Verified | ISO 10-MWS-PD-P41-0271-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
MWS-01 | MWS-01 | PI07373 | Verified | ISO 10-MWS-PD-P41-0271-02 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07374 | Verified | ISO 10-MWS-PD-P41-0272-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07375 | Verified | ISO 10-MWS-PD-P41-0273-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07376 | Verified | ISO 10-MWS-PD-P41-0275-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07377 | Verified | ISO 10-MWS-PD-P41-0290-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
MWS-01 | MWS-01 | PI07378 | Verified | ISO 10-MWS-PD-P41-0310-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07379 | Verified | ISO 10-MWS-PD-P41-0320-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07380 | Verified | ISO 10-MWS-PD-P41-0330-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-23 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07381 | Verified | ISO 10-MWS-PD-P41-0410-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
MWS-01 | MWS-01 | PI07382 | Verified | ISO 10-MWS-PD-P41-0440-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07383 | Verified | ISO 10-MWS-PD-P41-0455-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07384 | Verified | ISO 10-MWS-PD-P41-0460-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07385 | Verified | ISO 10-MWS-PD-P41-0465-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-19 | Kelvin Cook
MWS-01 | MWS-01 | PI07386 | Verified | ISO 10-MWS-PD-P41-0470-01 is not installed | A | P | James Beech | McD | 2019-09-27 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
MWS-01 | MWS-01 | PI07387 | Verified | ISO 10-MWS-PD-P40-0803-01 install all bolts at the UG and 10-MWS-CLR-0100 the same length | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI07388 | Verified | ISO 10-MWS-PD-P40-0804-01 install all bolts at the UG and 10-MWS-CLR-0100 the same length | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-28 | Kelvin Cook
MWS-01 | MWS-01 | PI09147 | Verified | Ground all cable trays. | A | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-11-06 | Mike Tabbert
MWS-01 | MWS-01 | PI09148 | Verified | Extend cable tray at clarifier down to stub-ups. | A | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-09 | Dustin Futrell | 2019-11-06 | Mike Tabbert
MWS-01 | MWS-01 | PI09149 | Verified | Cables in manhole need more support. | A | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-15 | Fred Michael
MWS-01 | MWS-01 | PI09150 | Verified | Label cables in duct bank. | B | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09151 | Verified | Label conduits at duct bank. | B | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-15 | Fred Michael
MWS-01 | MWS-01 | PI09152 | Verified | Perform Clean & Close for manhole. | A | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-15 | Fred Michael
MWS-01 | MWS-01 | PI09153 | Verified | Feeder cables in 10-MWS-M-0700A termination box need collar for rub prevention. | A | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09154 | Verified | Feeder cables in 10-MWS-M-0700B termination box need collar for rub prevention. | A | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09155 | Verified | 10-MWS-M-0700B termination box missing gasket. | A | E | Chris Colvin | McD | 2019-10-07 | Chris Colvin | Const | 2019-10-16 | Dustin Futrell | 2020-01-13 | Fred Michael
MWS-01 | MWS-01 | PI09156 | Verified | Cable tray at clarifier missing dividers. Include plastic splices. | B | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09157 | Verified | Tag panels 10-MWS-CP-0500A & B. | C | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Fred Michael | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09158 | Verified | Panel 10-MWS-CP-0500A has damaged door. | B | E | Chris Colvin | McD | 2019-10-07 | Chris Colvin | Const | 2020-03-09 | Michael Law | 2020-04-21 | Michael Law
MWS-01 | MWS-01 | PI09159 | Verified | 10-MWS-CP-0001 - REPAIR DOOR HANDLE | B | E | Chris Colvin | McD | 2019-10-07 | Chris Colvin | Const |  |  | 2020-01-30 | Fred Michael
MWS-01 | MWS-01 | PI09160 | Verified | Seal penetrations in panels (after cable pulls). | B | E | Chris Colvin | McD | 2019-10-07 | Chris Colvin | Const | 2019-12-03 | Brad Stanford | 2020-01-13 | Fred Michael
MWS-01 | MWS-01 | PI09161 | Verified | Ground all panels. | A | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09162 | Verified | 10-MWS-CP-0320 needs ground. | A | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Fred Michael | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09163 | Verified | 10-MWS-JB-0310 - missing receptacle cover. | B | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Fred Michael | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09164 | Verified | Panel at polymer skid needs label. | C | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Fred Michael | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09165 | Verified | 10-MWS-M-0130 needs label. | C | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09166 | Verified | 10-MWS-M-0120 needs label. | C | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09167 | Verified | 10-MWS-M-0120 - plug conduit. | B | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09168 | Verified | 10-MWS-M-0140 needs label. | C | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09169 | Verified | Panel 10-MWS-DRV-0140 - remove tape on glass. | B | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Fred Michael | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09171 | Verified | Motors 10-MWS-M-0600A & B are tagged incorrectly as 0006A & B. | C | E | Dustin Futrell | McD | 2019-10-07 | Dustin Futrell | Const | 2019-10-11 | Brad Stanford | 2019-10-11 | Fred Michael
MWS-01 | MWS-01 | PI09172 | Verified | 10-MWS-QUIL-0470 not installed. | A | I | Gonzalo Pena | McD | 2019-10-07 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2019-11-05 | Albert Burge
MWS-01 | MWS-01 | PI09173 | Verified | 10-MWS-PP-0118 not installed. | A | I | Gonzalo Pena | McD | 2019-10-07 | Gonzalo Pena | Const | 2019-10-09 | Gonzalo Pena | 2019-11-04 | Albert Burge
MWS-01 | MWS-01 | PI09237 | Verified | 10MWSX0150, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-06 | Mike Tabbert
MWS-01 | MWS-01 | PI09238 | Verified | 10MWSX0151, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-06 | Mike Tabbert
MWS-01 | MWS-01 | PI09239 | Verified | 10MWSX0154, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09240 | Verified | 10MWSX0155, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09242 | Verified | 10DCSX0105, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09243 | Verified | 10MWSC0020, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09244 | Verified | 10MWSC0021, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09245 | Verified | 10MWSC0023, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09246 | Verified | 10MWSC0051, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09247 | Verified | 10MWSC0052, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09248 | Verified | 10MWSK0020, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09249 | Verified | 10MWSK0040, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09250 | Verified | 10MWSK0052, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09251 | Verified | 10MWSK0053, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09252 | Verified | 10MWSL0001A, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09253 | Verified | 10MWSL0001B, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09254 | Verified | 10MWSL0001C, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09255 | Verified | 10MWSL0001G, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09256 | Verified | 10MWSL0002A, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09257 | Verified | 10MWSL0002B, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09258 | Verified | 10MWSL0002C, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09259 | Verified | 10MWSL0002G, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09260 | Verified | 10MWSL0044A, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09261 | Verified | 10MWSL0044B, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09262 | Verified | 10MWSL0044C, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09263 | Verified | 10MWSL0044G, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09264 | Verified | 10MWSX0008, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-06 | Mike Tabbert
MWS-01 | MWS-01 | PI09265 | Verified | 10MWSX0010, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09266 | Verified | 10MWSX0026, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09267 | Verified | 10MWSX0029, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09268 | Verified | 10MWSX0034, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09269 | Verified | 10MWSX0037, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09270 | Verified | 10MWSX0038, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09271 | Verified | 10MWSX0039, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09272 | Verified | 10MWSX0042, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09273 | Verified | 10MWSX0046, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09274 | Verified | 10MWSX0063, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09275 | Verified | 10MWSX0064, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09276 | Verified | 10MWSX0072, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09277 | Verified | 10MWSX0148, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MWS-01 | MWS-01 | PI09278 | Verified | 10MWSX0149, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MWS-01 | MWS-01 | PI09279 | Verified | 10MWSX0150, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-06 | Mike Tabbert
MWS-01 | MWS-01 | PI09280 | Verified | 10MWSX0151, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-06 | Mike Tabbert
MWS-01 | MWS-01 | PI09281 | Verified | 10MWSX0154, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09282 | Verified | 10MWSX0155, From Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09284 | Verified | 10DCSX0105, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09285 | Verified | 10MWSC0019, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09286 | Verified | 10MWSC0020, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09287 | Verified | 10MWSK0003, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09288 | Verified | 10MWSK0011, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09289 | Verified | 10MWSK0013, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09290 | Verified | 10MWSK0014, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09291 | Verified | 10MWSK0050, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
MWS-01 | MWS-01 | PI09292 | Verified | 10MWSX0008, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-11-06 | Dustin Futrell | 2019-11-06 | Mike Tabbert
MWS-01 | MWS-01 | PI09293 | Verified | 10MWSX0009, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-06 | Mike Tabbert
MWS-01 | MWS-01 | PI09294 | Verified | 10MWSX0010, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MWS-01 | MWS-01 | PI09295 | Verified | 10MWSX0012, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09296 | Verified | 10MWSX0013, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09297 | Verified | 10MWSX0014, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09298 | Verified | 10MWSX0036, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
MWS-01 | MWS-01 | PI09299 | Verified | 10MWSX0045, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-06 | Mike Tabbert
MWS-01 | MWS-01 | PI09300 | Verified | 10MWSX0055, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-21 | Mike Tabbert
MWS-01 | MWS-01 | PI09301 | Verified | 10MWSX0057, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-10-25 | Mike Tabbert
MWS-01 | MWS-01 | PI09302 | Verified | 10MWSX0059, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09303 | Verified | 10MWSX0060, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-18 | Tommy Vuong | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09304 | Verified | 10MWSX0073, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MWS-01 | MWS-01 | PI09305 | Verified | 10MWSX0148, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MWS-01 | MWS-01 | PI09306 | Verified | 10MWSX0149, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
MWS-01 | MWS-01 | PI09307 | Verified | 10MWSX0150, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-06 | Mike Tabbert
MWS-01 | MWS-01 | PI09308 | Verified | 10MWSX0151, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-06 | Mike Tabbert
MWS-01 | MWS-01 | PI09309 | Verified | 10MWSX0154, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09310 | Verified | 10MWSX0155, To Termination | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-19 | Mike Tabbert
MWS-01 | MWS-01 | PI09312 | Verified | 10-MWS-CP-0001, replace rusted mounting hardware with stainless nuts and washers. | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-11-06 | Mike Tabbert
MWS-01 | MWS-01 | PI09313 | Verified | 10-MWS-CP-0001, Cables have been installed with no bushings and free aired from underground stub-ups. | A | E | Dustin Futrell | McD | 2019-10-08 | Dustin Futrell | Const | 2019-10-16 | Fred Michael | 2019-10-16 | Fred Michael
MWS-01 | MWS-01 | PI09687 | Verified | 10-MWS-M-0700A requires rework of terminations in motor connection box. | A | E | Dustin Futrell | McD | 2019-10-16 | Dustin Futrell | Const |  |  | 2019-10-24 | Mike Tabbert
MWS-01 | MWS-01 | PI09688 | Verified | 10-MWS-M-0700B requires rework of terminations in motor connection box. | A | E | Dustin Futrell | McD | 2019-10-16 | Dustin Futrell | Const |  |  | 2019-10-24 | Mike Tabbert
MWS-01 | MWS-01 | PI09818 | Verified | Test Package MWS-T-01 need to be tested | B | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-08 | Kelvin Cook
MWS-01 | MWS-01 | PI12599 | Verified | Clarifier scraper rake arm needs setting and welding. | A | M | Shane Crowe | McD | 2019-10-29 | Shane Crowe | Const | 2019-11-11 | Shane Crowe | 2019-11-11 | Joshua Sturgeon
MWS-01 | MWS-01 | PI12617 | Verified | Clarifier - Repair leaks on clarifier. | B | C | Johnny Campbell | McD | 2019-10-29 | Johnny Campbell | Const | 2019-11-21 | Johnny Campbell | 2020-01-02 | William Mitchell
MWS-01 | MWS-01 | PI12618 | Verified | Clarifier - Complete sand pumps. | A | I | Gonzalo Pena | McD | 2019-10-29 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2020-01-02 | William Mitchell
MWS-01 | MWS-01 | PI12619 | Verified | Clarifier - Install chlorine injection quill. | A | I | Gonzalo Pena | McD | 2019-10-29 | Gonzalo Pena | Const | 2019-11-04 | Gonzalo Pena | 2020-01-02 | William Mitchell
MWS-01 | MWS-01 | PI12620 | Verified | Clarifier - Complete chemical lines. | A | P | James Beech | McD | 2019-10-29 | James Beech | Const | 2019-11-04 | James Beech | 2020-01-02 | William Mitchell
MWS-01 | MWS-01 | PI12621 | Verified | Clarifer - Hydro chemical lines. | A | P | James Beech | McD | 2019-10-29 | James Beech | Const | 2019-11-04 | James Beech | 2020-01-02 | William Mitchell
MWS-01 | MWS-01 | PI12713 | Verified | 10--MWS-P-0600A - send pump out for bearing modification work. | B | M | Shane Crowe | McD | 2019-11-04 | Shane Crowe | Const |  |  | 2019-11-22 | Joshua Sturgeon
MWS-01 | MWS-01 | PI12714 | Verified | 10--MWS-P-0600B - send pump out for bearing modification work. | B | M | Shane Crowe | McD | 2019-11-04 | Shane Crowe | Const |  |  | 2019-11-22 | Joshua Sturgeon
MWS-01 | MWS-01 | PI12811 | Verified | Dress up cables in all trays, tie wrap in place and trim tie raps. | B | E | Chris Colvin | McD | 2019-11-06 | Chris Colvin | Const | 2019-12-03 | Brad Stanford | 2019-12-18 | Mike Tabbert
MWS-01 | MWS-01 | PI12812 | Verified | Complete installation of all tray dividers in all trays, including plastic splices. | B | E | Chris Colvin | McD | 2019-11-06 | Chris Colvin | Const | 2019-12-03 | Brad Stanford | 2019-12-18 | Mike Tabbert
MWS-01 | MWS-01 | PI12813 | Verified | Cold galvanizie all exposeed threads on all conduit. | B | E | Chris Colvin | McD | 2019-11-06 | Chris Colvin | Const | 2019-12-03 | Brad Stanford | 2019-12-18 | Mike Tabbert
MWS-01 | MWS-01 | PI12814 | Verified | Reroute analyzer cables on top of clarifier and on bottom west side of clarifier, remove from handrails and install conduit or instrument tray to support cables. | B | E | Chris Colvin | McD | 2019-11-06 | Chris Colvin | Const | 2020-03-04 | Mike Tabbert | 2020-03-04 | Mike Tabbert
MWS-01 | MWS-01 | PI12815 | Verified | Seal all duct bank stub-ups at south end of clarifier. | B | E | Chris Colvin | McD | 2019-11-06 | Chris Colvin | Const | 2019-11-18 | Brad Stanford | 2019-12-18 | Mike Tabbert
MWS-01 | MWS-01 | PI12816 | Verified | Install 10-MWS-PI and FI-0902A/B and 0906A/B. | B | I | Gonzalo Pena | McD | 2019-11-06 | Gonzalo Pena | Const | 2019-12-07 | James Tanner | 2019-12-13 | Gonzalo Pena
MWS-01 | MWS-01 | PI12818 | Verified | The bulk caustic tank's fill line is routed in different location than the Caustic Truck fill control panel. Operator has no indication for when the tank is full & creates possible overfill hazard. | C | I | Chris Colvin | McD | 2019-11-06 | Chris Colvin | Const | 2021-06-17 | Eric Policarpio | 2021-06-17 | John Watts
MWS-01 | MWS-01 | PI12859 | Verified | Provide static head test for Tanks 200, 220 230 & 400. | B | M | William Mitchell | McD | 2019-11-09 | William Mitchell | Const |  |  | 2020-01-22 | Kelvin Cook
MWS-01 | MWS-01 | PI12889 | Verified | 1-MWS-CYC-0300B has a crack and needs to be replaced. | A | P | Kelvin Cook | McD | 2019-11-12 | Kelvin Cook | Const |  |  | 2020-02-07 | Kelvin Cook
MWS-01 | MWS-01 | PI14851 | Verified | Install 6" riser clamp and shim accordingly to make the flange level 10-MWS-LIT-0700 | B | P | James Beech | McD | 2019-12-20 | James Beech | Comm | 2020-01-14 | Tim Green | 2020-01-14 | Ethan Byrd
MWS-01 | MWS-01 | PI14854 | Verified | Install 6" riser clamp and shim accordingly to make the flange level 10-MWS-LIT-0600 | B | P | James Beech | McD | 2019-12-20 | James Beech | Comm | 2020-01-14 | Tim Green | 2020-01-14 | Ethan Byrd
MWS-01 | MWS-01 | PI14866 | Verified | 10-MWS-P-0320C - Clarifier polymer dosing pump 'C' is not working. There is a run indication on the HMI and pump control panel. However, the pump indicator shows 0 Hz and no flow is shown on draw down. Pump was placed in OFF position. | B | E | Jonathan Donham | McD | 2019-12-24 | Jonathan Donham | Comm | 2020-03-02 | Jonathan Donham | 2020-04-07 | Bernard Stasse
MWS-01 | MWS-01 | PI14867 | Verified | 10-MWS-P-0230A/B - Clarifier Injection Caustic Pumps are not controlling in auto to correct pH. Tuning is required on both pumps. Caustic Pump A is not treating adequately even when in manual. | B | I | Albert Burge | McD | 2019-12-24 | Albert Burge | Comm | 2020-02-28 | Albert Burge | 2020-02-28 | John Watts
MWS-01 | MWS-01 | PI14868 | Verified | 10-MWS-M-0151 - The HMI manual control push buttons on the clarifier scrapper lift motor are reversed. If the UP button is pressed, the scrapper goes DOWN. When the DOWN button is pressed, the scraper goes UP. | B | E | Chris Boudreaux | McD | 2019-12-24 | Chris Boudreaux | Comm |  |  | 2020-01-22 | Shannon Scott
MWS-01 | MWS-01 | PI14869 | Verified | 10-MWS-P-0400B - Sludge Pump B had oil that leaked from the pump motor. | B | E | Jonathan Donham | McD | 2019-12-24 | Jonathan Donham | Comm | 2020-03-26 | Jonathan Donham | 2020-04-07 | Bernard Stasse
MWS-01 | MWS-01 | PI14871 | Verified | 10-MWS-LIT-0700 - The conduit by the clarifier's stairs is is creating a tripping hazard | B | E | Chris Colvin | McD | 2019-12-24 | Chris Colvin | Comm | 2020-03-23 | Mike Tabbert | 2020-04-07 | Bernard Stasse
MWS-01 | MWS-01 | PI14873 | Verified | Sodium Hypochlorite Tank Ladder - There's an incomplete mounting bracket on the Sodium Hypochlorite Tank ladder. | B | M | Shane Crowe | McD | 2019-12-24 | Shane Crowe | Comm | 2020-02-24 | Shane Crowe | 2020-02-25 | John Watts
MWS-01 | MWS-01 | PI14874 | Verified | 10-MWS-PV-0045 - Clearwell recirc valve has air leak. | B | I | Gonzalo Pena | McD | 2019-12-24 | Gonzalo Pena | Comm | 2020-01-13 | Shannon Scott | 2020-01-13 | Shannon Scott
MWS-01 | MWS-01 | PI13866 | Verified | 10-MWS-PI-0202A - replace gauge with silicone filled diaphragm gauge combo. | B | I | James Beech | McD | 2019-12-03 | James Beech | Comm | 2020-03-10 | Tim Green | 2020-03-11 | Michael Law
MWS-01 | MWS-01 | PI13867 | Verified | 10-MWS-PI-0202B - replace gauge with silicone filled diaphragm gauge combo. | B | I | James Beech | McD | 2019-12-03 | James Beech | Comm | 2020-03-10 | Tim Green | 2020-03-11 | Michael Law
MWS-01 | MWS-01 | PI13868 | Verified | 10-MWS-PI-0222A - replace gauge with silicone filled diaphragm gauge combo. | B | I | James Beech | McD | 2019-12-03 | James Beech | Comm | 2020-03-10 | Tim Green | 2020-03-11 | Michael Law
MWS-01 | MWS-01 | PI13869 | Verified | 10-MWS-PI-0222B - replace gauge with silicone filled diaphragm gauge combo. | B | I | James Beech | McD | 2019-12-03 | James Beech | Comm | 2020-03-10 | Tim Green | 2020-03-11 | Michael Law
MWS-01 | MWS-01 | PI13870 | Verified | 1A-MWS-PI-0231A - replace gauge with silicone filled diaphragm gauge combo. | B | I | James Beech | McD | 2019-12-03 | James Beech | Comm | 2020-03-10 | Tim Green | 2020-03-11 | Michael Law
MWS-01 | MWS-01 | PI13874 | Verified | 1A-MWS-PI-0322A - replace gauge with silicone filled diaphragm gauge combo. | B | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Comm | 2020-03-09 | Tim Green | 2020-03-09 | Michael Law
MWS-01 | MWS-01 | PI13873 | Verified | 1A-MWS-PI-0321A - replace gauge with silicone filled diaphragm gauge combo. | B | I | James Beech | McD | 2019-12-03 | James Beech | Comm | 2020-03-10 | Tim Green | 2020-03-11 | Michael Law
MWS-01 | MWS-01 | PI13872 | Verified | 1A-MWS-PI-0317 - replace gauge with silicone filled diaphragm gauge combo. | B | I | James Beech | McD | 2019-12-03 | James Beech | Comm | 2020-03-10 | Tim Green | 2020-03-11 | Michael Law
MWS-01 | MWS-01 | PI13871 | Verified | 1A-MWS-PI-0231B - replace gauge with silicone filled diaphragm gauge combo. | B | I | James Beech | McD | 2019-12-03 | James Beech | Comm | 2020-03-10 | Tim Green | 2020-03-11 | Michael Law
MWS-01 | MWS-01 | PI13875 | Verified | 1B-MWS-PI-0322B - replace gauge with silicone filled diaphragm gauge combo. | B | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Comm | 2020-03-09 | Tim Green | 2020-03-09 | Michael Law
MWS-01 | MWS-01 | PI13876 | Verified | 1B-MWS-PI-0322C - replace gauge with silicone filled diaphragm gauge combo. | B | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Comm | 2020-03-09 | Tim Green | 2020-03-09 | Michael Law
MWS-01 | MWS-01 | PI13877 | Verified | 1B-MWS-PI-0503A - replace gauge with silicone filled diaphragm gauge combo. | B | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Comm | 2020-03-09 | Tim Green | 2020-03-09 | Michael Law
MWS-01 | MWS-01 | PI13878 | Verified | 1B-MWS-PI-0503B - replace gauge with silicone filled diaphragm gauge combo. | B | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Comm | 2020-03-09 | Tim Green | 2020-03-09 | Michael Law
MWS-01 | MWS-01 | PI15568 | Verified | 10-MWS-CLR-PLC - The analog input card in rack 4 is not communicating. Failed two times in 24 hrs | C | I | Albert Burge | McD | 2020-01-08 | Albert Burge | Comm | 2020-03-30 | Albert Burge | 2020-04-07 | Bernard Stasse
MWS-01 | MWS-01 | PI15906 | Verified | 10-MWS-QUIL-0470 - The caustic quill is leaking, environmental concern | B | M | William Mitchell | McD | 2020-01-13 | William Mitchell | Comm |  |  | 2020-01-22 | Shannon Scott
MWS-01 | MWS-01 | PI15907 | Verified | 10-MWS-QUIL-0200 - The sodium hypochlorite quil is leaking & causing corrosion | B | M | William Mitchell | McD | 2020-01-13 | William Mitchell | Comm |  |  | 2020-01-22 | Shannon Scott
MWS-01 | MWS-01 | PI15908 | Verified | 10-MWS-CLR-0100 - PLC/DCS flatlines at 15 NTU even though the actual reading is much higher. | C | I | Albert Burge | McD | 2020-01-13 | Albert Burge | Comm | 2020-03-30 | Albert Burge | 2020-04-07 | Bernard Stasse
MWS-01 | MWS-01 | PI15909 | Verified | 10-MWS-P-0100B - The Clarifier Sand Recirc Pump failed. | B | M | William Mitchell | McD | 2020-01-13 | William Mitchell | Comm | 2020-01-22 | William Mitchell | 2020-01-22 | Shannon Scott
MWS-01 | MWS-01 | PI16679 | Verified | 10-MWS-T-0120 - There's a leak at the bottom of the RWS inlet piping into the coagulant tank. | B | M | William Mitchell | McD | 2020-02-07 | William Mitchell | Comm | 2020-03-17 | William Mitchell | 2020-04-07 | Bernard Stasse
MWS-01 | MWS-01 | PI16680 | Verified | 10-MWS-T-0140 - There's a leak on plant east side of tank adjacent to the steps going up the clarifier. | B | M | William Mitchell | McD | 2020-02-07 | William Mitchell | Comm | 2020-03-17 | William Mitchell | 2020-04-07 | Bernard Stasse
MWS-01 | MWS-01 | PI16693 | Verified | 10-MWS-P-0220A/B - Coagulant is leaking from the pump pressure relief valve (10-MWS-PSV-0221A/B) | B | P | William Mitchell | McD | 2020-02-10 | William Mitchell | Comm | 2020-02-28 | William Mitchell | 2020-02-28 | John Watts
MWS-01 | MWS-01 | PI17158 | Verified | Condolet open on East side of Clarifier, wiring exposed | C | E | Sheri Fritz | TRI | 2020-02-22 | Sheri Fritz | Comm | 2020-05-26 | Sheri Fritz | 2020-08-17 | Dave Goldak
MWS-01 | MWS-01 | PI17159 | Verified | Condolet open on East side of Clarifier just below top stair landing, wiring exposed | C | E | Sheri Fritz | TRI | 2020-02-22 | Sheri Fritz | Comm | 2020-05-26 | Sheri Fritz | 2020-08-17 | Dave Goldak
MWS-01 | MWS-01 | PI17160 | Verified | Power cable conduit to 10-MWS-LIT-0700; Clearwell Sump Level Indicating Transmitter causing trip hazard at West side of Clearwell Sump cover | C | E | Chris Colvin | McD | 2020-02-22 | Chris Colvin | Comm | 2020-04-01 | Chris Colvin | 2020-04-01 | Randy Carpenter
MWS-01 | MWS-01 | PI17161 | Verified | Condolet missing on power cable conduit to MWS-PIT-0045; Clearwell Pump Discharge Header Pressure Indicating Transmitter | C | E | Chris Colvin | McD | 2020-02-22 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2020-08-17 | Dave Goldak
MWS-01 | MWS-01 | PI17163 | Verified | Raise storm drain to grade at Southeast side of Clearwell, currently storm drain is well below grade | C | C | Brooks Baker | McD | 2020-02-22 | Brooks Baker | Comm | 2020-04-01 | Brooks Baker | 2020-04-28 | Mark Williamson
MWS-01 | MWS-01 | PI17164 | Verified | Coupling guard missing at 10-MWS-P-0400A; Clarifier Sludge Transfer Pump A | B | P | William Mitchell | McD | 2020-02-22 | William Mitchell | Comm | 2020-03-17 | William Mitchell | 2020-04-16 | Keith Pollock
MWS-01 | MWS-01 | PI17165 | Verified | Coupling guard missing at 10-MWS-P-0400B; Clarifier Sludge Transfer Pump B | B | P | William Mitchell | McD | 2020-02-22 | William Mitchell | Comm | 2020-03-17 | William Mitchell | 2020-04-16 | Keith Pollock
MWS-01 | MWS-01 | PI17169 | Verified | Clarifier Rake Torque Gauge is not working, does not indicate torque when rake is in operation - need clarifier down | C | I | Albert Burge | McD | 2020-02-22 | Albert Burge | Comm | 2020-04-09 | Albert Burge | 2020-04-16 | Keith Pollock
MWS-01 | MWS-01 | PI17170 | Verified | Clean up Clarifier grating platform | C | C | Alan Huntsman | McD | 2020-02-22 | Alan Huntsman | Comm | 2020-03-18 | Johnny Campbell | 2020-08-17 | Dave Goldak
MWS-01 | MWS-01 | PI17171 | Verified | Complete heat trace throughout system | C | E | Sheri Fritz | TRI | 2020-02-22 | Sheri Fritz | Comm | 2020-04-03 | Sheri Fritz | 2021-06-17 | John Watts
MWS-01 | MWS-01 | PI17172 | Verified | Complete insulation throughout system | C | Q | Sheri Fritz | PCI | 2020-02-22 | Sheri Fritz | Comm | 2020-05-11 | Michael Law | 2020-05-11 | Michael Law
MWS-01 | MWS-01 | PI17173 | Verified | Disc Filter Backwash Pump 2" discharge piping disconnected at 10-MWS-FLT-0500B; Disc Filter B, North side | B | P | William Mitchell | McD | 2020-02-22 | William Mitchell | Comm | 2020-03-26 | William Mitchell | 2020-04-16 | Keith Pollock
MWS-01 | MWS-01 | PI17174 | Verified | Power cables to 10-MWS-P-0510 A & B; Disc Filter Backwash Pumps A & B need protection (conduit or cable wrap) | D | E | Mike Tabbert | McD | 2020-02-22 | Mike Tabbert | Comm | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
MWS-01 | MWS-01 | PI17175 | Verified | Repair epoxy coating inside Clarifier Coagulant Tank containment | C | X | Sheri Fritz | BRA | 2020-02-22 | Sheri Fritz | Comm | 2020-04-28 | Johnny Campbell | 2020-08-17 | Dave Goldak
MWS-01 | MWS-01 | PI17176 | Verified | Coupling guard missing at 10-MWS-P-0100A; Clarifier Sand Recirculation Pump A | B | P | William Mitchell | McD | 2020-02-22 | William Mitchell | Comm | 2020-03-17 | William Mitchell | 2020-04-16 | Keith Pollock
MWS-01 | MWS-01 | PI17177 | Verified | Coupling guard missing at 10-MWS-P-0100B; Clarifier Sand Recirculation Pump B | B | P | William Mitchell | McD | 2020-02-22 | William Mitchell | Comm | 2020-03-17 | William Mitchell | 2020-04-16 | Keith Pollock
MWS-01 | MWS-01 | PI17178 | Verified | Broken Fault indicator light at 10-MWS-DRV-0140; Maturation Tank Mixer Variable Frequency Drive panel, Clarifier platform, West side | B | E | Mike Tabbert | McD | 2020-02-22 | Mike Tabbert | Comm | 2020-03-20 | Mike Tabbert | 2020-04-16 | Keith Pollock
MWS-01 | MWS-01 | PI17179 | Verified | Clean out 10-MWS-T-0200; Clarifier Sodium Hypochlorite Tank and 10-MWS-T-0220 Clarifier Coagulant Tank containment | C | C | Johnny Campbell | McD | 2020-02-22 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2021-01-05 | Keith Pollock
MWS-01 | MWS-01 | PI17180 | Verified | Clean up Clarifier Sodium Hypochlorite Metering Pump A & B skid | C | C | Johnny Campbell | McD | 2020-02-22 | Johnny Campbell | Comm | 2020-04-09 | Johnny Campbell | 2020-08-17 | Dave Goldak
MWS-01 | MWS-01 | PI17181 | Verified | Rework vertical pipe support for 10-MWS-LIT-0200; Clarifier Sodium Hypochlorite Tank level indicator, current support is not making contact | C | P | Tim Green | McD | 2020-02-22 | Tim Green | Comm | 2020-05-29 | James Beech | 2020-08-17 | Dave Goldak
MWS-01 | MWS-01 | PI17182 | Verified | Remove unused support at Southeast corner of Clarifier 25% Caustic Tank containment | C | P | James Beech | McD | 2020-02-22 | James Beech | Comm | 2020-05-27 | James Beech | 2020-08-17 | Dave Goldak
MWS-01 | MWS-01 | PI17183 | Verified | Clean out 10-MWS-T-0230; Clarifier 25% Caustic Tank containment | C | C | Alan Huntsman | McD | 2020-02-22 | Alan Huntsman | Comm | 2020-03-13 | Johnny Campbell | 2020-12-03 | Dave Goldak
MWS-01 | MWS-01 | PI17185 | Verified | Clean out Clarifier 25% Caustic Metering Pumps A & B skid | C | C | Johnny Campbell | McD | 2020-02-22 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-12-03 | Dave Goldak
MWS-01 | MWS-01 | PI17186 | Verified | Need permanent clamp supports for Pulsation Dampers A & B at Clarifier Coagulant Metering Pump skid, currently supported with tie wraps | B | P | James Beech | McD | 2020-02-22 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-08-17 | Dave Goldak
MWS-01 | MWS-01 | PI17189 | Verified | Repair concrete around Service Water stub up at South side of Polymer Feed Pump skid enclosure | C | C | Alan Huntsman | McD | 2020-02-22 | Alan Huntsman | Comm | 2020-03-13 | Johnny Campbell | 2020-12-03 | Dave Goldak
MWS-01 | MWS-01 | PI17190 | Verified | Adjust 10-MWS-FLT-0500A; Disc Filter A enclosure door hinge, door will not stay open | C | M | William Mitchell | McD | 2020-02-22 | William Mitchell | Comm | 2020-04-20 | William Mitchell | 2021-04-26 | Keith Pollock
MWS-01 | MWS-01 | PI17654 | Verified | The Veolia rep recommends moving the clarifier coagulant injection point from the clarifier feed piping to the coagulation tank. He says the caustic injection is too close to the coagulant injection, and the caustic is breaking down the coagulant. | D | M | Charles Worthington | McD | 2020-03-04 | Charles Worthington | Comm | 2020-07-22 | Bryan Sturgies | 2021-02-01 | Dave Goldak
MWS-01 | MWS-01 | PI17669 | Verified | 10-MWS-P-0700B - The packing is leaking. It needs to be adjusted or repacked - 3/27 currently tuning the system | C | M | William Mitchell | McD | 2020-03-04 | William Mitchell | Comm | 2020-04-20 | William Mitchell | 2020-04-20 | William Mitchell
MWS-01 | MWS-01 | PI17670 | Verified | 10-MWS-FV-0016 - When shutting down the clarifier, operators have to manually slow down the clarifier feed valve because the RWS pump minimum flow valve does not respond quickly enough, thus causing the RWS feed pumps to trip - 3/27 Flowserve to visit site | C | M | Mike Wilferd | McD | 2020-03-04 | Mike Wilferd | Comm | 2020-06-23 | Mike Wilferd | 2021-02-01 | Dave Goldak
MWS-01 | MWS-01 | PI17676 | Verified | 10-MWS-PI-0131A & 10-MWS-PI-0131B - The discharge pressure indicators, 10-MWS-PI-0131A/B, do not show pressure when the pump is running. | B | I | Albert Burge | McD | 2020-03-04 | Albert Burge | Comm | 2020-03-04 | Albert Burge | 2020-12-16 | Dave Goldak
MWS-01 | MWS-01 | PI18007 | Cleared | 10-MWS-CLR-PLC - Some handles on the Allen Bradley PLC cabinet do not operate properly. Also, some doors are unable to open. Check all handles and doors. | C | E | Mike Tabbert | McD | 2020-03-17 | Mike Tabbert | Comm | 2020-05-04 | Matt Gilmore
MWS-01 | MWS-01 | PI18008 | Verified | 10-MWS-CLR-PLC - 10-MWS-P-0230B is not working at all when placed in AUTO on the HMI. Compare the ladder logic and settings to the 10-MWS-P-0230A. | C | M | Mike Wilferd | McD | 2020-03-17 | Mike Wilferd | Comm | 2020-05-28 | Mike Wilferd | 2021-07-08 | John Watts
MWS-01 | MWS-01 | PI18012 | Verified | 10-MWS-PSV-0130 - The PSV will not seat and is leaking by. | C | M | James Beech | McD | 2020-03-17 | James Beech | Comm | 2020-05-19 | Tim Green | 2021-07-08 | John Watts
MWS-01 | MWS-01 | PI18107 | Verified | 10-MWS-P-0100A - There's a significant packing leak on this pump. The packing needs to be replaced. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-20 | William Mitchell | 2020-07-28 | Keith Pollock
MWS-01 | MWS-01 | PI18140 | Verified | 10-MWS-P-0700A and 10-MWS-P-0700B - Both Clearwell pumps leak significantly at the packing. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-05-05 | William Mitchell | 2020-12-16 | Dave Goldak
MWS-01 | MWS-01 | PI18149 | Verified | 10-MWS-SCRP-0150 - Clarifier scraper torque - bad quality | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-14 | William Mitchell | 2020-04-30 | John Watts
MWS-01 | MWS-01 | PI18154 | Verified | Clarifier solids carry over to the UF. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-20 | William Mitchell | 2020-04-30 | John Watts
MWS-01 | MWS-01 | PI18158 | Verified | 10-MWS-FLT-0500A and 10-MWS-FLT-0500B - Can only run one Disc Filter at a time. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2020-06-05 | Tanner Hillman
MWS-01 | MWS-01 | PI18181 | Verified | 10-MWS-P-0510B - The discharge piping is missing a coupling, preventing water from reaching backwash spray heads. | C | M | William Mitchell | McD | 2020-03-24 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2021-05-24 | Keith Pollock
MWS-01 | MWS-01 | PI18182 | Verified | 10-MWS-P-0400A - Sludge pump A is leaking oil out of the breather on the top of the bearing housing. | C | M | William Mitchell | McD | 2020-03-24 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2021-04-26 | Keith Pollock
MWS-01 | MWS-01 | PI18198 | Verified | Veolia Commissioning Field Service Report to submit | C | M | William Mitchell | McD | 2020-03-30 | William Mitchell | Comm | 2020-04-23 | William Mitchell | 2020-04-23 | Eric Policarpio
MWS-01 | MWS-01 | PI18303 | Verified | Clean mess in bottom of Coagulent skid 10-MWS-CP-0220 following commissioning activities. See photo. | C | C | Johnny Campbell | McD | 2020-05-21 | Johnny Campbell | Const | 2020-05-28 | Jason Ezell | 2020-12-03 | Dave Goldak
MWS-01 | MWS-01 | PI18304 | Verified | Clean mess in bottom of Bleach skid 10-MWS-CP-0200 following commissioning activities. See photo. | C | C | Johnny Campbell | McD | 2020-05-21 | Johnny Campbell | Const | 2020-05-28 | Jason Ezell | 2020-12-03 | Dave Goldak
NBS-02 | NBS-02 | PI02315 | Verified | 1B-NBS-FXH-0100A needs to be longer | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-02 | NBS-02 | PI02316 | Verified | 1B-NBS-FXH-0100B needs to be longer | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-02 | NBS-02 | PI02317 | Verified | 1B-NBS-PD-P41-0100-01 install vent valve per new revision | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-22 | Kelvin Cook
NBS-02 | NBS-02 | PI02318 | Verified | 1B-NBS-PD-P41-0101-01 install vent valve per new revision | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-22 | Kelvin Cook
NBS-02 | NBS-02 | PI02319 | Verified | 1B-NBS-PD-P41-0101-01 Install proper gaskets at 1B-NBS-PV-0100B | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Justin Houdeshell
NBS-02 | NBS-02 | PI02320 | Verified | 1B-NBS-PD-P41-0101-01 Install proper gaskets at 1B-NBS-PV-0100B | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Kelvin Cook | 2019-07-26 | Kelvin Cook
NBS-02 | NBS-02 | PI02321 | Verified | Cold Galvanize all supports | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-08-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02322 | Verified | Complete all pressure testing | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Kelvin Cook
NBS-02 | NBS-02 | PI02323 | Verified | Grout all supports | C | P | Johnny Campbell | McD | 2019-07-18 | Johnny Campbell | Const | 2019-07-31 | Jack Fields | 2019-08-08 | Kelvin Cook
NBS-02 | NBS-02 | PI02324 | Verified | 1B-NBS-PD-P41-0100-01 HGR-0069 need to have full thread engagement at eye bolt "2 thrd min." | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02325 | Verified | 1B-NBS-V-0101A make tubing connection | A | I | Gonzalo Pena | McD | 2019-07-18 | Gonzalo Pena | Const | 2019-07-19 | Gonzalo Pena | 2019-07-19 | Kelvin Cook
NBS-02 | NBS-02 | PI02326 | Verified | 1B-NBS-V-0101B make tubing connection | A | I | Gonzalo Pena | McD | 2019-07-18 | Gonzalo Pena | Const | 2019-07-19 | Gonzalo Pena | 2019-07-19 | Kelvin Cook
NBS-02 | NBS-02 | PI02327 | Verified | 1B-NBS-PD-P41-0101-01 Install proper gaskets at 1B-NBS-PV-0100B | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Kelvin Cook | 2019-07-26 | Kelvin Cook
NBS-02 | NBS-02 | PI02328 | Verified | 1B-NBS-PD-P41-0101-01 Install proper gaskets at 1B-NBS-PV-0100B | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Kelvin Cook
NBS-02 | NBS-02 | PI02329 | Verified | 1B-NBS-PD-P41-0100-01 HGR-0066 need to have full thread engagement at eye bolt "2 thrd min." | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02330 | Verified | 1B-NBS-PD-P41-0103-01 Install u bolt per the detail HGR-0128 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02331 | Verified | 1B-NBS-PD-P41-0103-01 Install support per the detail HGR-0129 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02332 | Verified | 1B-NBS-PD-P41-0103-01 Install support per the detail HGR-0130 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02333 | Verified | 1B-NBS-PD-P41-0105-01 Install u bolts per the detail HGR 0119, HGR-0120, HGR-0121 and HGR-0122 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02334 | Verified | 1B-NBS-PD-P41-106-01 Install u bolts per the detail HGR-0123 and HGR-0125 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-02 | NBS-02 | PI02335 | Verified | 1B-NBS-PD-P41-0106-01 Install threaded cap to 1B-NBS-V-0107 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-02 | NBS-02 | PI02336 | Verified | 1B-NBS-PD-P41-0107-01 Install u bolts per the detail HGR-0126 and HGR-0127 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02337 | Verified | 1B-NBS-PD-P41-0107-01 Install 1B-NBS-RC-0106 | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
NBS-02 | NBS-02 | PI02338 | Verified | 1B-HRSG-HP Drum Nooter NBS piping requires a support | B | P | Bobby Williams | McD | 2019-07-18 | Bobby Williams | Const | 2019-07-29 | Bobby Williams | 2019-08-01 | Kelvin Cook
NBS-02 | NBS-02 | PI02339 | Verified | 1B-NBS-PD-P41-0110-01 Install u bolts per the detail HGR-0102 and HGR-0103 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02340 | Verified | 1B-NBS-PD-P41-0111-01 Install u bolts per the detail HGR-0110 and HGR-0111 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-02 | NBS-02 | PI02341 | Verified | 1B-NBS-PD-P41-0111-01 Install support per the detail HGR-0109 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02342 | Verified | 1B-NBS-PD-P41-0111-01 Broken cover on 1B-NBS-PI-0111 | B | I | Gonzalo Pena | McD | 2019-07-18 | Gonzalo Pena | Const | 2019-07-23 | Gonzalo Pena | 2019-08-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02343 | Verified | 1B-NBS-PD-P41-0112-01 Install HGR-0108 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02344 | Verified | 1B-NBS-PD-P41-0112-01 Install 1B- NBS-RC-0111 | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
NBS-02 | NBS-02 | PI02345 | Verified | 1B-NBS-PD-P41-0115-01 Install u bolts per the detail HGR-0112, HGR-0113 and HGR-0114 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02346 | Verified | 1B-NBS-PD-P41-0115-01 1B-NBS-PCV-0115 is installed up side down stem needs to be up. | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02347 | Verified | 1B-NBS-PD-P41-0116-01 Install HGR-0115 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02348 | Verified | 1B-NBS-PD-P41-0116-01 Install threaded cap to 1B-NBS-V-0117 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02349 | Verified | 1B-NBS-PD-P41-0117-01 Install u bolt per the detail HGR-0117 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02350 | Verified | 1B-NBS-PD-P41-0117-01 Install 1B-NBS-RC-0116 | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
NBS-02 | NBS-02 | PI02351 | Verified | On ISO 1B-NBS-PD-P41-0100-01 pipe support 1B-NBS-PD-HGR-0069 has loose nuts at top | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-08-01 | Kelvin Cook
NBS-02 | NBS-02 | PI02356 | Verified | On ISO 1B-NBS-PD-P41-0102-02 pipe support 1B-NBS-PD-HGR-0078 not installed | B | P | Damon Turner | McD | 2019-07-18 | Damon Turner | Const |  |  | 2019-10-01 | Kelvin Cook
NBS-02 | NBS-02 | PI02357 | Verified | On ISO 1B-NBS-PD-P41-0102-02 pipe support 1B-NBS-PD-HGR-0077 is incomplete | B | P | Damon Turner | McD | 2019-07-18 | Damon Turner | Const |  |  | 2019-10-01 | Kelvin Cook
NBS-02 | NBS-02 | PI02557 | Verified | 1BNBS-PI-0100 incorrectly tagged (Has FGS fuel gas tag). | B | I | Gonzalo Pena | McD | 2019-07-23 | Gonzalo Pena | Const | 2019-07-25 | Gonzalo Pena | 2019-10-03 | Nelson Eichelberger
NBS-02 | NBS-02 | PI02558 | Verified | 2-1B-NBS-0103-151X1-NI vent not plumb | B | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-08 | Terry Deaton | 2019-10-03 | Nelson Eichelberger
NBS-02 | NBS-02 | PI02559 | Verified | 1BNBS-PI-0106 - broken needle on indicator. | A | I | Gonzalo Pena | McD | 2019-07-23 | Gonzalo Pena | Const | 2019-07-25 | Gonzalo Pena | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02560 | Verified | PCVs 0105, 0115 removed for testing at time of walkdown | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02561 | Verified | PI-0106, 0116 removed for testing at time of walkdown | A | I | Gonzalo Pena | McD | 2019-07-23 | Gonzalo Pena | Const | 2019-07-25 | Gonzalo Pena | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02562 | Verified | Blinds remain installed at SRVs -0105, -0115-, -0103 | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-02 | NBS-02 | PI02563 | Verified | Loose support at PI-0100 drain tubing | A | I | Gonzalo Pena | McD | 2019-07-23 | Gonzalo Pena | Const | 2019-07-25 | Gonzalo Pena | 2019-08-15 | Dave Goldak
NBS-02 | NBS-02 | PI02564 | Verified | Pipe supports for Nooter piping at High Pressure branch not per standard. Attached to handrail. | B | P | Bobby Williams | McD | 2019-07-23 | Bobby Williams | Const | 2019-07-30 | Bobby Williams | 2019-10-03 | Nelson Eichelberger
NBS-02 | NBS-02 | PI02565 | Verified | Bent tubing at bleed line/drain at PI-0111 | A | I | Gonzalo Pena | McD | 2019-07-23 | Gonzalo Pena | Const | 2019-07-25 | Gonzalo Pena | 2019-08-08 | Dave Goldak
NBS-02 | NBS-02 | PI02841 | Verified | 1B-NBS-PD-P41-0103-01 - rain cap not installed. | B | P | Terry Deaton | McD | 2019-07-27 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
NBS-02 | NBS-02 | PI02842 | Verified | 1B-NBS-PD-P41-0107-01 - rain cap not installed. | B | P | Terry Deaton | McD | 2019-07-27 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
NBS-02 | NBS-02 | PI02843 | Verified | 1B-NBS-PD-P41-0112-01 - rain cap not installed. | B | P | Terry Deaton | McD | 2019-07-27 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
NBS-02 | NBS-02 | PI02844 | Verified | 1B-NBS-PD-P41-0117-01 - rain cap not installed. | B | P | Terry Deaton | McD | 2019-07-27 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
NBS-02 | NBS-02 | PI09430 | Verified | Clean and paint entire system piping. | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-04-08 | Bernard Stasse
NBS-02 | NBS-02 | PI09431 | Verified | Install protective caps for 1B-NBS-FXH-0100A & B Flex Hose quick disconnect fittings. | C | M | Kelvin Cook | McD | 2019-10-11 | Kelvin Cook | Comm | 2020-02-10 | Kelvin Cook | 2020-04-08 | Bernard Stasse
NBS-02 | NBS-02 | PI09432 | Verified | Install tags for all system components. | C | P | Tim Green | McD | 2019-10-11 | Tim Green | Comm | 2021-01-22 | Eric Policarpio | 2021-01-22 | Eric Policarpio
NBS-02 | NBS-02 | PI09433 | Verified | Connect rod hanger at Line No. 2-1A-NBS-0101 down stream of 1B-NBS-FXH-0100B; SS flex hose | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Tim Green | 2020-02-10 | Nelson Eichelberger
NBS-02 | NBS-02 | PI09434 | Verified | Relocate 1BNBS-PI-0100; Nitrogen Discharge Header Pressure Indicator between 1B-NBS-V-0100A and 1B-NBS-V-0100B; Nitrogen Discharge Isolation Valve, to improve operator visual contact. | D | I | Michael Law | McD | 2019-10-11 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-07-07 | Nelson Eichelberger
NBS-02 | NBS-02 | PI09435 | Verified | Connect Instrument Air tubing to 1BNBS-PV-0100B; Pressure Control Valve | B | I | Gonzalo Pena | McD | 2019-10-11 | Gonzalo Pena | Comm | 2019-12-18 | Blake Boudreaux | 2019-12-18 | Blake Boudreaux
NBS-02 | NBS-02 | PI09436 | Verified | Remove carbon contamination at 1BNBS-PV-0100A; Pressure Control Valve | C | X | Tim Green | McD | 2019-10-11 | Tim Green | Comm | 2020-07-24 | Tim Green | 2020-08-14 | Nelson Eichelberger
NBS-02 | NBS-02 | PI09437 | Verified | Ensure all Safety Relief Valve certifications are placed in Turnover Package. | C | M | Ed Gober | McD | 2019-10-11 | Ed Gober | Comm | 2019-10-14 | Ed Gober | 2019-10-28 | Shannon Scott
NBS-02 | NBS-02 | PI09438 | Verified | Remove rope, wire, tape, tie wraps, spool tags from all system piping and components. | C | C | Tim Gallegos | McD | 2019-10-11 | Tim Gallegos | Comm | 2020-05-11 | Tim Gallegos | 2020-08-05 | Nelson Eichelberger
NBS-02 | NBS-02 | PI09478 | Verified | 2-1B-NBS-0112 missing support on vent line vertical pipe | B | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-02-10 | Tim Green | 2020-03-06 | Nelson Eichelberger
NBS-02 | NBS-02 | PI09479 | Verified | 2-1B-NBS-0112 support is loose and line to level and straighten up | B | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-02-11 | Tim Green | 2020-03-06 | Nelson Eichelberger
NBS-02 | NBS-02 | PI09480 | Verified | 1B-NBS-PI-0111 remove carbon contamination on PI and tubing | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-04-08 | Bernard Stasse
NBS-02 | NBS-02 | PI09481 | Verified | Tag all valves with permanent tag ID - N2 lines going to HP, IP and LP drums | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-02-04 | James Beech | 2020-04-08 | Bernard Stasse
NBS-02 | NBS-02 | PI09482 | Verified | Paint all welds and supports - N2 lines going to HP, IP and LP drums | C | X | Johnny Campbell | McD | 2019-10-11 | Johnny Campbell | Comm | 2020-04-23 | Johnny Campbell | 2020-04-24 | Mark Williamson
NBS-02 | NBS-02 | PI09483 | Verified | Clean and remove all tie wraps, plastics, ropes on the lines going to drums - N2 lines going to HP, IP and LP drums | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Tim Green | 2020-04-08 | Bernard Stasse
NBS-02 | NBS-02 | PI09484 | Verified | 1B-NBS-PCV-0115, no lubrication on bolts and backward nut installed to correct | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-03-27 | James Beech | 2020-04-08 | Bernard Stasse
NBS-02 | NBS-02 | PI09485 | Verified | 1B-NBS-V-0117 remove teflon on valve vent side | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Tim Green | 2020-04-08 | Bernard Stasse
NBS-02 | NBS-02 | PI09486 | Verified | 1B-NBS-V-0117 valve handle to provide stops and to correct a pinch point to another valve handle | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-08 | Bernard Stasse
NBS-02 | NBS-02 | PI09487 | Verified | 1B-NBS-SRV-0105 Nuts to correct the under flush and was installed backwards | B | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-03-09 | Tim Green | 2020-04-08 | Bernard Stasse
NBS-02 | NBS-02 | PI09488 | Verified | 1B-NBS-V-0105 u-bolt support to tighten going to PCV | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-02-06 | James Beech | 2020-04-08 | Bernard Stasse
NBS-02 | NBS-02 | PI09489 | Verified | 1B-NBS-PCV-0105, installation of PCV is lower than the SRV. To verify if this design is correct | C | P | Kelvin Cook | McD | 2019-10-11 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-08 | Bernard Stasse
NBS-02 | NBS-02 | PI09490 | Verified | 1B-NBS-PI-0106 replace broken PI - dial broken, needle up | B | I | Gonzalo Pena | McD | 2019-10-11 | Gonzalo Pena | Comm | 2019-12-18 | Blake Boudreaux | 2019-12-18 | Blake Boudreaux
NBS-02 | NBS-02 | PI09491 | Verified | 1B-NBS-V-0107 valve handle to correct the pinch point on another valve handle | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-03-27 | James Beech | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI02287 | Verified | 1A-NBS-FXH-0100A needs to be longer | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-01 | NBS-01 | PI02288 | Verified | 1A-NBS-FXH-0100B needs to be longer | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-01 | NBS-01 | PI02289 | Verified | 1A-NBS-PD-P41-0100-01 install vent valve per new revision | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-22 | Kelvin Cook
NBS-01 | NBS-01 | PI02290 | Verified | 1A-NBS-PD-P41-0101-01 install vent valve per new revision | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-22 | Kelvin Cook
NBS-01 | NBS-01 | PI02291 | Verified | Cold Galvanize all supports | C | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-08-27 | Kelvin Cook
NBS-01 | NBS-01 | PI02292 | Verified | Complete all pressure testing | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-25 | Terry Deaton | 2019-07-25 | Kelvin Cook
NBS-01 | NBS-01 | PI02293 | Verified | Grout all supports | B | P | Johnny Campbell | McD | 2019-07-18 | Johnny Campbell | Const | 2019-07-31 | Jack Fields | 2019-08-08 | Kelvin Cook
NBS-01 | NBS-01 | PI02294 | Verified | 1A-NBS-PD-P41-0100 HGR-0004 need to have full thread engagement at eye bolt "2 thrd min." | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-01 | NBS-01 | PI02295 | Verified | 1A-NBS-V-0101A make tubing connection | A | I | Gonzalo Pena | McD | 2019-07-18 | Gonzalo Pena | Const | 2019-07-19 | Gonzalo Pena | 2019-07-19 | Kelvin Cook
NBS-01 | NBS-01 | PI02296 | Verified | 1A-NBS-V-0101B make tubing connection | A | I | Gonzalo Pena | McD | 2019-07-18 | Gonzalo Pena | Const | 2019-07-19 | Gonzalo Pena | 2019-07-19 | Kelvin Cook
NBS-01 | NBS-01 | PI02297 | Verified | 1A-NBS-PD-P41-0103-01 Bolts are too long at connection to 1A-NBS-SRV-0103 | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-01 | NBS-01 | PI02298 | Verified | 1A-NBS-PD-P41-0103-01 Install HGR-0063 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-01 | NBS-01 | PI02299 | Verified | 1A-NBS-PD-P41-0103-01 Install 1A-NBS-RC-0103 | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
NBS-01 | NBS-01 | PI02300 | Verified | 1A-NBS-PD-P41-0105-01 Install HGR-0054 and HGR-0055 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-19 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-01 | NBS-01 | PI02301 | Verified | 1A-NBS-PD-P41-0105-01 Fill in extra holes in HGR-0057, grind smooth and cold galvanize. | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-01 | NBS-01 | PI02302 | Verified | 1A-NBS-PD-P41-0106-01 Install threaded cap at 1A-NBS-V-0107 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-19 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-01 | NBS-01 | PI02303 | Verified | 1A-NBS-PD-P41-0106-01 Install u bolt proper per the detail HGR-0123 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-19 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-01 | NBS-01 | PI02304 | Verified | 1A-NBS-PD-P41-0106-01 Install support per the detail HGR-0124 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-01 | NBS-01 | PI02305 | Verified | 1A-HRSG-HP Drum Nooter NBS piping requires a support | B | P | Bobby Williams | McD | 2019-07-18 | Bobby Williams | Const | 2019-07-29 | Bobby Williams | 2019-08-01 | Kelvin Cook
NBS-01 | NBS-01 | PI02306 | Verified | 1A-NBS-PD-P41-0110-01 Install HGR-0037 and 0038 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-19 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-01 | NBS-01 | PI02307 | Verified | 1A-NBS-PD-P41-0111-01 Fix the u bolt at HGR-0044 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-19 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-01 | NBS-01 | PI02308 | Verified | 1A-NBS-PD-P41-0111-01 Install threaded cap to 1A-NBS-V-0112 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-19 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-01 | NBS-01 | PI02309 | Verified | 1A-NBS-PD-P41-0112-01 Install u bolt per the detail | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-19 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-01 | NBS-01 | PI02310 | Verified | 1A-NBS-PD-P41-0112-01 Install 1A-NBS-RC-0111 | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
NBS-01 | NBS-01 | PI02311 | Verified | 1A-NBS-PD-P41-0115-01 Install HGR-0113 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-01 | NBS-01 | PI02312 | Verified | 1A-NBS-PD-P41-0116-01 Install threaded cap to 1A-NBS-V-0117 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-01 | NBS-01 | PI02313 | Verified | 1A-NBS-PD-P41-0117-01 Install u bolts proper per the details, HGR-0051, HGR-0052 and HGR-0053 | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-26 | Kelvin Cook
NBS-01 | NBS-01 | PI02314 | Verified | 1A-NBS-PD-P41-0107-01 Install 1A-NBS-RC-0116 | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
NBS-01 | NBS-01 | PI02352 | Verified | On ISO 1A-NBS-PD-P41-0100-01 pipe support 1A-NBS-PD-HGR-0004 out of leveled | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-01 | NBS-01 | PI02353 | Verified | On ISO 1A-NBS-PD-P41-0101-01 pipe support 1A-NBS-PD-HGR-0001 out of leveled | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-01 | NBS-01 | PI02354 | Verified | On ISO 1A-NBS-PD-P41-0117-01 1A-NBS-RC-0116 is not installed | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-20 | Kelvin Cook
NBS-01 | NBS-01 | PI02355 | Verified | On ISO 1A-NBS-PD-P41-0117-01 1A-NBS-PD-HGR-0053 is loose | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-01 | NBS-01 | PI02358 | Verified | On ISO 1A-NBS-PD-P41-0112-01 specialty item 1A-NBS-RC-0111 is not installed | B | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-27 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-01 | NBS-01 | PI02359 | Verified | On ISO 1A-NBS-PD-P41-0117-01 1A-NBS-PD-HGR-0052 is not installed | A | P | Terry Deaton | McD | 2019-07-18 | Terry Deaton | Const | 2019-07-22 | Terry Deaton | 2019-07-27 | Kelvin Cook
NBS-01 | NBS-01 | PI09421 | Verified | Clean and paint entire system piping. | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09422 | Verified | Install protective caps for 1A-NBS-FXH-0100A & B Flex Hose quick disconnect fittings. | C | M | Reggie Brown | McD | 2019-10-11 | Reggie Brown | Comm | 2020-02-10 | Kelvin Cook | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09423 | Verified | Install tags for all system components. | C | P | Tim Green | McD | 2019-10-11 | Tim Green | Comm | 2021-01-22 | Eric Policarpio | 2021-01-22 | Eric Policarpio
NBS-01 | NBS-01 | PI09424 | Verified | Loose U-Bolt at Line No. 2-1A-NBS-0102, Train B discharge piping. | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Tim Green | 2020-07-07 | Nelson Eichelberger
NBS-01 | NBS-01 | PI09425 | Verified | Relocate 1ANBS-PI-0100; Nitrogen Discharge Header Pressure Indicator between 1A-NBS-V-0100A and 1B-NBS-V-0100B; Nitrogen Discharge Isolation Valve, to improve operator visual contact. | D | M | Michael Law | McD | 2019-10-11 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-01-05 | Keith Pollock
NBS-01 | NBS-01 | PI09426 | Verified | Remove teflon tape from 1A-NBS-V-0101A; Nitrogen supply .75 inch isolation valve to 1A-NBS-PC-0100A | C | M | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-02-12 | James Beech | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09427 | Verified | 1A-NBS-PV-0100A Pneumatic Control Box access is impeded by conduit and angle iron. | C | E | Chris Colvin | McD | 2019-10-11 | Chris Colvin | Comm | 2020-05-04 | Matt Gilmore | 2020-07-07 | Nelson Eichelberger
NBS-01 | NBS-01 | PI09428 | Verified | Ensure all Safety Relief Valve certifications are placed in Turnover Package. | C | M | Ed Gober | McD | 2019-10-11 | Ed Gober | Comm | 2019-10-14 | Ed Gober | 2019-10-28 | Shannon Scott
NBS-01 | NBS-01 | PI09429 | Verified | Remove rope, wire, tape, tie wraps, spool tags from all system piping and components. | C | C | Tim Gallegos | McD | 2019-10-11 | Tim Gallegos | Comm | 2020-05-11 | Tim Gallegos | 2020-08-05 | Nelson Eichelberger
NBS-01 | NBS-01 | PI09463 | Verified | 1A-NBS-PI-0111 tighten the U-bolt support between the PI and vent valve V-0112 | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Tim Green | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09464 | Verified | 1B-NBS-V-0112 remove teflon tape | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Tim Green | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09465 | Verified | Tag all valves with permanent tag ID - N2 lines going to HP, IP and LP drums | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-02-04 | James Beech | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09466 | Verified | Paint all welds and supports - N2 lines going to HP, IP and LP drums | C | X | Jerry Smith | McD | 2019-10-11 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09467 | Verified | Clean and remove all tie wraps, plastics, ropes on the lines going to drums - N2 lines going to HP, IP and LP drums | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Tim Green | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09468 | Verified | 1A-NBS-PI-0116 sensor line on PI not installed properly. To level | C | I | Gonzalo Pena | McD | 2019-10-11 | Gonzalo Pena | Comm |  |  | 2019-12-18 | Blake Boudreaux
NBS-01 | NBS-01 | PI09469 | Verified | 1A-NBS-V-0105 remove wire on handle | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Tim Green | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09470 | Verified | 1A-NBS-PI-0106 replace broken PI - gauge cracked | B | I | Gonzalo Pena | McD | 2019-10-11 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
NBS-01 | NBS-01 | PI09471 | Verified | 1A-NBS-V-0105 pinch point on valve handle | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Tim Green | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09472 | Verified | 1A-NBS-PCV-0105 bolts on PCV to lubricate | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Tim Green | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09473 | Verified | 1A-NBS-PI-0105 cracked PI to replace | C | I | Gonzalo Pena | McD | 2019-10-11 | Gonzalo Pena | Comm | 2020-01-03 | Gonzalo Pena | 2020-01-10 | Blake Boudreaux
NBS-01 | NBS-01 | PI09474 | Verified | 1A-NBS-SRV-0105 correct backward nut | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Tim Green | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09475 | Verified | 1A-NBS-V-0107 remove teflon tape on vent | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Tim Green | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09476 | Verified | 1A-NBS-V-0107 pinch point on valve | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-01-16 | Tim Green | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI09477 | Verified | Line between NBS-PCV-0105 and SRV-0105 out of level | C | P | James Beech | McD | 2019-10-11 | James Beech | Comm | 2020-02-04 | James Beech | 2020-04-08 | Bernard Stasse
NBS-01 | NBS-01 | PI15845 | Verified | Missing cap at 1A-NBS-V-0117. | C | P | Tim Green | McD | 2020-01-10 | Tim Green | Comm | 2020-06-02 | Tim Green | 2020-08-05 | Nelson Eichelberger
NJS-01 | NJS-01 | PI00211 | Verified | Wipe down inside of bus duct from the transformer - back. | A | E | Shannon Savoy | McD | 2019-02-28 | Shannon Savoy | Const | 2019-03-01 | Mike Tabbert | 2019-03-04 | Shannon Scott
NJS-01 | NJS-01 | PI00213 | Verified | Torque grounds in rear compartment of 10-NJS-XFM-0001A. | B | E | Logan Holland | McD | 2019-02-28 | Logan Holland | Const | 2019-09-05 | Logan Holland | 2019-09-05 | Mike Tabbert
NJS-01 | NJS-01 | PI00215 | Verified | Patch foam door protector on inside of rear compartment of 10-NJS-XFM-0001A. | C | E | Luis Cantu | McD | 2019-02-28 | Luis Cantu | Const | 2019-07-24 | Ken Mundy | 2019-07-29 | Mike Tabbert
NJS-01 | NJS-01 | PI00217 | Verified | 10-NJS-XFM-0001A space heaters are on temp. power - hook up permanent cables after perm. power. | C | E | Logan Holland | McD | 2019-02-28 | Logan Holland | Const | 2019-06-21 | Logan Holland | 2019-06-21 | Logan Holland
NJS-01 | NJS-01 | PI00219 | Verified | 10-NJS-XFM-0001A - missing 2 bolts above panel on east side & 1 on west (top of enclosure). | B | E | Shannon Savoy | McD | 2019-02-28 | Shannon Savoy | Const | 2019-03-01 | Mike Tabbert | 2019-03-14 | Danny Pase
NJS-01 | NJS-01 | PI00220 | Verified | Braids in 10-NJS-XFM-0001A are hot bolted. Torque after commissioning. | B | E | Logan Holland | McD | 2019-02-28 | Logan Holland | Const | 2019-06-21 | Logan Holland | 2019-06-21 | Logan Holland
NJS-01 | NJS-01 | PI00222 | Verified | Tighten all bolts on 10-NJS-BD-0001A | A | E | Shannon Savoy | McD | 2019-02-28 | Shannon Savoy | Const | 2019-03-01 | Mike Tabbert | 2019-03-01 | Mike Tabbert
NJS-01 | NJS-01 | PI00224 | Verified | Cannot open heater cover on 10-NJS-BD-0001A due to cable tray interference. | B | E | Shannon Savoy | McD | 2019-02-28 | Shannon Savoy | Const | 2019-04-10 | Mike Tabbert | 2019-04-10 | Mike Tabbert
NJS-01 | NJS-01 | PI00226 | Verified | Clean interior & remove dessicant bags in 10-NJS-XVM-0001A | A | E | Shannon Savoy | McD | 2019-02-28 | Shannon Savoy | Const | 2019-03-01 | Mike Tabbert | 2019-03-01 | Mike Tabbert
NJS-01 | NJS-01 | PI00228 | Verified | Label all rear compartments on the Main PDC. | C | E | Mike Tabbert | McD | 2019-02-28 | Mike Tabbert | Const | 2020-04-28 | Charles Worthington | 2020-06-02 | Randy Carpenter
NJS-01 | NJS-01 | PI00231 | Verified | Weld transformer in place. | B | E | Luis Cantu | McD | 2019-02-28 | Luis Cantu | Const | 2019-04-30 | Shannon Savoy | 2019-06-14 | Mike Tabbert
NJS-01 | NJS-01 | PI00233 | Verified | Complete paperwork. | A | E | Shannon Savoy | McD | 2019-02-28 | Shannon Savoy | Const | 2019-03-04 | Ed Gober | 2019-03-04 | Ed Gober
NJS-01 | NJS-01 | PI04813 | Verified | Selector switch SS33 need new cover | C | E | Mike Tabbert | McD | 2019-09-06 | Mike Tabbert | Comm | 2020-04-06 | Mike Tabbert | 2020-04-06 | Randy Carpenter
NJS-01 | NJS-01 | PI04814 | Verified | Final clean / wipe off on the cabinets at handover to operations | C | E | Jonathan Donham | McD | 2019-09-06 | Jonathan Donham | Comm | 2020-04-09 | Jonathan Donham | 2021-03-03 | John Watts
NJS-01 | NJS-01 | PI04817 | Verified | Paint transformer weld on pads | C | E | Chris Colvin | McD | 2019-09-06 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Randy Carpenter
NJS-01 | NJS-01 | PI08449 | Verified | Move in GSN, cable 10NJSC0013 to NJS-02 | C | E | Mike Tabbert | McD | 2019-10-02 | Mike Tabbert | Comm | 2019-10-18 | Mike Tabbert | 2019-10-18 | Eric Policarpio
NJS-01 | NJS-01 | PI08450 | Verified | Move in GSN cable 10-NJSC0040 to subsystem NJS-02 | C | E | Mike Tabbert | McD | 2019-10-02 | Mike Tabbert | Const | 2019-10-18 | Mike Tabbert | 2019-10-18 | Eric Policarpio
NJS-01 | NJS-01 | PI16158 | Verified | Relay test report to submit SEL-751A and BE1-25 | C | E | Jonathan Donham | McD | 2020-01-20 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2021-03-03 | John Watts
NJS-01 | NJS-01 | PI16204 | Verified | 10-NJS-XFM-0001A - Missing ground wires across the flex conduit | D | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm | 2020-01-29 | Randy Carpenter | 2020-02-05 | Shannon Scott
NJS-01 | NJS-01 | PI16681 | Verified | 10-NJS-XFM-0001A - 10-NJS-SWG-0001A PR4 is unable to communicate through Comm Port F on the SEL-751A feeder protection relay. The relay still functions properly - just unable to get into it with software. | B | E | Jonathan Donham | McD | 2020-02-07 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-07 | Bernard Stasse
NJS-02 | NJS-02 | PI00212 | Verified | Wipe down inside of bus duct from the transformer - back. | A | E | Shannon Savoy | McD | 2019-02-28 | Shannon Savoy | Const | 2019-03-01 | Mike Tabbert | 2019-03-04 | Shannon Scott
NJS-02 | NJS-02 | PI00214 | Verified | Torque grounds in rear compartment of 10-NJS-XFM-0001B. | B | E | Logan Holland | McD | 2019-02-28 | Logan Holland | Const | 2019-09-05 | Logan Holland | 2019-09-05 | Mike Tabbert
NJS-02 | NJS-02 | PI00216 | Verified | Patch foam door protector on inside of rear compartment of 10-NJS-XFM-0001B. | C | E | Luis Cantu | McD | 2019-02-28 | Luis Cantu | Const | 2019-07-24 | Ken Mundy | 2019-07-29 | Mike Tabbert
NJS-02 | NJS-02 | PI00218 | Verified | 10-NJS-XFM-0001B space heaters are on temp. power - hook up permanent cables after perm. power. | C | E | Logan Holland | McD | 2019-02-28 | Logan Holland | Const | 2019-06-21 | Logan Holland | 2019-06-21 | Mike Tabbert
NJS-02 | NJS-02 | PI00221 | Verified | Braids in 10-NJS-XFM-0001B are hot bolted. Torque after commissioning. | B | E | Luis Cantu | McD | 2019-02-28 | Luis Cantu | Const | 2019-06-07 | Shannon Savoy | 2019-06-21 | Mike Tabbert
NJS-02 | NJS-02 | PI00223 | Verified | Tighten all bolts on 10-NJS-BD-0001B | A | E | Shannon Savoy | McD | 2019-02-28 | Shannon Savoy | Const | 2019-03-01 | Mike Tabbert | 2019-03-01 | Mike Tabbert
NJS-02 | NJS-02 | PI00225 | Verified | Cannot open heater cover on 10-NJS-BD-0001B due to cable tray interference. | B | E | Shannon Savoy | McD | 2019-02-28 | Shannon Savoy | Const | 2019-04-10 | Mike Tabbert | 2019-04-10 | Mike Tabbert
NJS-02 | NJS-02 | PI00227 | Verified | Clean interior & remove dessicant bags in 10-NJS-XVM-0001B | A | E | Shannon Savoy | McD | 2019-02-28 | Shannon Savoy | Const | 2019-03-01 | Mike Tabbert | 2019-03-01 | Mike Tabbert
NJS-02 | NJS-02 | PI00229 | Verified | Strap conduit on transformer B heater cover. | B | E | Shannon Savoy | McD | 2019-02-28 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-02 | Shannon Scott
NJS-02 | NJS-02 | PI00230 | Verified | Red line wiring diagram 10-NJS-EE-WIR-0010 to show proper connection for cable 10NJSC0040 (or check wir. dia. revision). | B | E | Mike Tabbert | McD | 2019-02-28 | Mike Tabbert | Const | 2019-03-04 | Mike Tabbert | 2019-06-26 | Logan Holland
NJS-02 | NJS-02 | PI00232 | Verified | Weld transformer in place. | B | E | Luis Cantu | McD | 2019-02-28 | Luis Cantu | Const | 2019-06-07 | Shannon Savoy | 2019-06-14 | Mike Tabbert
NJS-02 | NJS-02 | PI04815 | Verified | Final clean / wipe off on the cabinets at handover to operations | C | E | Jonathan Donham | McD | 2019-09-06 | Jonathan Donham | Comm | 2020-04-09 | Jonathan Donham | 2021-03-03 | John Watts
NJS-02 | NJS-02 | PI04816 | Verified | Paint transformer weld on pads | C | E | Chris Colvin | McD | 2019-09-06 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Randy Carpenter
NJS-02 | NJS-02 | PI16159 | Verified | Missing: SEL 751A-1B, CTs 4000/5 test records | C | E | Jonathan Donham | McD | 2020-01-20 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2021-03-03 | John Watts
NJS-02 | NJS-02 | PI16205 | Verified | 10-NJS-XFM-0001B - Missing ground wires across the flex conduit | D | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm | 2020-01-29 | Randy Carpenter | 2020-02-05 | Shannon Scott
NJS-03 | NJS-03 | PI01451 | Verified | 10-NJS-XFM-0003A, Transformer to be welded in place | A | E | Luis Cantu | McD | 2019-06-11 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-06-14 | Mike Tabbert
NJS-03 | NJS-03 | PI01452 | Verified | Cooling Tower PDC , maintain cleanliness, all material provided by EATON maintain in safe place. | C | E | Luis Cantu | McD | 2019-06-11 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-06-28 | Mike Tabbert
NJS-03 | NJS-03 | PI01456 | Verified | Install arc flash chute on cooling tower PDC. | A | E | Luis Cantu | McD | 2019-06-11 | Luis Cantu | Const | 2019-06-17 | Luis Cantu | 2019-06-18 | Mike Tabbert
NJS-03 | NJS-03 | PI01457 | Verified | Need arc flash label on 10-NJS-SWG-0003A in the cooling tower PDC. | B | E | Mike Tabbert | McD | 2019-06-11 | Mike Tabbert | Const | 2019-07-19 | Mike Tabbert | 2019-07-19 | Mike Tabbert
NJS-03 | NJS-03 | PI01460 | Verified | Install breakers in 10-NJS-SWG-0003A in cooling tower PDC. | B | E | Luis Cantu | McD | 2019-06-11 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-06-28 | Mike Tabbert
NJS-03 | NJS-03 | PI01461 | Verified | Primary cables in 10-NJS-XFM-0003A are hot bolted at the cooling tower PDC. Torque after commissioning. | B | E | Logan Holland | McD | 2019-06-11 | Logan Holland | Const | 2019-06-21 | Logan Holland | 2019-06-21 | Logan Holland
NJS-03 | NJS-03 | PI01464 | Verified | Torque braids in 10-NJS-XFM-0003A at the cooling tower PDC. After commissioning. | B | E | Logan Holland | McD | 2019-06-11 | Logan Holland | Const | 2019-06-21 | Logan Holland | 2019-06-21 | Logan Holland
NJS-03 | NJS-03 | PI01465 | Verified | Tighten 2 bolts at the non-seg bus connection to the cooling tower PDC. | A | E | Luis Cantu | McD | 2019-06-11 | Luis Cantu | Const | 2019-06-11 | Luis Cantu | 2019-06-18 | Luis Cantu
NJS-03 | NJS-03 | PI01466 | Verified | Terminal blocks in DCS cab EXP 3-2 10-DCS-CAB-0303 Rear are missing tags. Cooling tower PDC. | B | E | Mike Tabbert | McD | 2019-06-11 | Mike Tabbert | Const | 2019-08-08 | Mike Tabbert | 2019-08-16 | Shannon Scott
NJS-03 | NJS-03 | PI18131 | Verified | 10-NJS-XFM-0003A - TEMP Hi alarm on 10-NJS-XFM-0003A Alarm | C | E | Jonathan Donham | McD | 2020-03-20 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2020-04-30 | John Watts
NJS-04 | NJS-04 | PI01453 | Verified | 10-NJS-XFM-0003B, Transformer to be welded in place | A | E | Luis Cantu | McD | 2019-06-11 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-06-14 | Mike Tabbert
NJS-04 | NJS-04 | PI01454 | Verified | 10MH008, complete all grounding, conduit identification and cable supports in manhole. | B | E | Dustin Futrell | McD | 2019-06-11 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-28 | Mike Tabbert
NJS-04 | NJS-04 | PI01455 | Verified | Cooling Tower PDC , maintain cleanliness, all material provided by EATON maintain in safe place. | C | E | Luis Cantu | McD | 2019-06-11 | Luis Cantu | Const | 2019-06-12 | Luis Cantu | 2019-06-21 | Mike Tabbert
NJS-04 | NJS-04 | PI01458 | Verified | Need arc flash label on 10-NJS-SWG-0003B in cooling tower PDC. | B | E | Mike Tabbert | McD | 2019-06-11 | Mike Tabbert | Const | 2019-07-19 | Mike Tabbert | 2019-07-19 | Mike Tabbert
NJS-04 | NJS-04 | PI01459 | Verified | Install breakers in 10-NJS-SWG-0003B in cooling tower PDC. | B | E | Luis Cantu | McD | 2019-06-11 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-06-28 | Mike Tabbert
NJS-04 | NJS-04 | PI01462 | Verified | Primary cables in 10-NJS-XFM-0003B are hot bolted at the cooling tower PDC. Torque after commissioning. | B | E | Logan Holland | McD | 2019-06-11 | Logan Holland | Const | 2019-06-21 | Logan Holland | 2019-06-21 | Logan Holland
NJS-04 | NJS-04 | PI01463 | Verified | Torque braids in 10-NJS-XFM-0003B at the cooling tower PDC. After commissioning. | B | E | Logan Holland | McD | 2019-06-11 | Logan Holland | Const | 2019-06-21 | Logan Holland | 2019-06-21 | Logan Holland
NJS-04 | NJS-04 | PI01467 | Verified | Need new tags (faded) for 10-NJSC0043-5 and 10-NJSC0043-6 in DCS cab EXP 3-2 10-DCS-CAB-0302 Rear in the cooling tower PDC. | B | E | Dustin Futrell | McD | 2019-06-11 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-11 | Shannon Scott
NJS-04 | NJS-04 | PI01468 | Verified | Need edge guard in DCS cab EXP 3-2 10-DCS-CAB-0302 Rear in the cooling tower PDC. | B | E | Luis Cantu | McD | 2019-06-11 | Luis Cantu | Const | 2019-07-19 | Luis Cantu | 2019-07-23 | Shannon Scott
NJS-04 | NJS-04 | PI01469 | Verified | Install arc flash chute on cooling tower PDC. | A | E | Luis Cantu | McD | 2019-06-11 | Luis Cantu | Const | 2019-06-17 | Luis Cantu | 2019-06-18 | Mike Tabbert
NJS-05 | NJS-05 | PI00234 | Verified | 10-NJS-XFM-0004A Install New Offset Bus Plates for splice between transfomer and Bus Duct. | A | E | Shannon Savoy | EAT | 2019-03-01 | Shannon Savoy | Const | 2019-03-06 | Mike Tabbert | 2019-03-06 | Mike Tabbert
NJS-05 | NJS-05 | PI00235 | Verified | 10-NJS-XFM-0004A Install Braids From Transformer to Bus Duct. | A | E | Shannon Savoy | McD | 2019-03-01 | Shannon Savoy | Const | 2019-03-06 | Mike Tabbert | 2019-03-06 | Mike Tabbert
NJS-05 | NJS-05 | PI00236 | Verified | 10-NJS-XFM-0004A Weld Transformer Down to Weld Plates when all electrical conections have been made. | B | E | Luis Cantu | McD | 2019-03-01 | Luis Cantu | Const | 2019-06-07 | Shannon Savoy | 2019-06-14 | Mike Tabbert
NJS-05 | NJS-05 | PI00237 | Verified | Cable Tray Main PDC, Install cable tray grounding. | A | E | Shannon Savoy | McD | 2019-03-01 | Shannon Savoy | Const | 2019-03-07 | Shannon Savoy | 2019-03-08 | Mike Tabbert
NJS-05 | NJS-05 | PI00238 | Verified | Main PDC, Install Permenant Tags on duct bank stub-ups, temporary tags have been installed. | C | E | Chris Colvin | McD | 2019-03-01 | Chris Colvin | Const | 2020-06-11 | Chris Colvin | 2020-06-16 | Mike Tabbert
NJS-05 | NJS-05 | PI00239 | Verified | 10-NJS-SWG-0004A Install Arc Flash Labels | B | E | Mike Tabbert | McD | 2019-03-01 | Mike Tabbert | Const | 2019-07-19 | Mike Tabbert | 2019-07-19 | Mike Tabbert
NJS-05 | NJS-05 | PI00253 | Verified | Medium voltage terminations in rear compartment of 10-NJS-XFM-0004A are hot bolted. Torque after commissioning. | B | E | Logan Holland | McD | 2019-03-04 | Logan Holland | Const | 2019-06-21 | Logan Holland | 2019-06-21 | Logan Holland
NJS-05 | NJS-05 | PI00255 | Verified | Replace damaged door inner foam protector on rear compartments. | B | E | Luis Cantu | McD | 2019-03-04 | Luis Cantu | Const | 2019-07-24 | Ken Mundy | 2019-07-26 | Shannon Scott
NJS-05 | NJS-05 | PI00257 | Verified | Transformer heater cables are on temp. power - permanent cables need to be termed after commissioning. | B | E | Logan Holland | McD | 2019-03-04 | Logan Holland | Const | 2019-06-21 | Logan Holland | 2019-06-21 | Logan Holland
NJS-05 | NJS-05 | PI00259 | Verified | Replace dried out washers on panel on north side of transformer 0004A. | C | E | Shannon Savoy | McD | 2019-03-04 | Shannon Savoy | Const | 2019-03-12 | Mike Tabbert | 2019-03-15 | Shannon Scott
NJS-05 | NJS-05 | PI00261 | Verified | Seal conduits in transformer 0004A. | B | E | Logan Holland | McD | 2019-03-04 | Logan Holland | Const | 2019-09-05 | Logan Holland | 2019-09-05 | Logan Holland
NJS-05 | NJS-05 | PI00263 | Verified | Duct seal conduits under main PDC. | C | E | Luis Cantu | McD | 2019-03-04 | Luis Cantu | Const | 2019-07-19 | Ken Mundy | 2019-07-29 | Mike Tabbert
NJS-05 | NJS-05 | PI00266 | Verified | Grout Supports on west side of transformers 10-NJS-XFM-0004A & B at main PDC. | C | C | Johnny Campbell | McD | 2019-03-04 | Johnny Campbell | Const | 2019-07-30 | Johnny Campbell | 2019-08-08 | Shannon Scott
NJS-05 | NJS-05 | PI16160 | Verified | Missing test reports for 86LOR, SEL-751, & CTs | C | E | Jonathan Donham | McD | 2020-01-20 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2021-03-03 | John Watts
NJS-05 | NJS-05 | PI16206 | Verified | 10-NJS-XFM-0004A - Missing ground wires across the flex conduit | D | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm | 2020-01-29 | Randy Carpenter | 2020-02-05 | Shannon Scott
NJS-05 | NJS-05 | PI00206 | Verified | Seal all cable entrance after commissioning - 10-NJS-SWG-004A | C | E | Jonathan Donham | McD | 2019-02-26 | Jonathan Donham | Const | 2020-06-02 | Randy Carpenter | 2021-03-03 | John Watts
NJS-06 | NJS-06 | PI00240 | Verified | 10-NJS-XFM-0004B, Install New Offset Bus Plates for splice between transformer and Bus Duct. | A | E | Shannon Savoy | EAT | 2019-03-01 | Shannon Savoy | Const | 2019-03-06 | Mike Tabbert | 2019-03-06 | Mike Tabbert
NJS-06 | NJS-06 | PI00241 | Verified | 10-NJS-XFM-0004B, Install Braids from transformer to bus duct. | A | E | Shannon Savoy | McD | 2019-03-01 | Shannon Savoy | Const | 2019-03-06 | Mike Tabbert | 2019-03-06 | Mike Tabbert
NJS-06 | NJS-06 | PI00242 | Verified | 10-NJS-XFM-0004A Weld Transformer Down to Weld Plates when all electrical connections have been made. | B | E | Shannon Savoy | McD | 2019-03-01 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-06-03 | Mike Tabbert
NJS-06 | NJS-06 | PI00243 | Verified | Cable Tray Main PDC, Install cable tray grounding. | A | E | Shannon Savoy | McD | 2019-03-01 | Shannon Savoy | Const | 2019-03-07 | Shannon Savoy | 2019-03-08 | Mike Tabbert
NJS-06 | NJS-06 | PI00244 | Verified | Main PDC, Install Permenant Tags on duct bank stub-ups, temporary tags have been installed. | C | E | Chris Colvin | McD | 2019-03-01 | Chris Colvin | Const | 2020-06-11 | Chris Colvin | 2020-06-16 | Mike Tabbert
NJS-06 | NJS-06 | PI00254 | Verified | Medium voltage terminations in rear compartment of 10-NJS-XFM-0004B are hot bolted. Torque after commissioning. | B | E | Logan Holland | McD | 2019-03-04 | Logan Holland | Const | 2019-06-21 | Logan Holland | 2019-06-21 | Logan Holland
NJS-06 | NJS-06 | PI00256 | Verified | Replace damaged door inner foam protector on rear compartments. | B | E | Luis Cantu | McD | 2019-03-04 | Luis Cantu | Const | 2019-07-25 | Ken Mundy | 2019-07-26 | Shannon Scott
NJS-06 | NJS-06 | PI00258 | Verified | Transformer heater cables are on temp. power - permanent cables need to be termed after commissioning. | B | E | Logan Holland | McD | 2019-03-04 | Logan Holland | Const | 2019-06-21 | Logan Holland | 2019-06-21 | Logan Holland
NJS-06 | NJS-06 | PI00260 | Verified | Replace dried out washers on panel on north side of transformer 0004B. | C | E | Shannon Savoy | McD | 2019-03-04 | Shannon Savoy | Const | 2019-03-12 | Mike Tabbert | 2019-03-15 | Shannon Scott
NJS-06 | NJS-06 | PI00262 | Verified | Seal conduits in transformer 0004B. | B | E | Logan Holland | McD | 2019-03-04 | Logan Holland | Const | 2019-09-05 | Logan Holland | 2019-09-05 | Logan Holland
NJS-06 | NJS-06 | PI00264 | Verified | Duct seal conduits under main PDC. | C | E | Luis Cantu | McD | 2019-03-04 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-29 | Mike Tabbert
NJS-06 | NJS-06 | PI00265 | Verified | Replace stripped bolt at heater plate at the 90 of the bus duct. | B | E | Shannon Savoy | McD | 2019-03-04 | Shannon Savoy |  | 2019-03-12 | Mike Tabbert | 2019-03-12 | Mike Tabbert
NJS-06 | NJS-06 | PI00267 | Verified | Red line 10-NOS-EE-WIR-0004 - delete cable 10NJSC0051. | B | E | Mike Tabbert | McD | 2019-03-04 | Mike Tabbert | Const | 2019-03-05 | Mike Tabbert | 2019-06-26 | Logan Holland
NJS-06 | NJS-06 | PI16207 | Verified | 10-NJS-XFM-0004B - Missing ground wires across the flex conduit | D | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm | 2020-01-29 | Randy Carpenter | 2020-02-10 | Shannon Scott
NJS-06 | NJS-06 | PI00207 | Verified | Seal all cable entrance after commissioning - 10-NJS-SWG-004B | C | E | Jonathan Donham | McD | 2019-02-26 | Jonathan Donham | Const | 2020-06-02 | Randy Carpenter | 2021-03-03 | John Watts
NJS-07 | NJS-07 | PI00181 | Verified | Install and torque connections from 0002A and 0002B Bus to SWG-0002 and 0001A and 0001B. | A | E | Shannon Savoy | EAT | 2019-02-18 | Shannon Savoy | Const | 2019-03-06 | Mike Tabbert | 2019-03-06 | Mike Tabbert
NJS-07 | NJS-07 | PI00182 | Verified | General clean-up in all SWG compartments. | A | E | Shannon Savoy | McD | 2019-02-18 | Shannon Savoy | Const | 2019-03-06 | Mike Tabbert | 2019-03-06 | Mike Tabbert
NJS-07 | NJS-07 | PI00188 | Verified | Seal all penetrations. | C | E | Chris Colvin | McD | 2019-02-18 | Chris Colvin | Const | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
NJS-07 | NJS-07 | PI00194 | Verified | Heater JB for 2A switchgear bus duct missing 2 basket nuts. | B | E | Shannon Savoy | McD | 2019-02-18 | Shannon Savoy | Const | 2019-04-03 | Shannon Savoy | 2019-04-03 | Mike Tabbert
NJS-07 | NJS-07 | PI00195 | Verified | Need cable tray clamp for conduit under northwest corner of main PDC. | B | E | Shannon Savoy | McD | 2019-02-18 | Shannon Savoy | Const | 2019-02-18 | Dan Dula | 2019-02-19 | Curtis Platzek
NJS-07 | NJS-07 | PI00196 | Verified | 2B bus duct angle support missing 1 bolt - under main PDC northwest corner. | A | E | Shannon Savoy | McD | 2019-02-18 | Shannon Savoy | Const | 2019-02-19 | Dan Dula | 2019-02-26 | Curtis Platzek
NJS-07 | NJS-07 | PI00197 | Verified | Space heaters in bottom of switchgear 2A - inspect terminations for being too close to ground. | B | E | Logan Holland | EAT | 2019-02-18 | Logan Holland | Const | 2019-03-25 | Michael Law | 2019-03-25 | Michael Law
NJS-07 | NJS-07 | PI17667 | Verified | 10-NJS-SWG-0002B_TRBL been coming in since December 2019. Description: '480V SWG 1B Mn Bkr Protective Relay OK' | B | E | Mayur Patel | McD | 2020-03-04 | Mayur Patel | Comm | 2020-03-19 | Mayur Patel | 2020-04-30 | John Watts
NJS-08 | NJS-08 | PI00680 | Verified | 1A-NJS-MCC-0005 in HRSG PDC needs arc flash labels. | B | E | Mike Tabbert | McD | 2019-04-26 | Mike Tabbert | Const | 2019-06-21 | Mike Tabbert | 2019-06-21 | Mike Tabbert
NJS-08 | NJS-08 | PI00682 | Verified | Cover holes in PDC floor (temporary for safety). | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-02 | Shannon Scott
NJS-08 | NJS-08 | PI00684 | Verified | General clean up needed in HRSG PDC. | B | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-02 | Shannon Scott
NJS-08 | NJS-08 | PI00686 | Verified | Grout cable tray supports under HRSG PDC. | C | C | Johnny Campbell | McD | 2019-04-26 | Johnny Campbell | Const | 2019-07-31 | Jack Fields | 2019-08-21 | Fred Michael
NJS-08 | NJS-08 | PI00692 | Verified | Loose nut in 1A-NJS-MCC-0005 (2M) on cable 1ANJSL0001B3 in the 1A HRSG PDC. Check all connections for tightness/torque. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00693 | Verified | Paint peeling on widing in 1A HRSG transformer. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00694 | Verified | Missing bolt on meralack strap in the 1A HRSG transformer. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00695 | Verified | Re-route heater cable in the 1A HRSG transformer. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00696 | Verified | Tighten bolts on the 1A HRSG transformer exterior enclosure panels. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00706 | Verified | 1ANJSC0002, Pull and Terminate | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00707 | Verified | 1A-NJS-XFM-0005, Clean Transformer top to bottom. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00708 | Verified | 1ANJSK0001, Complete termination of heater cable, replace terminal block, after commissioning. Provide torque sheet to turnover. | B | E | Luis Cantu | McD | 2019-04-26 | Luis Cantu | Const | 2019-06-07 | Shannon Savoy | 2019-07-24 | Mike Tabbert
NJS-08 | NJS-08 | PI00709 | Verified | 1A-NJS-XFM-0005, Fabricate plate to cover opening in transformer scondary side. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00710 | Verified | 1A-NJS-XFM-0005, Remove all shipping material from transformer. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const |  |  | 2019-04-26 | Ed Gober
NJS-08 | NJS-08 | PI00711 | Verified | 1ATL121701, Ground Cable Tray. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00713 | Verified | 1A-NJS-XFM-0005, Ground ground bushings on conduit to tray, install condulet covers. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00714 | Verified | 1A-NJS-XFM-0005, Install external ground on sealtight at transformer. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-06 | Mike Tabbert
NJS-08 | NJS-08 | PI00715 | Verified | 1A-NJS-XFM-0005, Ground grounding bushings inside transformer at secondary penetrations. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00716 | Verified | 1A-NJS-XFM-0005, Replace split bolts with c-taps at primary conduit ground bushings. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00717 | Verified | 1A-NJS-XFM-0005, Remove braid ground from grounding clamp, replace with tie raps. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00718 | Verified | 1A-NJS-MCC-0005, Incoming section missing frame and internal cover. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00719 | Verified | 1A-NJS-MCC-0005, All Completion forms to be complete, cubicle to be cleaned, all torque sheets and meg sheets completed. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-06 | Ed Gober
NJS-08 | NJS-08 | PI00720 | Verified | 1A-NJS-XFM-0005, All completion forms to be completed, all torque sheets and meg sheets completed. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Ed Gober
NJS-08 | NJS-08 | PI00721 | Verified | 10-NOS-SWG-0001A, Section 3D, install insulating boots at 6.9KV terminations, Cubicle to be cleaned. | B | E | Dustin Futrell | McD | 2019-04-26 | Dustin Futrell | Const | 2019-06-07 | Shannon Savoy | 2019-08-07 | Mike Tabbert
NJS-08 | NJS-08 | PI00722 | Verified | 10-NOS-SWG-0001A, All completion forms to be completed, all torque sheets and meg sheets completed. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-08 | NJS-08 | PI00723 | Verified | 10-NOS-SWG-0001A, 1A-NJS-XFM-0005, Cables hot bolted at this time. | B | E | Chris Boudreaux | McD | 2019-04-26 | Chris Boudreaux | Const | 2019-12-07 | Michael Law | 2019-12-18 | Mike Tabbert
NJS-08 | NJS-08 | PI08447 | Verified | HVAC1 not working | B | E | Jonathan Donham | EAT | 2019-10-02 | Jonathan Donham | Comm | 2020-03-02 | Jonathan Donham | 2020-03-04 | Jonathan Donham
NJS-08 | NJS-08 | PI18031 | Verified | HRSG 1A PDC - There are leaks in HRSG 1A's PDC. | C | P | Mike Tabbert | McD | 2020-03-17 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2021-05-27 | John Watts
NJS-09 | NJS-09 | PI00681 | Verified | 1B-NJS-MCC-0005 in HRSG PDC needs arc flash labels. | B | E | Mike Tabbert | McD | 2019-04-26 | Mike Tabbert | Const | 2019-06-21 | Mike Tabbert | 2019-06-21 | Mike Tabbert
NJS-09 | NJS-09 | PI00683 | Verified | Cover holes in PDC floor (temporary for safety). | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-02 | Shannon Scott
NJS-09 | NJS-09 | PI00685 | Verified | General clean up needed in HRSG PDC. | B | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-02 | Shannon Scott
NJS-09 | NJS-09 | PI00687 | Verified | Grout cable tray supports under HRSG PDC. | C | C | Johnny Campbell | McD | 2019-04-26 | Johnny Campbell | Const | 2019-07-31 | Jack Fields | 2019-08-21 | Fred Michael
NJS-09 | NJS-09 | PI00688 | Verified | Complete insulated ground on north side of HRSG PDC. | B | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-02 | Shannon Savoy | 2019-05-06 | Mike Tabbert
NJS-09 | NJS-09 | PI00689 | Verified | Secondary feeders in transformer not torqued (loose). | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-02 | Shannon Scott
NJS-09 | NJS-09 | PI00690 | Verified | Replace door screen in south side of thransformer. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00691 | Verified | Re-route XO bushing term. in transformer. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-02 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00724 | Verified | 1BNJSC0002, Pull and Terminate | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00725 | Verified | 1B-NJS-XFM-0005, Clean Transformer top to bottom. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00726 | Verified | 1BNJSK0001, Complete termination of heater cable, install terminal block, after commissioning. Provide torque sheet to turnover. | B | E | Luis Cantu | McD | 2019-04-26 | Luis Cantu | Const | 2019-06-07 | Shannon Savoy | 2019-07-24 | Mike Tabbert
NJS-09 | NJS-09 | PI00727 | Verified | 1B-NJS-XFM-0005, Fabricate plate to cover opening in transformer scondary side. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00728 | Verified | 1B-NJS-XFM-0005, Remove all shipping material from transformer. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00729 | Verified | 1BTL121701, Ground Cable Tray. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00731 | Verified | 1B-NJS-XFM-0005, Install external ground on sealtight at transformer. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-06 | Mike Tabbert
NJS-09 | NJS-09 | PI00732 | Verified | 1B-NJS-XFM-0005, Ground grounding bushings inside transformer at secondary penetrations. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00733 | Verified | 1B-NJS-XFM-0005, Replace split bolts with c-taps at primary conduit ground bushings. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00734 | Verified | 1B-NJS-XFM-0005, Remove braid ground from grounding clamp, replace with tie raps. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00735 | Verified | 1B-NJS-MCC-0005, Incoming section missing frame and internal cover. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00736 | Verified | 1B-NJS-MCC-0005, Complete grounding of grounding bushings at incoming section. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00737 | Verified | 1B-NJS-MCC-0005, All Completion forms to be complete, cubicle to be cleaned, all torque sheets and meg sheets completed. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00738 | Verified | 1B-NJS-XFM-0005, All completion forms to be completed, all torque sheets and meg sheets completed. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Ed Gober
NJS-09 | NJS-09 | PI00739 | Verified | 10-NOS-SWG-0002B, Section 11A, Install bolted raceway in lower cubicle, install insulating boots at 6.9KV terminations, Cubicle to be cleaned. | B | E | Dustin Futrell | McD | 2019-04-26 | Dustin Futrell | Const | 2019-06-07 | Shannon Savoy | 2019-08-07 | Mike Tabbert
NJS-09 | NJS-09 | PI00740 | Verified | 10-NOS-SWG-0002B, All completion forms to be completed, all torque sheets and meg sheets completed. | A | E | Shannon Savoy | McD | 2019-04-26 | Shannon Savoy | Const | 2019-05-01 | Shannon Savoy | 2019-05-03 | Mike Tabbert
NJS-09 | NJS-09 | PI00741 | Verified | 10-NOS-SWG-0002B, 1B-NJS-XFM-0005, Cables hot bolted at this time. | B | E | Chris Boudreaux | McD | 2019-04-26 | Chris Boudreaux | Const | 2019-12-07 | Michael Law | 2019-12-18 | Mike Tabbert
NJS-09 | NJS-09 | PI08448 | Verified | Redline dwg 1B-NJS-EE-SLD-0001-S01, at top left side of drawing, to reflect correct "drawing from" reference to 10-NOS-EE-SLD-0002-S02 | C | E | Mike Tabbert | McD | 2019-10-02 | Mike Tabbert | Comm | 2020-01-20 | Mike Tabbert | 2020-01-20 | Michael Law
NJS-09 | NJS-09 | PI17671 | Verified | 1B-NJS-XFM-0005 - The temperature monitor panel is not functional for operations to be able to take readings. | B | E | Jonathan Donham | McD | 2020-03-04 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2020-06-09 | Love Kayode
NJS-10 | NJS-10 | PI01261 | Verified | Terminate grounds in the incoming section of 1ABFJ01 GT MCC in the 1A GT Control Package. | A | E | Shannon Savoy | McD | 2019-05-30 | Shannon Savoy | Const | 2019-05-31 | Shannon Savoy | 2019-06-03 | Mike Tabbert
NJS-10 | NJS-10 | PI01262 | Verified | Torque cables 1ACTSL0008A1 through 5, B1-5 & C1-5 in the incoming section of 1ABFJ01 GT MCC in the 1A GT Control Package and at the Main PDC. | A | E | Shannon Savoy | McD | 2019-05-30 | Shannon Savoy | Const | 2019-05-31 | Shannon Savoy | 2019-06-03 | Mike Tabbert
NJS-10 | NJS-10 | PI01264 | Verified | Firestop penetrations in the incoming section of 1ABFJ01 in the 1A GT Control Module and in 10-NJS-SWG-0001A at the Main PDC. | A | E | Shannon Savoy | McD | 2019-05-30 | Shannon Savoy | Const | 2019-05-31 | Shannon Savoy | 2019-06-04 | Mike Tabbert
NJS-10 | NJS-10 | PI01266 | Verified | Clean out cubicles in the Main PDC. | A | E | Shannon Savoy | McD | 2019-05-30 | Shannon Savoy | Const | 2019-05-31 | Shannon Savoy | 2019-06-04 | Mike Tabbert
NJS-10 | NJS-10 | PI01268 | Verified | Trim ty-wraps in cable trays. | B | E | Dustin Futrell | McD | 2019-05-30 | Dustin Futrell | Const | 2019-05-31 | Shannon Savoy | 2019-08-07 | Mike Tabbert
NJS-10 | NJS-10 | PI01270 | Verified | Terminate cables 1ACTSL0002A, B & C at the transformer end after permanent power. | B | E | Chris Boudreaux | McD | 2019-05-30 | Chris Boudreaux | Comm | 2019-12-23 | Michael Law | 2020-01-08 | Mike Tabbert
NJS-10 | NJS-10 | PI01289 | Verified | Cable Tray Tee's feeding HRSG 1A need supports all levels. | B | E | Luis Cantu | McD | 2019-05-30 | Luis Cantu | Const | 2019-07-18 | Ken Mundy | 2019-07-23 | Mike Tabbert
NJS-10 | NJS-10 | PI01296 | Verified | Cable Tray Rack GT 1A, at control building waterfall, missing supports. | B | E | Dustin Futrell | McD | 2019-05-30 | Dustin Futrell | Const | 2019-07-18 | Ken Mundy | 2019-08-16 | Eric Policarpio
NJS-10 | NJS-10 | PI01297 | Verified | All system completion forms to be completed and turned in | B | E | Dustin Futrell | McD | 2019-05-30 | Dustin Futrell | Const | 2019-09-06 | Mike Tabbert | 2019-09-06 | Mike Tabbert
NJS-10 | NJS-10 | PI13797 | Verified | 1ABFJ01 GT 480V AC MCC panel is missing screws | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-10 | NJS-10 | PI13798 | Verified | Clean off top of all MCC's | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-10 | NJS-10 | PI13799 | Verified | Remove all tape and old tags from MCC panels | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-10 | NJS-10 | PI13800 | Verified | All bottom doors are missing screws | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-10 | NJS-10 | PI13801 | Verified | Heat shrink all cable tags | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-10 | Shannon Scott
NJS-10 | NJS-10 | PI13802 | Verified | 1AQEF13AN101-MO1; GT Casing Cooling Air Fan Motor MCC has two cables missing tag | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-10 | NJS-10 | PI13803 | Verified | Remove all plastic bags hanging inside MCC's | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-10 | NJS-10 | PI13804 | Verified | Trim excess from all tie-wraps inside MCC's | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-10 | NJS-10 | PI13805 | Verified | Tag all wire missing tag | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-10 | NJS-10 | PI13806 | Verified | Seal all penetrations | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-10 | NJS-10 | PI13807 | Verified | Need general cleanup inside A PDC enclosure | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-10 | NJS-10 | PI13808 | Verified | Place vendor manuals in holder at N end of MCC panels | D | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
NJS-10 | NJS-10 | PI13809 | Verified | Label all spare cables under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-10 | NJS-10 | PI13810 | Verified | Label both ends of spare cables as "spare" under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-10 | NJS-10 | PI13812 | Verified | Feeder cable hubs under PDC need to be grounded | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-10 | NJS-10 | PI13813 | Verified | Tape end of all spare cables under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-10 | NJS-10 | PI13814 | Verified | Penetration flashing under A PDC is missing screw | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-10 | NJS-10 | PI01285 | Verified | Cable Tray Rack on north end of Main PDC, some missing splice plate bolts, missing hold down clamps, missing cable tray labels. | B | E | Chris Colvin | McD | 2019-05-30 | Chris Colvin | Const | 2019-12-11 | Scottie Landeneau | 2019-12-16 | Mike Tabbert
NJS-10 | NJS-10 | PI01294 | Verified | Cable Tray Rack to GT 1A control building, missing hold down clamps at offset. | B | E | Dustin Futrell | McD | 2019-05-30 | Dustin Futrell | Const | 2019-07-31 | Ken Mundy | 2019-10-05 | Mike Tabbert
NJS-11 | NJS-11 | PI00936 | Verified | Cable Tray Rack on north end of Main PDC, some missing splice plate bolts, missing hold down clamps, missing cable tray labels and grounding incomplete. | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2019-12-11 | Scottie Landeneau | 2019-12-16 | Mike Tabbert
NJS-11 | NJS-11 | PI00940 | Verified | Cable Tray Tee's feeding HRSG 1A need supports all levels. | B | E | Luis Cantu | McD | 2019-05-03 | Luis Cantu | Const | 2019-07-18 | Ken Mundy | 2019-07-23 | Mike Tabbert
NJS-11 | NJS-11 | PI00941 | Verified | Cable Tray offset to the north just east of GT 1A needs supports on levels, also grounding not complete, hold down clamps missing and cable tray labels need to be installed. | B | E | Dustin Futrell | McD | 2019-05-03 | Dustin Futrell | Const | 2019-07-31 | Ken Mundy | 2019-08-21 | Fred Michael
NJS-11 | NJS-11 | PI00947 | Verified | Complete and turn in all system completion forms. | A | E | Shannon Savoy | McD | 2019-05-03 | Shannon Savoy | Const | 2019-05-14 | Shannon Savoy | 2019-05-21 | Mike Tabbert
NJS-11 | NJS-11 | PI00948 | Verified | Complete all firestop installation at feeder cable entrance. | A | E | Shannon Savoy | McD | 2019-05-03 | Shannon Savoy | Const | 2019-05-15 | Dan Dula | 2019-05-16 | Mike Tabbert
NJS-11 | NJS-11 | PI00961 | Verified | Torque all 1BCTSL0008 cables in 1BBFJ01 GT in the 1B GT PDC. | A | E | Shannon Savoy | McD | 2019-05-03 | Shannon Savoy | Const | 2019-05-15 | Dan Dula | 2019-05-17 | Phil Carter
NJS-11 | NJS-11 | PI00962 | Verified | Seal conduits with fire caulk in 1BBFJ01 GT in the 1B GT PDC. | A | E | Shannon Savoy | McD | 2019-05-03 | Shannon Savoy | Const | 2019-05-15 | Dan Dula | 2019-05-17 | Phil Carter
NJS-11 | NJS-11 | PI00963 | Verified | Torque the cables in the rear compartment of 1B-CTS-BFJ01 in the main PDC. | A | E | Shannon Savoy | McD | 2019-05-03 | Shannon Savoy | Const | 2019-05-15 | Dan Dula | 2019-05-17 | Phil Carter
NJS-11 | NJS-11 | PI00964 | Verified | Seal conduits in the rear compartment of 1B-CTS-BFJ01 in the main PDC. | A | E | Shannon Savoy | McD | 2019-05-03 | Shannon Savoy | Const | 2019-05-15 | Dan Dula | 2019-05-17 | Phil Carter
NJS-11 | NJS-11 | PI01030 | Verified | 1BCTSL0002A, Terminate Cable to end. | B | E | Luis Cantu | McD | 2019-05-09 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
NJS-11 | NJS-11 | PI01031 | Verified | 1BCTSL0002B, Terminate Cable to end. | B | E | Luis Cantu | McD | 2019-05-09 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
NJS-11 | NJS-11 | PI01032 | Verified | 1BCTSL0002C, Terminate Cable to end. | B | E | Luis Cantu | McD | 2019-05-09 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
NJS-11 | NJS-11 | PI01033 | Verified | 1BCTSL0002G, Terminate Cable to end. | B | E | Luis Cantu | McD | 2019-05-09 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
NJS-11 | NJS-11 | PI13815 | Verified | Straighten all panel lifting lugs at top of MCC panels | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-11 | NJS-11 | PI13816 | Verified | 1ABMXO1 AP 102-M01; GT Control Oil Pump MCC needs tag | C | E | Mike Tabbert | McD | 2019-12-01 | Mike Tabbert | Comm | 2020-04-30 | Mike Tabbert | 2021-05-24 | Keith Pollock
NJS-11 | NJS-11 | PI13817 | Verified | Clean off top of all MCC's | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-11 | NJS-11 | PI13818 | Verified | Remove all tape and old tags from MCC panels | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-11 | NJS-11 | PI13819 | Verified | All bottom doors are missing screws | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-11 | NJS-11 | PI13820 | Verified | Heat shrink all cable tags | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-11 | NJS-11 | PI13821 | Verified | Remove all plastic bags hanging inside MCC's | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-11 | NJS-11 | PI13822 | Verified | Trim excess from all tie-wraps inside MCC's | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-10 | Fred Michael
NJS-11 | NJS-11 | PI13823 | Verified | Tag all wire missing tag | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-11 | NJS-11 | PI13824 | Verified | Seal all penetrations | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-11 | NJS-11 | PI13825 | Verified | Need general cleanup inside A PDC enclosure | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-11 | NJS-11 | PI13826 | Verified | Label all spare cables under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-11 | NJS-11 | PI13827 | Verified | Label both ends of spare cables as "spare" under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-04-07 | Bernard Stasse
NJS-11 | NJS-11 | PI13829 | Verified | Feeder cable hubs under PDC need to be grounded | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-11 | NJS-11 | PI13830 | Verified | Tape end of all spare cables under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-11 | NJS-11 | PI13831 | Verified | Spare MCC missing reset button | C | E | Mike Tabbert | McD | 2019-12-01 | Mike Tabbert | Comm | 2020-05-04 | Matt Gilmore | 2021-01-05 | Keith Pollock
NJS-11 | NJS-11 | PI13832 | Verified | Need tag at 1ABTMO2, DC Battery Charger B | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-07 | Bernard Stasse
NJS-12 | NJS-12 | PI01003 | Verified | Provide arc flash labels for 10-NJS-MCC-0006A & B. | B | E | Mike Tabbert | McD | 2019-05-06 | Mike Tabbert | Const | 2019-06-14 | Mike Tabbert | 2019-06-14 | Mike Tabbert
NJS-12 | NJS-12 | PI12697 | Verified | Need final cleaning inside 10NJS-MCC-0006A & 0006B. | C | E | Jonathan Donham | McD | 2019-11-01 | Jonathan Donham | Comm |  |  | 2020-02-10 | Fred Michael
NJS-13 | NJS-13 | PI01004 | Verified | Provide arc flash labels for 10-NJS-MCC-0003A & B. | B | E | Mike Tabbert | McD | 2019-05-06 | Mike Tabbert | Const | 2019-06-14 | Mike Tabbert | 2019-06-14 | Mike Tabbert
NJS-13 | NJS-13 | PI12699 | Verified | Need final cleaning inside 10NJS-MCC-0003A & 0003B. | C | E | Jonathan Donham | McD | 2019-11-01 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-03-31 | Randy Carpenter
NJS-14 | NJS-14 | PI00208 | Verified | 10-NJS-SWG-0004A, Arc Flash Labels. | B | E | Mike Tabbert | McD | 2019-02-26 | Mike Tabbert | Const | 2019-07-19 | Mike Tabbert | 2019-07-19 | Mike Tabbert
NJS-14 | NJS-14 | PI00209 | Verified | 10-NJS-SWG-0004B, Arc Flash Labels. | B | E | Mike Tabbert | McD | 2019-02-26 | Mike Tabbert | Const | 2019-07-19 | Mike Tabbert | 2019-07-19 | Mike Tabbert
NJS-14 | NJS-14 | PI00205 | Verified | Cable 10NJSSWG0004A-2C-L1 missing label. Rear compartment of swg. 4A/B | A | E | Shannon Savoy | McD | 2019-02-26 | Shannon Savoy | Const | 2019-02-27 | Mike Tabbert | 2019-02-27 | Shannon Scott
NJS-15 | NJS-15 | PI01263 | Verified | Torque cables 1ACTSL0009A1 through 5, B1-5 & C1-5 in the incoming section of 1ABMC01 GT MCC in the 1A GT Control Package and at the Main PDC. | A | E | Shannon Savoy | McD | 2019-05-30 | Shannon Savoy | Const | 2019-05-31 | Shannon Savoy | 2019-06-03 | Mike Tabbert
NJS-15 | NJS-15 | PI01265 | Verified | Firestop penetrations in the incoming section of 1ABMC01 in the 1A GT Control Module and in 10-NJS-SWG-0002 at the Main PDC. | A | E | Shannon Savoy | McD | 2019-05-30 | Shannon Savoy | Const | 2019-05-31 | Shannon Savoy | 2019-06-04 | Mike Tabbert
NJS-15 | NJS-15 | PI01267 | Verified | Clean out cubicles in the Main PDC. | A | E | Shannon Savoy | McD | 2019-05-30 | Shannon Savoy | Const | 2019-05-31 | Shannon Savoy | 2019-06-04 | Mike Tabbert
NJS-15 | NJS-15 | PI01269 | Verified | Trim ty-wraps in cable trays. | B | E | Luis Cantu | McD | 2019-05-30 | Luis Cantu | Const | 2019-08-01 | Mike Tabbert | 2019-08-01 | Mike Tabbert
NJS-15 | NJS-15 | PI01271 | Verified | Terminate cables 1ACTSL0006A, B & C at the transformer end after permanent power. | B | E | Dustin Futrell | McD | 2019-05-30 | Dustin Futrell | Const | 2019-09-13 | Richard Cruz | 2019-10-05 | Mike Tabbert
NJS-15 | NJS-15 | PI01276 | Verified | Cable Tray Tee's feeding HRSG 1A need supports all levels. | B | E | Luis Cantu | McD | 2019-05-30 | Luis Cantu | Const | 2019-07-18 | Ken Mundy | 2019-07-23 | Mike Tabbert
NJS-15 | NJS-15 | PI01281 | Verified | Cable Tray Rack to GT 1A control building, missing hold down clamps at offset. | B | E | Dustin Futrell | McD | 2019-05-30 | Dustin Futrell | Const | 2019-07-31 | Ken Mundy | 2019-10-05 | Mike Tabbert
NJS-15 | NJS-15 | PI01282 | Verified | Cable Tray Rack GT 1A, from offset to control building, cable tray labels need to be installed. | B | E | Luis Cantu | McD | 2019-05-30 | Luis Cantu | Const | 2019-07-18 | Ken Mundy | 2019-07-23 | Mike Tabbert
NJS-15 | NJS-15 | PI01284 | Verified | All system completion forms to be completed and turned in | B | E | Dustin Futrell | McD | 2019-05-30 | Dustin Futrell | Const | 2019-08-16 | Eric Policarpio | 2019-08-16 | Eric Policarpio
NJS-15 | NJS-15 | PI13778 | Verified | Straighten all panel lifting lugs at top of MCC panels | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-15 | NJS-15 | PI13779 | Verified | Clean off top of all MCC's | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-15 | NJS-15 | PI13780 | Verified | Remove all tape and old tags from MCC panels | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-15 | NJS-15 | PI13781 | Verified | All bottom doors are missing screws | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-15 | NJS-15 | PI13782 | Verified | Heat shrink all cable tags | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-15 | NJS-15 | PI13783 | Verified | Remove all plastic bags hanging inside MCC's | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-15 | NJS-15 | PI13784 | Verified | Trim excess from all tie-wraps inside MCC's | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-15 | NJS-15 | PI13785 | Verified | Tag all wire missing tags | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-15 | NJS-15 | PI13786 | Verified | Seal all penetrations inside panels | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-15 | NJS-15 | PI13787 | Verified | Need general cleanup inside B PDC enclosure | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-15 | NJS-15 | PI13788 | Verified | Label all spare cables under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-07 | Bernard Stasse
NJS-15 | NJS-15 | PI13789 | Verified | Label both ends of spare cables as "spare" under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-15 | NJS-15 | PI13791 | Verified | Ground all Feeder cable hubs under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-15 | NJS-15 | PI13792 | Verified | Tape end of all spare cables under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-15 | NJS-15 | PI13794 | Verified | Remove orange rubber mat from calbe tray under B PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-25 | Jared Stimpson | 2020-01-28 | Fred Michael
NJS-15 | NJS-15 | PI13795 | Verified | Plug unused hole under under B PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-15 | NJS-15 | PI13796 | Verified | Seal all cable penetrations under B PDC | B | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-16 | NJS-16 | PI00953 | Verified | Cable Tray Tee's feeding HRSG 1A need supports all levels. | B | E | Luis Cantu | McD | 2019-05-03 | Luis Cantu | Const | 2019-07-18 | Ken Mundy | 2019-07-23 | Mike Tabbert
NJS-16 | NJS-16 | PI00959 | Verified | Complete and turn in all system completion forms. | A | E | Shannon Savoy | McD | 2019-05-03 | Shannon Savoy | Const | 2019-05-14 | Shannon Savoy | 2019-05-21 | Mike Tabbert
NJS-16 | NJS-16 | PI00960 | Verified | Complete all firestop installation at feeder cable entrance. | B | E | Luis Cantu | McD | 2019-05-03 | Luis Cantu | Const | 2019-06-07 | Shannon Savoy | 2019-06-14 | Mike Tabbert
NJS-16 | NJS-16 | PI00965 | Verified | Seal conduits with fire caulk in 1BBMC01 GT in the 1B GT PDC. | A | E | Shannon Savoy | McD | 2019-05-03 | Shannon Savoy | Const | 2019-05-15 | Dan Dula | 2019-05-17 | Phil Carter
NJS-16 | NJS-16 | PI00966 | Verified | Seal conduits in the rear compartment of SWG-0002 at the main PDC when complete with unit A (NJS-15) | B | E | Chris Colvin | McD | 2019-05-03 | Chris Colvin | Const | 2019-06-14 | Mike Tabbert | 2020-01-15 | Michael Law
NJS-16 | NJS-16 | PI01026 | Verified | 1BCTSL0006A, Terminate to end. | B | E | Dustin Futrell | McD | 2019-05-09 | Dustin Futrell | Const | 2019-07-17 | Michael Law | 2019-08-21 | Fred Michael
NJS-16 | NJS-16 | PI01027 | Verified | 1BCTSL0006B, Terminate to end. | B | E | Dustin Futrell | McD | 2019-05-09 | Dustin Futrell | Const | 2019-07-17 | Michael Law | 2019-08-21 | Fred Michael
NJS-16 | NJS-16 | PI01028 | Verified | 1BCTSL0006C, Terminate to end. | B | E | Dustin Futrell | McD | 2019-05-09 | Dustin Futrell | Const | 2019-07-17 | Michael Law | 2019-08-21 | Fred Michael
NJS-16 | NJS-16 | PI01029 | Verified | 1BCTSL0006G, Terminate to end. | B | E | Dustin Futrell | McD | 2019-05-09 | Dustin Futrell | Const | 2019-07-17 | Michael Law | 2019-08-21 | Fred Michael
NJS-16 | NJS-16 | PI13761 | Verified | Straighten all panel lifting lugs at top of MCC panels | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-16 | NJS-16 | PI13762 | Verified | Clean off top of all MCC's | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-16 | NJS-16 | PI13763 | Verified | Remove all tape and old tags from MCC panels | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-16 | NJS-16 | PI13764 | Verified | All bottom doors are missing screws | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-16 | NJS-16 | PI13765 | Verified | Heat shrink all cable tags | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-16 | NJS-16 | PI13766 | Verified | Remove all plastic bags hanging inside MCC's | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-07 | Shannon Scott
NJS-16 | NJS-16 | PI13767 | Verified | Trim excess from all tie-wraps inside MCC's | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-16 | NJS-16 | PI13768 | Verified | Tag all wire missing tag | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-16 | NJS-16 | PI13769 | Verified | Seal all penetrations inside panels | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-16 | NJS-16 | PI13770 | Verified | Need general cleanup inside B PDC enclosure | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-16 | NJS-16 | PI13771 | Verified | Label all spare cables under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-16 | NJS-16 | PI13772 | Verified | Label both ends of spare cables as "spare" under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-16 | NJS-16 | PI13774 | Verified | Ground all Feeder cable hubs under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-16 | NJS-16 | PI13775 | Verified | Tape end of all spare cables under PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-05 | Shannon Scott
NJS-16 | NJS-16 | PI13777 | Verified | Remove orange rubber mat from calbe tray under B PDC | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-01-25 | Jared Stimpson | 2020-01-28 | Fred Michael
NJS-17 | NJS-17 | PI00091 | Verified | Nameplate for 1C-GMS-ACU-9040B Change "Cubical" to "Cubicle" in section 8 | C | E | Mike Tabbert | EAT | 2019-01-22 | Mike Tabbert | Const | 2019-12-24 | Michael Law | 2020-01-08 | Mike Tabbert
NJS-17 | NJS-17 | PI00138 | Verified | Re-route grounds in 10-NJS-MCC-0002. | A | E | Phil Work | McD | 2019-01-28 | Phil Work | Const | 2019-06-21 | Logan Holland | 2019-06-21 | Logan Holland
NJS-17 | NJS-17 | PI00139 | Verified | Need arc flash label on 10-NJS-MCC-0002. | B | E | Michael Law | McD | 2019-01-28 | Michael Law | Const | 2019-06-14 | Mike Tabbert | 2019-06-14 | Mike Tabbert
NJS-17 | NJS-17 | PI00140 | Verified | Verify that proper termination bolts were used in 10-NJS-MCC-0002; cables 10NJSSST0002-4A-L1, L2 and L3. | A | E | Mike Tabbert | McD | 2019-01-28 | Mike Tabbert | Const | 2019-02-14 | Mike Tabbert | 2019-02-14 | Shannon Scott
NJS-18 | NJS-18 | PI02176 | Verified | 1CSTOC0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-17 | Michael Law | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02177 | Verified | Install DCS cabinets 0204 | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02178 | Verified | Install and ground 10-NJS-MCC-0007A & B | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02179 | Verified | 10NJSC0034, Pull And Terminate Cable | B | E | Dustin Futrell | McD | 2019-07-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
NJS-18 | NJS-18 | PI02180 | Verified | 10NJSC0037, Pull And Terminate Cable | B | E | Dustin Futrell | McD | 2019-07-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
NJS-18 | NJS-18 | PI02181 | Verified | 10NJSC0068, Pull And Terminate Cable | B | E | Dustin Futrell | McD | 2019-07-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
NJS-18 | NJS-18 | PI02182 | Verified | 10NJSC0069, Pull And Terminate Cable | B | E | Dustin Futrell | McD | 2019-07-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
NJS-18 | NJS-18 | PI02183 | Verified | 10NJSC0070, Pull And Terminate Cable | B | E | Dustin Futrell | McD | 2019-07-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
NJS-18 | NJS-18 | PI02184 | Verified | 10NJSC0071, Pull And Terminate Cable | B | E | Dustin Futrell | McD | 2019-07-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
NJS-18 | NJS-18 | PI02185 | Verified | 10NJSC0085, Pull And Terminate Cable | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-17 | Michael Law | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02186 | Verified | 10NJSC0086, Pull And Terminate Cable | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-17 | Michael Law | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02187 | Verified | 10NJSH0007A, Pull And Terminate Cable | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-22 | Luis Cantu | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02188 | Verified | 10NJSH0007B, Pull And Terminate Cable | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-22 | Luis Cantu | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02189 | Verified | 10NJSH0007C, Pull And Terminate Cable | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-22 | Luis Cantu | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02190 | Verified | 10NJSH0007G, Pull And Terminate Cable | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-22 | Luis Cantu | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02191 | Verified | 10NJSK0007, Pull And Terminate Cable | B | E | Dustin Futrell | McD | 2019-07-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
NJS-18 | NJS-18 | PI02192 | Verified | 10NJSK0008, Pull And Terminate Cable | B | E | Dustin Futrell | McD | 2019-07-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
NJS-18 | NJS-18 | PI02193 | Verified | 10NJSK0026, Pull And Terminate Cable | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-08-01 | Luis Cantu | 2019-08-01 | Mike Tabbert
NJS-18 | NJS-18 | PI02194 | Verified | 10NJSL0006G1, Pull And Terminate Cable | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-17 | Michael Law | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02195 | Verified | 10NJSL0006G2, Pull And Terminate Cable | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-17 | Michael Law | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02196 | Verified | 10NJSL0007G1, Pull And Terminate Cable | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
NJS-18 | NJS-18 | PI02197 | Verified | 10NJSL0007G2, Pull And Terminate Cable | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
NJS-18 | NJS-18 | PI02198 | Verified | 10-NJS-XFM-0007A and 0007B Remove Foam packing material from outside of transformers. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02199 | Verified | Install nipples and ground bushings on MCC house keeping pad conduit stub-ups. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-23 | Mike Tabbert
NJS-18 | NJS-18 | PI02200 | Verified | 10-NJS-MCC-0007A and 0007B MCC sections, secure and ground. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02201 | Verified | 10-NJS-XFM-0007A and 0007B Install nipples and ground bushings in all conduit stub-ups in transformers. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02202 | Verified | Seal all spare conduits. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-19 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02203 | Verified | 10-NJS-XFM-0007A and 0007B Missing bolts on transformer lids. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02204 | Verified | 10-NJS-XFM-0007A and 0007B Tighten all bolts on transformer lids. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02205 | Verified | 10-NJS-XFM-0007A and 0007B Ground transformers. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02206 | Verified | 10-DCS-CAB-0204, Install DCS cabinet at Raw Water. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02207 | Verified | Complete all conduit, cable tray to facilitate pulling cable. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-23 | Mike Tabbert | 2019-07-23 | Mike Tabbert
NJS-18 | NJS-18 | PI02208 | Verified | Complete all sealtight and sealtight grounding. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-23 | Mike Tabbert | 2019-07-23 | Mike Tabbert
NJS-18 | NJS-18 | PI02209 | Verified | Completeall grounding to equipment and raceway. | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-23 | Mike Tabbert | 2019-07-23 | Mike Tabbert
NJS-18 | NJS-18 | PI02210 | Verified | Complete all completion paperwork. | A | E | Dustin Futrell | McD | 2019-07-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-10-05 | Mike Tabbert
NJS-18 | NJS-18 | PI02211 | Verified | Torque cables after Hy-Pot 10NJSH0007A-C and 10NJJSH0008A-C | B | E | Chris Colvin | McD | 2019-07-09 | Chris Colvin | Const | 2019-11-05 | J.L. Bickham | 2019-12-16 | Mike Tabbert
NJS-18 | NJS-18 | PI02212 | Verified | Weld 10-NJS-XFM-0007A and 7B Transformers down | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02213 | Verified | Duct Seal transformer conduits | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-19 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02214 | Verified | Duct seal feeder cable conduitin 10-NJS-MCC-0007A and 7B | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-19 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02215 | Verified | Replace 10NJSH0008A stress cone | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02216 | Verified | Grounds torqued and marked on every ground | B | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02217 | Verified | Bond 10-NJS-MCC-0007A and 7B ground bars | A | E | Dustin Futrell | McD | 2019-07-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-16 | Logan Holland
NJS-18 | NJS-18 | PI02218 | Verified | Put 10-NJS-MCC-0007A and 7B heaters on temp power | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-19 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI02219 | Verified | Clean floors of 10-NJS-MCC-0007A and 7B | A | E | Luis Cantu | McD | 2019-07-09 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
NJS-18 | NJS-18 | PI03754 | Verified | Ground bushings in DCS Cab RIO 2-1, 10-DCS-CAB-0201 at the raw water structure. | A | E | Dustin Futrell | McD | 2019-08-12 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Michael Law
NJS-18 | NJS-18 | PI03755 | Verified | Remove temporary shipping brace on transformer & overhead fan in the raw water enclosure. | B | E | Dustin Futrell | McD | 2019-08-12 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-21 | Fred Michael
NJS-18 | NJS-18 | PI03756 | Verified | Re-pull cables 10NJSC0085 & 10NJSC0086 and land on correct termination points in 10-NJS-MCC-0007A & 7B in the raw water enclosure. | A | E | Mike Tabbert | McD | 2019-08-12 | Mike Tabbert | Const | 2019-08-13 | Dustin Futrell | 2019-08-16 | Logan Holland
NJS-18 | NJS-18 | PI03757 | Verified | Tag all TBs in 10-DCS-CAB-0204 at the raw water structure. | B | E | Mike Tabbert | McD | 2019-08-12 | Mike Tabbert | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
NJS-18 | NJS-18 | PI03758 | Verified | Ground the cable tray in the raw water enclosure. | A | E | Dustin Futrell | McD | 2019-08-12 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Michael Law
NJS-18 | NJS-18 | PI03759 | Verified | Finish heater circuit in 10-NJS-MCC-0007A in the raw water enclosure. | A | E | Chris Colvin | McD | 2019-08-12 | Chris Colvin | Const | 2019-08-19 | Mike Tabbert | 2020-01-15 | Michael Law
NJS-18 | NJS-18 | PI03760 | Verified | Finish heater circuit in 10-NJS-MCC-0007B in the raw water enclosure. | A | E | Chris Colvin | McD | 2019-08-12 | Chris Colvin | Const | 2019-08-19 | Mike Tabbert | 2020-01-15 | Michael Law
NJS-18 | NJS-18 | PI03761 | Verified | Connect insulated ground in 10-DCS-CAB-0201 at the raw water structure. | A | E | Dustin Futrell | McD | 2019-08-12 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
NJS-18 | NJS-18 | PI04646 | Verified | Wiring changes on HRG for DCS points to check | B | E | Mike Tabbert | McD | 2019-08-27 | Mike Tabbert | Const | 2020-02-07 | Mike Tabbert | 2020-02-25 | Jonathan Donham
NJS-18 | NJS-18 | PI12833 | Verified | Remove cold galvanize and paint 10-NJS-XFM-007A enclosure | C | X | Johnny Campbell | McD | 2019-11-07 | Johnny Campbell | Comm | 2020-05-19 | Johnny Campbell | 2021-03-03 | John Watts
NJS-18 | NJS-18 | PI12834 | Verified | Remove protective paper cover and clean Eaton panel at West side of 10-NJS-XFM-007A | C | E | Chris Colvin | McD | 2019-11-07 | Chris Colvin | Comm | 2020-04-22 | Matt Gilmore | 2020-05-13 | Randy Carpenter
NJS-18 | NJS-18 | PI12835 | Verified | Tighten loose bolts at bottom of 10-NJS-XFM-007A enclosure South side | C | E | Jonathan Donham | McD | 2019-11-07 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-05-13 | Randy Carpenter
NJS-18 | NJS-18 | PI12836 | Verified | Tighten trim around top of 10-NJS-XFM-007A enclosure | C | E | Chris Colvin | McD | 2019-11-07 | Chris Colvin | Comm | 2020-04-14 | Chris Colvin | 2020-05-13 | Randy Carpenter
NJS-18 | NJS-18 | PI12837 | Verified | Seal ground cable conduit at 10-NJS-XFM-007A | C | E | Chris Colvin | McD | 2019-11-07 | Chris Colvin | Comm | 2020-04-14 | Chris Colvin | 2020-05-13 | Randy Carpenter
NJS-18 | NJS-18 | PI12838 | Verified | Remove cold galvanize and paint 10-NJS-XFM-007B enclosure | C | X | Jerry Smith | McD | 2019-11-07 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-05-13 | Randy Carpenter
NJS-18 | NJS-18 | PI12839 | Verified | Tighten trim around top of 10-NJS-XFM-007B enclosure | C | E | Jonathan Donham | McD | 2019-11-07 | Jonathan Donham | Comm | 2020-02-27 | Fred Michael | 2020-05-13 | Randy Carpenter
NJS-18 | NJS-18 | PI12840 | Verified | Tighten bolts on all four sides of 10-NJS-XFM-007B enclosure | C | E | Jonathan Donham | McD | 2019-11-07 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-05-13 | Randy Carpenter
NJS-18 | NJS-18 | PI12841 | Verified | Install missing enclosure bolts on all four sides of 10-NJS-XFM-007B enclosure | C | E | Jonathan Donham | McD | 2019-11-07 | Jonathan Donham | Comm | 2020-06-02 | Randy Carpenter | 2020-06-04 | Donovan Anderson
NJS-18 | NJS-18 | PI12842 | Verified | Seal ground cable conduit at 10-NJS-XFM-007B | C | E | Chris Colvin | McD | 2019-11-07 | Chris Colvin | Comm | 2020-04-14 | Chris Colvin | 2020-05-13 | Randy Carpenter
NJS-18 | NJS-18 | PI12843 | Verified | 10-ESH-XFM-0007 is mislabled, currently indicates EHS, replace with new label | C | E | Chris Colvin | McD | 2019-11-07 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-05-13 | Randy Carpenter
NJS-18 | NJS-18 | PI12844 | Verified | Loose bolts at 10-ESH-XFM-0007 enclosure | C | E | Jonathan Donham | McD | 2019-11-07 | Jonathan Donham | Comm | 2020-02-10 | Fred Michael | 2020-02-25 | Randy Carpenter
NJS-18 | NJS-18 | PI12845 | Verified | 10-ESH-PNL-0007 inside panel cover needs to be secured | C | E | Chris Colvin | McD | 2019-11-07 | Chris Colvin | Comm | 2020-04-14 | Chris Colvin | 2020-05-13 | Randy Carpenter
NJS-18 | NJS-18 | PI12846 | Verified | 10-ESH-PNL-0007 outer door is missing latch at top | C | E | Mike Tabbert | McD | 2019-11-07 | Mike Tabbert | Comm | 2019-12-24 | Michael Law | 2020-01-13 | Mike Tabbert
NJS-21 | NJS-21 | PI08242 | Verified | Panel 1B-NJS-PNL-0002 at 1B CEMS - needs label. | C | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
NJS-21 | NJS-21 | PI08243 | Verified | Panel 1B-NJS-PNL-0002 at 1B CEMS - needs ground. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-24 | Brad Stanford | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08244 | Verified | Panel 1B-NJS-PNL-0002 at 1B CEMS - needs grout. | C | C | Johnny Campbell | McD | 2019-10-01 | Johnny Campbell | Const | 2019-10-22 | Johnny Campbell | 2019-10-24 | Shannon Scott
NJS-21 | NJS-21 | PI08245 | Verified | Panel 1B-NJS-PNL-0002 at 1B CEMS - needs panel schedule. | B | E | Mike Tabbert | McD | 2019-10-01 | Mike Tabbert | Const |  |  | 2019-12-16 | Fred Michael
NJS-21 | NJS-21 | PI08246 | Verified | Panel 1A-NJS-PNL-0002 at 1A CEMS - needs label. | C | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
NJS-21 | NJS-21 | PI08247 | Verified | Panel 1A-NJS-PNL-0002 at 1A CEMS - needs ground. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-24 | Brad Stanford | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08248 | Verified | Panel 1A-NJS-PNL-0002 at 1A CEMS - needs grout. | C | C | Johnny Campbell | McD | 2019-10-01 | Johnny Campbell | Const | 2019-10-22 | Johnny Campbell | 2019-10-24 | Shannon Scott
NJS-21 | NJS-21 | PI08249 | Verified | Panel 1A-NJS-PNL-0002 at 1A CEMS - needs panel schedule. | B | E | Mike Tabbert | McD | 2019-10-01 | Mike Tabbert | Const |  |  | 2019-12-16 | Fred Michael
NJS-21 | NJS-21 | PI08250 | Verified | Panel 1A-NJS-PNL-0004 at top of 1A HRSG east side - needs label | C | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
NJS-21 | NJS-21 | PI08251 | Verified | Panel 1A-NJS-PNL-0004 at top of 1A HRSG east side - needs ground. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-24 | Brad Stanford | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08252 | Verified | Panel 1A-NJS-PNL-0004 at top of 1A HRSG east side - run conduit to panel. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
NJS-21 | NJS-21 | PI08253 | Verified | Panel 1A-NJS-PNL-0004 at top of 1A HRSG east side - needs panel schedule. | B | E | Mike Tabbert | McD | 2019-10-01 | Mike Tabbert | Const |  |  | 2019-12-16 | Fred Michael
NJS-21 | NJS-21 | PI08254 | Verified | Panel 1A-NJS-PNL-0003 at top of 1A HRSG west side - needs label. | C | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
NJS-21 | NJS-21 | PI08255 | Verified | Panel 1A-NJS-PNL-0003 at top of 1A HRSG west side - needs ground. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-24 | Brad Stanford | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08256 | Verified | Panel 1A-NJS-PNL-0003 at top of 1A HRSG west side - run conduit to panel. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
NJS-21 | NJS-21 | PI08257 | Verified | Panel 1A-NJS-PNL-0003 at top of 1A HRSG west side - needs panel schedule. | B | E | Mike Tabbert | McD | 2019-10-01 | Mike Tabbert | Const |  |  | 2019-12-16 | Fred Michael
NJS-21 | NJS-21 | PI08258 | Verified | Panel 1B-NJS-PNL-0004 at 1B at top of 1B HRSG east side - needs label. | C | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
NJS-21 | NJS-21 | PI08259 | Verified | Panel 1B-NJS-PNL-0004 at 1B at top of 1B HRSG east side - needs ground. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-24 | Brad Stanford | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08260 | Verified | Panel 1B-NJS-PNL-0004 at 1B at top of 1B HRSG east side - run conduit to panel. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
NJS-21 | NJS-21 | PI08261 | Verified | Panel 1B-NJS-PNL-0004 at 1B at top of 1B HRSG east side - needs panel schedule. | B | E | Mike Tabbert | McD | 2019-10-01 | Mike Tabbert | Const |  |  | 2019-12-16 | Fred Michael
NJS-21 | NJS-21 | PI08262 | Verified | Panel 1B-NJS-PNL-0003 at 1B at top of 1B HRSG west side - needs label. | C | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
NJS-21 | NJS-21 | PI08263 | Verified | Panel 1B-NJS-PNL-0003 at 1B at top of 1B HRSG west side - needs ground. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08264 | Verified | Panel 1B-NJS-PNL-0003 at 1B at top of 1B HRSG west side - run conduit to panel. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
NJS-21 | NJS-21 | PI08265 | Verified | Panel 1B-NJS-PNL-0003 at 1B at top of 1B HRSG west side - rotate panel 90 deg. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
NJS-21 | NJS-21 | PI08266 | Verified | Panel 1B-NJS-PNL-0003 at 1B at top of 1B HRSG west side - needs panel schedule. | B | E | Mike Tabbert | McD | 2019-10-01 | Mike Tabbert | Const |  |  | 2019-12-16 | Fred Michael
NJS-21 | NJS-21 | PI08267 | Verified | 10NJSL0008A, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08268 | Verified | 10NJSL0008B, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-06 | Mike Tabbert
NJS-21 | NJS-21 | PI08269 | Verified | 10NJSL0008C, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-06 | Mike Tabbert
NJS-21 | NJS-21 | PI08270 | Verified | 10NJSL0008G, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-06 | Mike Tabbert
NJS-21 | NJS-21 | PI08271 | Verified | 1BNJSK0005, Pull Cable | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08272 | Verified | 10NJSL0008A, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08273 | Verified | 10NJSL0008B, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08274 | Verified | 10NJSL0008C, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08275 | Verified | 10NJSL0008G, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08280 | Verified | 1ANJSK0004, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
NJS-21 | NJS-21 | PI08281 | Verified | 1ANJSK0005, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
NJS-21 | NJS-21 | PI08282 | Verified | 1ANJSK0006, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-10-04 | Mike Tabbert
NJS-21 | NJS-21 | PI08283 | Verified | 1BNJSK0005, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08284 | Verified | 1BNJSK0006, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08285 | Verified | 1CNJSK0001, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-25 | Mike Tabbert
NJS-21 | NJS-21 | PI08286 | Verified | 1CNJSK0002, From Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-16 | Dustin Futrell | 2019-10-25 | Mike Tabbert
NJS-21 | NJS-21 | PI08287 | Verified | 10NJSL0008A, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08288 | Verified | 10NJSL0008B, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08289 | Verified | 10NJSL0008C, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08290 | Verified | 10NJSL0008G, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08295 | Verified | 1ANJSK0006, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-30 | Dustin Futrell | 2019-11-06 | Mike Tabbert
NJS-21 | NJS-21 | PI08296 | Verified | 1BNJSK0005, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08297 | Verified | 1BNJSK0006, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08298 | Verified | 1CNJSK0001, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
NJS-21 | NJS-21 | PI08299 | Verified | 1CNJSK0002, To Termination | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const | 2019-10-11 | Dustin Futrell | 2019-10-15 | Mike Tabbert
NJS-21 | NJS-21 | PI08300 | Verified | Install 10-NJS-PNL-0008, location ground HRSG A. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08301 | Verified | 10-NJS-PNL-0008, Install conduit sealtight and grounding. | A | E | Dustin Futrell | McD | 2019-10-01 | Dustin Futrell | Const |  |  | 2019-11-09 | Mike Tabbert
NJS-21 | NJS-21 | PI08302 | Verified | 10-NJS-PNL-0008, Tag panel and install panel schedule. | B | E | Mike Tabbert | McD | 2019-10-01 | Mike Tabbert | Const |  |  | 2019-12-16 | Fred Michael
NJS-21 | NJS-21 | PI12947 | Verified | 1A-NJS-PNL-0004 - add support. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const |  |  | 2019-12-16 | Fred Michael
NJS-21 | NJS-21 | PI12948 | Verified | 1A-NJS-PNL-0004 - clean inside / outside of panel. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const |  |  | 2019-12-16 | Fred Michael
NJS-21 | NJS-21 | PI12949 | Verified | 1A-NJS-PNL-0004 - ground inside door panel. | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-13 | Mike Tabbert
NJS-21 | NJS-21 | PI12950 | Verified | 1A-NJS-PNL-0003 - re-route ground to cable tray ground. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const |  |  | 2019-12-16 | Fred Michael
NJS-21 | NJS-21 | PI12951 | Verified | 1A-NJS-PNL-0003 - need two 2" Hoffman plugs. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const |  |  | 2019-12-16 | Fred Michael
NJS-21 | NJS-21 | PI12985 | Verified | Panel 1B-NJS-PNL-0004, Redo grounding cable, existing cable is bird caged and twisted. | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-13 | Mike Tabbert
NJS-21 | NJS-21 | PI12986 | Verified | Panel 1B-NJS-PNL-0004, Add bracing to panel support frame to make more ridged. | B | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const |  |  | 2019-12-17 | Fred Michael
NJS-21 | NJS-21 | PI12987 | Verified | Panel 1B-NJS-PNL-0004, Secure feeder cable to back of panel | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-13 | Mike Tabbert
NJS-21 | NJS-21 | PI12988 | Verified | Panel 1B-NJS-PNL-0004, Install Kick Plate around grading penetrations. | C | M | Tim Gallegos | McD | 2019-11-13 | Tim Gallegos | Const | 2020-05-12 | Tim Gallegos | 2020-05-19 | Mike Tabbert
NJS-21 | NJS-21 | PI12989 | Verified | Panel 1B-NJS-PNL-0003, Secure feeder cable to back of panel. | A | E | Dustin Futrell | McD | 2019-11-13 | Dustin Futrell | Const |  |  | 2019-11-13 | Mike Tabbert
NJS-21 | NJS-21 | PI12990 | Verified | Panel 1B-NJS-PNL-0008, Grout panel support. | C | C | Johnny Campbell | McD | 2019-11-13 | Johnny Campbell | Const | 2020-04-08 | Johnny Campbell | 2020-04-21 | Mike Tabbert
NJS-21 | NJS-21 | PI12991 | Verified | Panel 1B-NJS-PNL-0008, T-Cover Missing screw. | C | E | Chris Colvin | McD | 2019-11-13 | Chris Colvin | Const | 2020-04-28 | Matt Gilmore | 2020-04-29 | Mike Tabbert
NJS-21 | NJS-21 | PI15211 | Verified | Need waterproof panel schedule for 1A-NJS-PNL-0003; HRSG 1A Top MOV Distribution PNL 3 | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
NJS-21 | NJS-21 | PI15212 | Verified | Clean up inside 1A-NJS-PNL-0003; HRSG 1A Top MOV Distribution PNL 3 | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-25 | Randy Carpenter
NJS-21 | NJS-21 | PI15214 | Verified | 1A-NJS-PNL-0003; HRSG 1A Top MOV Distribution PNL 3 needs touch up paint | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
NJS-21 | NJS-21 | PI15216 | Verified | Need waterproof panel schedule for 1A-NJS-PNL-0004; HRSG 1A Top MOV Distribution PNL 4 | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
NJS-21 | NJS-21 | PI15217 | Verified | Clean up inside 1A-NJS-PNL-0004; HRSG 1A Top MOV Distribution PNL 4 | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-25 | Randy Carpenter
NJS-21 | NJS-21 | PI15219 | Verified | 1A-NJS-PNL-0004; HRSG 1A Top MOV Distribution PNL 4 needs touch up paint | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
NJS-21 | NJS-21 | PI15221 | Verified | Need waterproof panel schedule for 1B-NJS-PNL-0003; HRSG 1B Top MOV Distribution PNL 3 | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
NJS-21 | NJS-21 | PI15222 | Verified | Clean up inside 1B-NJS-PNL-0003; HRSG 1B Top MOV Distribution PNL 3 | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-25 | Randy Carpenter
NJS-21 | NJS-21 | PI15224 | Verified | 1B-NJS-PNL-0003; HRSG 1B Top MOV Distribution PNL 3 needs touch up paint | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-15 | Johnny Campbell | 2020-04-24 | Mark Williamson
NJS-21 | NJS-21 | PI15226 | Verified | Need waterproof panel schedule for 1B-NJS-PNL-0004; HRSG 1B Top MOV Distribution PNL 4 | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
NJS-21 | NJS-21 | PI15227 | Verified | Clean up inside 1B-NJS-PNL-0004; HRSG 1B Top MOV Distribution PNL 4 | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-25 | Randy Carpenter
NJS-21 | NJS-21 | PI15229 | Verified | 1B-NJS-PNL-0004; HRSG 1B Top MOV Distribution PNL 4 needs touch up paint | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-15 | Johnny Campbell | 2020-04-24 | Mark Williamson
NJS-21 | NJS-21 | PI15230 | Verified | Trim plate missing inside 10-NJS-PNL-0005; CO2 & Hydrogen Area Power Panel | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-25 | Randy Carpenter
NJS-21 | NJS-21 | PI15231 | Verified | Trim plate hold down plates missing inside 10-NJS-PNL-0005; CO2 & Hydrogen Area Power Panel | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-25 | Randy Carpenter
NJS-21 | NJS-21 | PI15232 | Verified | 10-NJS-PNL-0005; CO2 & Hydrogen Area Power Panel needs waterproof panel schedule | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm | 2020-01-20 | Mike Tabbert | 2020-01-20 | Fred Michael
NJS-21 | NJS-21 | PI15233 | Verified | 10-NJS-PNL-0005; CO2 & Hydrogen Area Power Panel needs touch up paint | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-14 | Johnny Campbell | 2020-04-24 | Mark Williamson
NJS-21 | NJS-21 | PI15235 | Verified | Incoming cables to 10-NJS-PNL-0005; CO2 & Hydrogen Area Power Panel need heat shrink | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2021-03-03 | John Watts
NJS-21 | NJS-21 | PI15236 | Verified | 10-NJS-PNL-0008; 480V Main PDC Inst. Water Heater Panel needs waterproof panel schedule, E side of HRSG A, bottom of stairs | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
NJS-21 | NJS-21 | PI15238 | Verified | 1A-NJS-PNL-0002; 480V, HRSG 1A Bottom MOV Distribution PNL 2 needs waterproof panel schedule, NE side of HRSG A, near CEMS bldg | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
NJS-21 | NJS-21 | PI15239 | Verified | 1A-NJS-PNL-0002; 480V, HRSG 1A Bottom MOV Distribution PNL 2 needs touch up paint, NE side of HRSG A, near CEMS bldg | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
NJS-21 | NJS-21 | PI15240 | Verified | Conduit to 1A-NJS-PNL-0002; 480V, HRSG 1A Bottom MOV Distribution PNL 2 needs condolet covers, NE side of HRSG A, near CEMS bldg | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2021-03-03 | John Watts
NJS-21 | NJS-21 | PI15241 | Verified | Bottom trim plate missing inside 1B-NJS-PNL-0002; 480V, HRSG 1B Bottom East MOV Distribution PNL 2, NE side HRSG B, near CEMs bldg | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2021-03-03 | John Watts
NJS-21 | NJS-21 | PI15242 | Verified | 2" LB conduit missing covers at 1B-NJS-PNL-0002; 480V, HRSG 1B Bottom East MOV Distribution PNL 2, NE side HRSG B, near CEMs bldg | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2021-03-03 | John Watts
NJS-21 | NJS-21 | PI15243 | Verified | Need touch up paint at 1B-NJS-PNL-0002; 480V, HRSG 1B Bottom East MOV Distribution PNL 2, NE side HRSG B, near CEMs bldg | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-13 | Johnny Campbell | 2020-04-24 | Mark Williamson
NJS-21 | NJS-21 | PI15244 | Verified | Missing trim plate hold down plate at 1C-NJS-PNL-0001; 480V, STG Area Service Panel, STG Mez, SE side | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-04-06 | Johnny Campbell | 2020-06-02 | Randy Carpenter
NJS-21 | NJS-21 | PI15245 | Verified | Need touch up paint at 1C-NJS-PNL-0001; 480V, STG Area Service Panel, STG Mez, SE side | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-06 | Johnny Campbell | 2020-06-02 | Randy Carpenter
NJS-21 | NJS-21 | PI15246 | Verified | Need conduit condolet covers at 1C-NJS-PNL-0001; 480V, STG Area Service Panel, STG Mez, SE side | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2020-06-02 | Randy Carpenter
NJS-21 | NJS-21 | PI15247 | Verified | Need waterproof panel schedule at 1C-NJS-PNL-0001; 480V, STG Area Service Panel, STG Mez, SE side | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm | 2020-01-20 | Mike Tabbert | 2020-01-22 | Fred Michael
NJS-21 | NJS-21 | PI15248 | Verified | Eight cables need to be terminated at 1C-NJS-PNL-0001; 480V, STG Area Service Panel, STG Mez, SE side | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-06-02 | Randy Carpenter
NJS-21 | NJS-21 | PI15249 | Verified | Need waterproof panel schedule at 1C-NJS-PNL-0002; 480V, STG Area Service Panel, STG Mez, SE side | C | E | Mike Tabbert | McD | 2020-01-06 | Mike Tabbert | Comm |  |  | 2020-01-20 | Fred Michael
NJS-21 | NJS-21 | PI15250 | Verified | Need touch up paint at 1C-NJS-PNL-0002; 480V, STG Area Service Panel, STG Mez, SE side | C | X | Johnny Campbell | McD | 2020-01-06 | Johnny Campbell | Comm | 2020-04-15 | Johnny Campbell | 2020-06-02 | Randy Carpenter
NJS-21 | NJS-21 | PI15251 | Verified | Missing condolet covers at 1C-NJS-PNL-0002; 480V, STG Area Service Panel, STG Mez, SE side | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm | 2020-04-28 | Matt Gilmore | 2020-06-02 | Randy Carpenter
NOS-01 | NOS-01 | PI00198 | Verified | Pre-commissioning activity to verify all CT integrity. | B | E | Logan Holland | McD | 2019-02-19 | Logan Holland | Const | 2019-04-03 | Ed Gober | 2019-04-03 | Ed Gober
NOS-01 | NOS-01 | PI00204 | Verified | Missing 2 nuts & washers for back plate in 10-NOS-SWG-0001A/B, compartment 7A. | B | E | Mike Tabbert | McD | 2019-02-26 | Mike Tabbert | Const | 2019-03-26 | Mike Tabbert | 2019-04-09 | Shannon Scott
NOS-01 | NOS-01 | PI00210 | Verified | 10-NOS-SWG-0001A, 10-NOS-MCC-0001A, Arc Flash Labels. | B | E | Michael Law | McD | 2019-02-26 | Michael Law | Const | 2019-05-20 | Mike Tabbert | 2019-05-20 | Mike Tabbert
NOS-01 | NOS-01 | PI00277 | Verified | 10-NOS-SWG-0001A, Install Tie Breaker. | B | E | Shannon Savoy | McD | 2019-03-25 | Shannon Savoy | Comm | 2019-04-01 | Mike Tabbert | 2019-04-01 | Mike Tabbert
NOS-01 | NOS-01 | PI09772 | Verified | Grounding breakers to cover and properly store | C | E | Mike Tabbert | McD | 2019-10-22 | Mike Tabbert | Comm | 2020-03-18 | Jonathan Donham | 2020-03-18 | Randy Carpenter
NOS-01 | NOS-01 | PI09773 | Verified | Spare components and spare tools to store properly and coordinate with ops | C | E | Jonathan Donham | McD | 2019-10-22 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2021-01-05 | Keith Pollock
NOS-01 | NOS-01 | PI09774 | Verified | 2in conduit by the spare cabinet of SWG-0001B need ground to tray | C | E | Chris Colvin | McD | 2019-10-22 | Chris Colvin | Comm | 2020-05-04 | Matt Gilmore | 2021-01-05 | Keith Pollock
NOS-01 | NOS-01 | PI09775 | Verified | Need tag on LQ-1106 to 1120 (1x3 on white background) | C | E | Fred Michael | McD | 2019-10-22 | Fred Michael | Comm |  |  | 2020-01-08 | Fred Michael
NOS-01 | NOS-01 | PI09776 | Verified | Verify all redlines for the system (if any) are submitted and issued to Mike Tabbert. | C | E | Jonathan Donham | McD | 2019-10-22 | Jonathan Donham | Comm | 2020-04-28 | Michael Law | 2020-06-02 | Randy Carpenter
NOS-01 | NOS-01 | PI15013 | Verified | Clean up inside 10-NOS-SWG-0001A, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-02-27 | Fred Michael
NOS-01 | NOS-01 | PI15014 | Verified | Replace wiring duct covers inside 10-SWG-0001A , Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NOS-01 | NOS-01 | PI15015 | Verified | Heat shrink cable/wire tags inside 10-NOS-SWG-1000A, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NOS-01 | NOS-01 | PI15016 | Verified | Replace cable tags that are too big to heat shrink inside 10-NOS-SWG-1000A, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NOS-01 | NOS-01 | PI17849 | Verified | SEL-3530-1A voltage and amp readings on main switchgear are bad quality so the total auxiliary power usage on the buss is not reading | C | E | Mike Wilferd | McD | 2020-03-16 | Mike Wilferd | Comm | 2020-04-02 | Mike Wilferd | 2020-04-15 | Keith Pollock
NOS-01 | NOS-01 | PI18383 | Verified | Install conduit and F.O. cable for RTAC to 480V switchgears, 3 each Main PDC. | C | E | Mike Tabbert | McD | 2020-05-28 | Mike Tabbert | Const | 2020-06-16 | Mike Tabbert | 2021-03-03 | John Watts
NOS-02 | NOS-02 | PI00183 | Verified | Arc Flash Lables Need to be Installed. | B | E | Michael Law | McD | 2019-02-18 | Michael Law | Const | 2019-05-20 | Mike Tabbert | 2019-05-20 | Mike Tabbert
NOS-02 | NOS-02 | PI00187 | Verified | Re-locate bare ground to trough in Main Breaker - Bus B, compartments 9A & 9D | A | E | Shannon Savoy | McD | 2019-02-18 | Shannon Savoy | Const | 2019-02-18 | Dan Dula | 2019-02-19 | Curtis Platzek
NOS-02 | NOS-02 | PI00189 | Verified | Seal all penetrations. | C | E | Chris Colvin | McD | 2019-02-18 | Chris Colvin | Const | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
NOS-02 | NOS-02 | PI00199 | Verified | Pre-commissioning activity to verify all CT integrity. | B | E | Logan Holland | McD | 2019-02-19 | Logan Holland | Const | 2019-04-03 | Ed Gober | 2019-04-03 | Ed Gober
NOS-02 | NOS-02 | PI09771 | Verified | Handle missing on cubicle 12D (Spare) | C | E | Jonathan Donham | McD | 2019-10-22 | Jonathan Donham | Comm | 2020-03-02 | Jonathan Donham | 2021-01-05 | Keith Pollock
NOS-02 | NOS-02 | PI15017 | Verified | Clean up inside 10-NOS-SWG-0001B, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NOS-02 | NOS-02 | PI15018 | Verified | 50 OHM BNC Terminator missing at 10-NOS-SWG-0001B, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
NOS-02 | NOS-02 | PI15019 | Verified | Replace wiring duct covers inside 10-NOS-SWG-0001B , Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NOS-02 | NOS-02 | PI15020 | Verified | Heat shrink cable/wire tags inside 10-NOS-SWG-0001B, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NOS-02 | NOS-02 | PI17850 | Verified | SEL-3530-1B voltage and amp readings on main switchgear are bad quality so the total auxiliary power usage on the buss is not reading | C | E | Mike Wilferd | McD | 2020-03-16 | Mike Wilferd | Comm | 2020-04-02 | Mike Wilferd | 2020-04-15 | Keith Pollock
NOS-03 | NOS-03 | PI00179 | Verified | Clean each compartment 10-NOS-MCC-002A & 10-NOS-SWG-0002A | A | E | Phil Work | McD | 2019-02-07 | Phil Work | Const | 2019-02-19 | Dan Dula | 2019-02-19 | Mike Tabbert
NOS-03 | NOS-03 | PI00184 | Verified | Install Arc Flash Labels 10-NOS-SWG-0002A | B | E | Michael Law | McD | 2019-02-18 | Michael Law | Const | 2019-05-20 | Mike Tabbert | 2019-05-20 | Mike Tabbert
NOS-03 | NOS-03 | PI00190 | Verified | Seal all penetrations. | B | E | Chris Colvin | McD | 2019-02-18 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-04-21 | Michael Law
NOS-03 | NOS-03 | PI00192 | Verified | Re-locate bare ground to trough in Main Breaker - Bus A, compartments 5A & 5D | A | E | Shannon Savoy | McD | 2019-02-18 | Shannon Savoy | Const | 2019-02-18 | Dan Dula | 2019-02-19 | Curtis Platzek
NOS-03 | NOS-03 | PI00193 | Verified | Pull & terminate cable 1BNOSC0010 | A | E | Shannon Savoy | McD | 2019-02-18 | Shannon Savoy | Const | 2019-02-20 | Dan Dula | 2019-02-20 | Gregg Sellers
NOS-03 | NOS-03 | PI00200 | Verified | Pre-commissioning activity to verify all CT integrity. | B | E | Logan Holland | McD | 2019-02-19 | Logan Holland | Const | 2019-04-03 | Ed Gober | 2019-04-03 | Ed Gober
NOS-03 | NOS-03 | PI00278 | Verified | 10-NOS-SWG-0002A, Install Tie Breaker | B | E | Shannon Savoy | McD | 2019-03-25 | Shannon Savoy | Comm | 2019-04-03 | Shannon Savoy | 2019-04-03 | Mike Tabbert
NOS-03 | NOS-03 | PI15021 | Verified | Clean up inside 10-NOS-SWG-0002A, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NOS-03 | NOS-03 | PI15022 | Verified | Need phenolic label for tag no. 10-NOS-SWG-0002A (front side), Main PDC | C | E | Mike Tabbert | McD | 2020-01-02 | Mike Tabbert | Comm | 2020-04-29 | Mike Tabbert | 2020-04-29 | Randy Carpenter
NOS-03 | NOS-03 | PI17851 | Verified | SEL-3530-2A voltage and amp readings on main switchgear are bad quality so the total auxiliary power usage on the buss is not reading | C | E | Mike Wilferd | McD | 2020-03-16 | Mike Wilferd | Comm | 2020-04-14 | Mike Wilferd | 2020-04-15 | Keith Pollock
NOS-04 | NOS-04 | PI00185 | Verified | Arc flash labels 10-NOS-SWG-0002B | B | E | Michael Law | McD | 2019-02-18 | Michael Law | Const | 2019-05-20 | Mike Tabbert | 2019-05-20 | Mike Tabbert
NOS-04 | NOS-04 | PI00186 | Verified | 10-NOS-SWG-0002B compartment 8A door will not open, linkage seems like it has come apart. | B | E | Mike Tabbert | EAT | 2019-02-18 | Mike Tabbert | Const | 2019-03-26 | Mike Tabbert | 2019-03-26 | Mike Tabbert
NOS-04 | NOS-04 | PI00191 | Verified | Seal all penetrations. | B | E | Chris Colvin | McD | 2019-02-18 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-13 | Jonathan Donham
NOS-04 | NOS-04 | PI00201 | Verified | Pre-commissioning activity to verify all CT integrity. | B | E | Logan Holland | McD | 2019-02-19 | Logan Holland | Const | 2019-04-03 | Ed Gober | 2019-04-03 | Ed Gober
NOS-04 | NOS-04 | PI15023 | Verified | Clean up inside 10-NOS-SWG-0002B, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NOS-04 | NOS-04 | PI15024 | Verified | Need phenolic label for tag no. 10-NOS-SWG-0002B (front side), Main PDC | C | E | Mike Tabbert | McD | 2020-01-02 | Mike Tabbert | Comm | 2020-04-29 | Mike Tabbert | 2020-04-29 | Randy Carpenter
NOS-04 | NOS-04 | PI15025 | Verified | 50 OHM BNC Terminator missing at 10-NOS-SWG-0002B, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
NOS-04 | NOS-04 | PI17852 | Verified | SEL-3530-2B voltage and amp readings on main switchgear are bad quality so the total auxiliary power usage on the buss is not reading | C | E | Mike Wilferd | McD | 2020-03-16 | Mike Wilferd | Comm | 2020-04-02 | Mike Wilferd | 2020-04-15 | Keith Pollock
NQS-01 | NQS-01 | PI00417 | Verified | 10NOSC0029, Terminate | A | E | Shannon Savoy | McD | 2019-04-03 | Shannon Savoy | Const | 2019-04-08 | Shannon Savoy | 2019-04-08 | Mike Tabbert
NQS-01 | NQS-01 | PI00418 | Verified | Resolve discrepancy between MP Husky wiring diagram (dwg. # 071746-202) and actual terminations for feeder cables in rear compartment of 10-NOS-BD-0002A. | A | E | Mike Tabbert | McD | 2019-04-03 | Mike Tabbert | Const | 2019-04-11 | Shannon Savoy | 2019-06-21 | Logan Holland
NQS-01 | NQS-01 | PI00419 | Verified | Clean debris from cable tray 10-NOS-BD-0002A, east side of main PDC. | C | E | Shannon Savoy | McD | 2019-04-03 | Shannon Savoy | Const | 2019-04-08 | Shannon Savoy | 2019-04-09 | Mike Tabbert
NQS-01 | NQS-01 | PI00420 | Verified | Seal all conduits after commissioning. | B | E | Logan Holland | McD | 2019-04-03 | Logan Holland | Const | 2019-06-21 | Logan Holland | 2019-06-21 | Logan Holland
NQS-01 | NQS-01 | PI00421 | Verified | General clean up needed at the Unit A Aux. Transformer & area. | B | E | Luis Cantu | McD | 2019-04-03 | Luis Cantu | Const | 2019-04-08 | Shannon Savoy | 2019-06-21 | Logan Holland
NQS-01 | NQS-01 | PI00422 | Verified | Remove temp. power on the Unit A Aux. Transformer. | B | E | Luis Cantu | McD | 2019-04-03 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-19 | Logan Holland
NQS-01 | NQS-01 | PI00423 | Verified | General clean up needed in / at GCB 1A-NQS-BKR-0001. | A | E | Luis Cantu | McD | 2019-04-03 | Luis Cantu | Const | 2019-04-08 | Shannon Savoy | 2019-06-21 | Logan Holland
NQS-01 | NQS-01 | PI00424 | Verified | Complete conduit at GCB 1A-NQS-BKR-0001. | A | E | Luis Cantu | McD | 2019-04-03 | Luis Cantu | Const | 2019-04-09 | Shannon Savoy | 2019-06-21 | Logan Holland
NQS-01 | NQS-01 | PI00425 | Verified | Complete grounding on the Unit 1A generator circuit breaker. | A | E | Luis Cantu | McD | 2019-04-03 | Luis Cantu | Const | 2019-04-11 | Shannon Savoy | 2019-06-21 | Logan Holland
NQS-01 | NQS-01 | PI00426 | Verified | Center phase thermostat needs conduit & terms. on the isophase. | A | E | Luis Cantu | McD | 2019-04-03 | Luis Cantu | Const | 2019-04-15 | Shannon Savoy | 2019-06-21 | Logan Holland
NQS-01 | NQS-01 | PI00429 | Verified | Complete heater circ. on Unit 1A IPB. | A | E | Luis Cantu | McD | 2019-04-03 | Luis Cantu | Const | 2019-04-15 | Shannon Savoy | 2019-06-21 | Logan Holland
NQS-01 | NQS-01 | PI00430 | Verified | Need grating and hand rail installed on Generator Circuit Breaker Platform Unit A. | B | S | Robert Risher | McD | 2019-04-03 | Robert Risher | Const | 2019-05-23 | Tim Gallegos | 2019-05-30 | Mike Tabbert
NQS-01 | NQS-01 | PI00431 | Verified | Check connection bolts for tightness in the NORTH FIRE WALL - GCB 1A South area | A | E | Sheri Fritz | NCC | 2019-04-03 | Sheri Fritz | Const | 2019-04-05 | Jason Marshik | 2019-04-05 | Ayda Chaves
NQS-01 | NQS-01 | PI00432 | Verified | Perform HI POT Testing. (unit A) | A | E | Sheri Fritz | NCC | 2019-04-03 | Sheri Fritz | Const | 2019-04-12 | Mike Tabbert | 2019-04-12 | Mike Tabbert
NQS-01 | NQS-01 | PI00433 | Verified | Perform enclosure isolation check. | A | E | Luis Cantu | McD | 2019-04-03 | Luis Cantu | Const | 2019-04-30 | Shannon Savoy | 2019-06-21 | Logan Holland
NQS-01 | NQS-01 | PI00434 | Verified | Need grating and hand rail installed on Generator Circuit Breaker Platform Unit A | A | S | Robert Risher | McD | 2019-04-03 | Robert Risher | Const | 2019-04-04 | Robert Risher | 2019-04-08 | Mike Tabbert
NQS-01 | NQS-01 | PI00435 | Verified | 10-NOS-BD-0002A, Grout Bus Supports | B | C | Jessie Pipes | McD | 2019-04-03 | Jessie Pipes | Const | 2019-04-11 | Jessie Pipes | 2019-04-15 | Mike Tabbert
NQS-01 | NQS-01 | PI00436 | Verified | 10-NOS-CAB-0001A, Wire numbers 1ANOSK0001-2 and not landed. | B | E | Jonathan Donham | McD | 2019-04-03 | Jonathan Donham | Const | 2020-03-17 | Jonathan Donham | 2020-03-23 | Mike Tabbert
NQS-01 | NQS-01 | PI00437 | Verified | 1A-NOS-BKR-0001, Complete cable tray and conduit to Generator Circuit Breaker. (Cable Tray Labels, Grounding Cable Tray) | A | E | Shannon Savoy | McD | 2019-04-03 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-30 | Mike Tabbert
NQS-01 | NQS-01 | PI00438 | Verified | 1A-NOS-BKR-0001, Grout Cable Tray supports. | C | C | Johnny Campbell | McD | 2019-04-03 | Johnny Campbell | Const | 2019-07-30 | Johnny Campbell | 2019-10-07 | Mike Tabbert
NQS-01 | NQS-01 | PI00439 | Verified | 1ANQSK0004, Terminate Cable. | A | E | Shannon Savoy | McD | 2019-04-03 | Shannon Savoy | Const | 2019-04-08 | Shannon Savoy | 2019-04-08 | Mike Tabbert
NQS-01 | NQS-01 | PI00440 | Verified | 1ANQSK0005, Terminate Cable. | A | E | Shannon Savoy | McD | 2019-04-03 | Shannon Savoy | Const | 2019-04-04 | Mike Tabbert | 2019-04-04 | Mike Tabbert
NQS-01 | NQS-01 | PI00441 | Verified | 1ANQSK0006, Terminate Cable. | A | E | Shannon Savoy | McD | 2019-04-03 | Shannon Savoy | Const | 2019-04-04 | Mike Tabbert | 2019-04-04 | Mike Tabbert
NQS-01 | NQS-01 | PI00442 | Verified | 1ANQSK0007, Terminate Cable. | A | E | Shannon Savoy | McD | 2019-04-03 | Shannon Savoy | Const | 2019-04-08 | Shannon Savoy | 2019-04-08 | Mike Tabbert
NQS-01 | NQS-01 | PI00443 | Verified | 1A-NOS-BKR-0001, Install interconnecting cables for Generator Circuit Breaker. | A | E | Shannon Savoy | McD | 2019-04-03 | Shannon Savoy | Const | 2019-04-15 | Shannon Savoy | 2019-04-15 | Mike Tabbert
NQS-01 | NQS-01 | PI00444 | Verified | Bolts missing on diagonal support at first IPB support south of Blast wall. | A | S | Robert Risher | McD | 2019-04-03 | Robert Risher | Const | 2019-04-09 | Robert Risher | 2019-04-10 | Neil Simon
NQS-01 | NQS-01 | PI00445 | Verified | Bolts missing at C phase at IPB saddle | A | S | Sheri Fritz | NCC | 2019-04-03 | Sheri Fritz | Const | 2019-04-05 | Jason Marshik | 2019-04-10 | Neil Simon
NQS-01 | NQS-01 | PI00446 | Verified | Loose and missing bolts at both kickers at first IPB support South of Blast wall. | A | S | Sheri Fritz | NCC | 2019-04-03 | Sheri Fritz | Const | 2019-04-05 | Jason Marshik | 2019-04-10 | Neil Simon
NQS-01 | NQS-01 | PI00447 | Verified | Repair damage to column face Northwest corner column inside face. | B | C | Jessie Pipes | McD | 2019-04-03 | Jessie Pipes | Const | 2019-04-03 | Jessie Pipes | 2019-04-12 | Neil Simon
NQS-01 | NQS-01 | PI00448 | Verified | Repair damage to Blast wall at horizontal joint between 1st and 2nd level West wall Northwest corner inside face. | B | C | Jessie Pipes | McD | 2019-04-03 | Jessie Pipes | Const | 2019-04-11 | Jessie Pipes | 2019-04-12 | Neil Simon
NQS-01 | NQS-01 | PI00449 | Verified | Repair damage to West face of middle north column inside face. | B | C | Jessie Pipes | McD | 2019-04-03 | Jessie Pipes | Const | 2019-04-11 | Jessie Pipes | 2019-04-12 | Neil Simon
NQS-01 | NQS-01 | PI00450 | Verified | Loose bolts on kicker of IPB support North of Blast wall. | A | S | Sheri Fritz | NCC | 2019-04-03 | Sheri Fritz | Const | 2019-04-08 | Robert Risher | 2019-04-12 | Neil Simon
NQS-01 | NQS-01 | PI00451 | Verified | Bolts missing at X bracing at IPB support north of Blast wall. | A | S | Sheri Fritz | NCC | 2019-04-03 | Sheri Fritz | Const | 2019-04-08 | Robert Risher | 2019-04-12 | Neil Simon
NQS-01 | NQS-01 | PI00452 | Verified | Remove wires and exposed rebar chairs and rub down side of foundation at SFC Transformer foundation. | B | C | Jessie Pipes | McD | 2019-04-03 | Jessie Pipes | Const | 2019-04-11 | Jessie Pipes | 2019-04-25 | Neil Simon
NQS-01 | NQS-01 | PI00453 | Verified | Remove exposed rebar chairs and rub down side of foundation at IPB support foundation. | B | C | Jessie Pipes | McD | 2019-04-03 | Jessie Pipes | Const | 2019-04-11 | Jessie Pipes | 2019-04-25 | Neil Simon
NQS-01 | NQS-01 | PI00454 | Verified | Bolts missing at bracing at IPB support North of Blast wall. | A | S | Robert Risher | McD | 2019-04-03 | Robert Risher | Const | 2019-04-03 | Robert Risher | 2019-04-10 | Neil Simon
NQS-01 | NQS-01 | PI00455 | Verified | Bolts missing at C phase IPB saddle North of Blast wall | A | S | Robert Risher | McD | 2019-04-03 | Robert Risher | Const | 2019-04-08 | Robert Risher | 2019-04-12 | Neil Simon
NQS-01 | NQS-01 | PI00386 | Verified | Verify braid installation. | A | E | Sheri Fritz | NCC | 2019-04-02 | Sheri Fritz | Const | 2019-04-18 | Ayda Chaves | 2019-06-21 | Logan Holland
NQS-01 | NQS-01 | PI00387 | Verified | Perform clean & close on transformer isophase box. | B | E | Sheri Fritz | NCC | 2019-04-02 | Sheri Fritz | Const | 2019-04-30 | Mike Tabbert | 2019-06-21 | Logan Holland
NQS-01 | NQS-01 | PI00532 | Verified | Provide all test reports needed for subsystem turnover. | B | E | Sheri Fritz | NCC | 2019-04-10 | Sheri Fritz | Const | 2019-07-24 | Ed Gober | 2019-07-24 | Ed Gober
NQS-01 | NQS-01 | PI00631 | Verified | Complete heater circ. on Unit 1A GSU side. | B | E | Shannon Savoy | McD | 2019-04-15 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-30 | Mike Tabbert
NQS-01 | NQS-01 | PI00636 | Verified | Replace GCB 1A Cover. | C | E | Luis Cantu | McD | 2019-04-17 | Luis Cantu |  | 2019-06-07 | Shannon Savoy | 2019-06-21 | Logan Holland
NQS-01 | NQS-01 | PI10253 | Verified | 10-NOS-XFM-0001A - XFM monitoring panel is missing the "Up" button on panel. | C | E | Chris Boudreaux | McD | 2019-10-24 | Chris Boudreaux | Comm |  |  | 2020-01-23 | Shannon Scott
NQS-01 | NQS-01 | PI12700 | Verified | 10-NOS-XFM-0001A - The oil inlet to the Calisto has a moderate leak at the fitting. | C | E | Jonathan Donham | McD | 2019-11-01 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2020-03-31 | John Watts
NQS-01 | NQS-01 | PI15026 | Verified | Clean up inside 1A-NQS-PNL-1000A. Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Mike Tabbert | 2020-02-05 | Shannon Scott
NQS-01 | NQS-01 | PI15027 | Verified | Seal cable floor penetrations inside 1A-NQS-PNL-1000A, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Mike Tabbert | 2020-02-05 | Shannon Scott
NQS-01 | NQS-01 | PI15028 | Verified | Replace wiring duct covers inside 1A-NQS-PNL-1000A, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Mike Tabbert | 2020-02-05 | Shannon Scott
NQS-01 | NQS-01 | PI15029 | Verified | Heat shrink cable/wire tags inside 1A-NQS-PNL-1000A, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Mike Tabbert | 2020-01-30 | Fred Michael
NQS-01 | NQS-01 | PI15030 | Verified | Replace cable tags that are too big to heat shrink inside 1A-NQS-PNL-1000A , Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Mike Tabbert | 2020-01-30 | Fred Michael
NQS-01 | NQS-01 | PI15031 | Verified | Need phenolic label for Tag no. of 1A-NQS-PNL-1000A (backside), Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-02-27 | Fred Michael
NQS-01 | NQS-01 | PI15032 | Verified | Clean up inside 1A-NQS-PNL-1000B, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Mike Tabbert | 2020-01-30 | Fred Michael
NQS-01 | NQS-01 | PI15033 | Verified | Seal cable floor penetrations inside 1A-NQS-PNL-1000B, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
NQS-01 | NQS-01 | PI15034 | Verified | Replace wiring duct covers inside 1A-NQS-PNL-1000B, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Mike Tabbert | 2020-01-30 | Fred Michael
NQS-01 | NQS-01 | PI15035 | Verified | Heat shrink cable/wire tags inside 1A-NQS-PNL-1000B, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Mike Tabbert | 2020-01-30 | Fred Michael
NQS-01 | NQS-01 | PI15036 | Verified | Replace cable tags that are too big to heat shrink inside 1A-NQS-PNL-1000B , Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Mike Tabbert | 2020-01-30 | Fred Michael
NQS-01 | NQS-01 | PI15037 | Verified | Need phenolic label for tag no. 1A-NQS-PNL-1000B (backside), Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-02-27 | Fred Michael
NQS-01 | NQS-01 | PI15038 | Verified | Cables not terminated, verify and identify as spares or terminate AT 1A-NQS-PNL-1000B, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Mike Tabbert | 2020-01-30 | Fred Michael
NQS-01 | NQS-01 | PI15039 | Verified | Loose shield cable needs to be landed or taped back inside 1A-NQS-PNL-1000B | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-02-27 | Fred Michael
NQS-01 | NQS-01 | PI15110 | Verified | NQS-01 boundary scoping is incorrect, revise drawings to identify correct boundaries | B | E | Eric Policarpio | McD | 2020-01-02 | Eric Policarpio | Comm | 2020-01-13 | Eric Policarpio | 2020-03-31 | Randy Carpenter
NQS-01 | NQS-01 | PI15111 | Verified | NQS-01 cable list is incorrect, should be total of 135 cables, revise cable list as necessary | B | E | Eric Policarpio | McD | 2020-01-02 | Eric Policarpio | Comm | 2020-01-13 | Eric Policarpio | 2020-03-31 | Randy Carpenter
NQS-01 | NQS-01 | PI15112 | Verified | Unit A Isophase Bus Duct I-Beam vertical support is not grounded at baseplate, south side of generator, ground level | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-05 | Chris Colvin | 2020-03-05 | Randy Carpenter
NQS-01 | NQS-01 | PI15113 | Verified | Unit A Generator Circuit Breaker support is missing bolt on platform southwest side | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2020-06-02 | Randy Carpenter
NQS-01 | NQS-01 | PI15114 | Verified | Need general cleanup around Unit A Generator Circuit Breaker platform | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-04-14 | Chris Colvin | 2020-06-02 | Randy Carpenter
NQS-01 | NQS-01 | PI15115 | Verified | Unit A Generator Circuit Breaker actuator spring load and discharge sight glass is broken | C | E | Mike Tabbert | McD | 2020-01-02 | Mike Tabbert | Comm | 2020-03-31 | Mike Tabbert | 2020-06-02 | Randy Carpenter
NQS-01 | NQS-01 | PI15116 | Verified | Remove unsued chain falls from above Unit A Generator Circuit Breakers | C | E | Tim Gallegos | McD | 2020-01-02 | Tim Gallegos | Comm | 2020-04-23 | Tim Gallegos | 2020-06-02 | Randy Carpenter
NQS-01 | NQS-01 | PI15117 | Verified | Remove rope used for tying up cables underneath Unit A Generator Circuit Breakers, install permanent support | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-31 | Randy Carpenter
NQS-01 | NQS-01 | PI15118 | Verified | Unit A Generator Circuit Breaker platform grating needs toe plate underneath breakers | B | C | Bobby Williams | McD | 2020-01-02 | Bobby Williams | Comm | 2020-01-16 | Tim Gallegos | 2020-03-05 | Nelson Eichelberger
NQS-01 | NQS-01 | PI15119 | Verified | Unit A Generator Circuit Breaker support is missing bolt on north side | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-02-27 | Fred Michael
NQS-01 | NQS-01 | PI15120 | Verified | Clean off top of Unit A Generator Circuit Breaker covers | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-06-02 | Randy Carpenter
NQS-01 | NQS-01 | PI15121 | Verified | Unit A Isophase Bus Duct Voltage Transformer front cover has loose bolts | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-06-02 | Randy Carpenter
NQS-01 | NQS-01 | PI15122 | Verified | Remove extra ground cable from soutwest side of Unit A Aux Transformer | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-06-02 | Randy Carpenter
NQS-01 | NQS-01 | PI15123 | Verified | Install permanent support for Calibration Gas Bottle at Unit A Aux Transformer | C | E | Mike Tabbert | McD | 2020-01-02 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-07-10 | Nelson Eichelberger
NQS-01 | NQS-01 | PI15124 | Verified | Need general cleanup around Unit A Aux Transformer | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-05-13 | Randy Carpenter
NQS-01 | NQS-01 | PI15125 | Verified | Tighten loose bolts on Unit A Aux Transformer primary cover (cable termination enclosure) | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-06-02 | Randy Carpenter
NQS-01 | NQS-01 | PI17827 | Verified | 87GSUT-1A-2, 87UAT-1A-2, 87U-1A - Repair 'IRIG OK' (and any other) issues on all SEL-487E relays in the Main PDC. | C | E | Jonathan Donham | McD | 2020-03-16 | Jonathan Donham | Const | 2020-03-31 | Jonathan Donham | 2020-06-04 | Cintrel Spears
NQS-01 | NQS-01 | PI17833 | Verified | 1A-NQS-BKR-0001 - 125 volt power failure on 1A GCB | C | E | Jonathan Donham | McD | 2020-03-16 | Jonathan Donham | Const | 2020-03-17 | Jonathan Donham | 2020-06-03 | Chase Courtade
NQS-01 | NQS-01 | PI18016 | Verified | 1A-NQS-IPB-0001 - At St. Charles, there was a condensation issue in the generator isophase buses. It would be helpful if there was a common header connecting all three isophases with a drain valve in case condensation were to build up. At SCPS, they connected instrument air to the drains with a low pressure regulator to keep dry air in and to prevent condensation buildup. | D | E | Charles Worthington | McD | 2020-03-17 | Charles Worthington | Comm | 2020-04-28 | Michael Law | 2021-01-05 | Keith Pollock
NQS-01 | NQS-01 | PI18017 | Verified | 1B-NQS-IPB-0001 - At St. Charles, there was a condensation issue in the generator isophase buses. It would be helpful if there was a common header connecting all three isophases with a drain valve in case condensation were to build up. At SCPS, they connected instrument air to the drains with a low pressure regulator to keep dry air in and to prevent condensation buildup. | D | E | Charles Worthington | McD | 2020-03-17 | Charles Worthington | Comm | 2020-04-28 | Michael Law | 2021-01-05 | Keith Pollock
NQS-01 | NQS-01 | PI18165 | Verified | Calisto not operating properly Unit A Aux Transfromer | C | E | Mike Tabbert | McD | 2020-03-20 | Mike Tabbert | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
NQS-02 | NQS-02 | PI00485 | Verified | Seal all conduits. | B | E | Logan Holland | McD | 2019-04-05 | Logan Holland | Const | 2019-06-14 | Logan Holland | 2019-06-14 | Logan Holland
NQS-02 | NQS-02 | PI00486 | Verified | Missing 8 screws in bottom plate of 10-NOS-XFM-0001B. | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-08 | Shannon Savoy | 2019-04-08 | Mike Tabbert
NQS-02 | NQS-02 | PI00487 | Verified | Confirm GCB 1B-NQS-BKR-0001 grounding complete. | A | E | Luis Cantu | McD | 2019-04-05 | Luis Cantu | Const | 2019-04-11 | Shannon Savoy | 2019-06-14 | Mike Tabbert
NQS-02 | NQS-02 | PI00488 | Verified | Need grating and hand rail installed on Generator Circuit Breaker Platform Unit B. | A | S | Robert Risher | McD | 2019-04-05 | Robert Risher | Const | 2019-04-08 | Robert Risher | 2019-04-15 | Mike Tabbert
NQS-02 | NQS-02 | PI00489 | Verified | Wiring heaters (Conduit is installed) in the GSU 1B TO SOUTH FIRE WALL area | A | E | Sheri Fritz | NCC | 2019-04-05 | Sheri Fritz | Const | 2019-04-08 | Ayda Chaves | 2019-04-08 | Ayda Chaves
NQS-02 | NQS-02 | PI00490 | Verified | Wiring heaters and complete conduit for installation. in the NORTH FIRE WALL - GCB 1B South area | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-08 | Ayda Chaves | 2019-04-08 | Ayda Chaves
NQS-02 | NQS-02 | PI00491 | Verified | Need handrail installed on Generator Circuit Breaker Unit B | A | S | Robert Risher | McD | 2019-04-05 | Robert Risher | Const | 2019-04-08 | Mike Tabbert | 2019-04-08 | Mike Tabbert
NQS-02 | NQS-02 | PI00493 | Verified | 10-NOS-BD-0002B, Grout Bus Supports | C | C | Jessie Pipes | McD | 2019-04-05 | Jessie Pipes | Const | 2019-04-11 | Jessie Pipes | 2019-04-15 | Mike Tabbert
NQS-02 | NQS-02 | PI00494 | Verified | 10-NOS-BD-0001B, Grout Bus Supports. | C | C | Jessie Pipes | McD | 2019-04-05 | Jessie Pipes | Const | 2019-04-05 | Shannon Savoy | 2019-04-08 | Mike Tabbert
NQS-02 | NQS-02 | PI00495 | Verified | 10-NOS-CAB-0001B, Door keeper on right side missing bolt | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-08 | Shannon Savoy | 2019-04-08 | Mike Tabbert
NQS-02 | NQS-02 | PI00496 | Verified | 10-NOS-CAB-0001B, Wire numbers 1BNOSC0002-2 and 2-1 not landed. | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-05 | Shannon Savoy | 2019-04-08 | Mike Tabbert
NQS-02 | NQS-02 | PI00497 | Verified | 1B-NOS-BKR-0001, Complete cable tray and conduit to Generator Circuit Breaker. (Cable Tray Labels, Grounding Cable Tray) | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-17 | Mike Tabbert | 2019-04-17 | Mike Tabbert
NQS-02 | NQS-02 | PI00498 | Verified | 1B-NOS-BKR-0001, Grout Cable Tray supports. | C | C | Jessie Pipes | McD | 2019-04-05 | Jessie Pipes | Const | 2019-04-08 | Jessie Pipes | 2019-04-10 | Neil Simon
NQS-02 | NQS-02 | PI00499 | Verified | 1BNQSK0004, Pull and Terminate Cable. | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-09 | Shannon Savoy | 2019-04-09 | Mike Tabbert
NQS-02 | NQS-02 | PI00500 | Verified | 1BNQSK0005, Pull and Terminate Cable. | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-05 | Shannon Savoy | 2019-04-05 | Mike Tabbert
NQS-02 | NQS-02 | PI00501 | Verified | 1BNQSK0006, Pull and Terminate Cable. | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-05 | Shannon Savoy | 2019-04-05 | Mike Tabbert
NQS-02 | NQS-02 | PI00502 | Verified | 1BNQSK0007, Pull and Terminate Cable. | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-05 | Shannon Savoy | 2019-04-08 | Mike Tabbert
NQS-02 | NQS-02 | PI00503 | Verified | Bolts missing at 1st support on C phase IPB saddle South of Blast walls. | A | S | Sheri Fritz | NCC | 2019-04-05 | Sheri Fritz | Const | 2019-04-05 | Jason Marshik | 2019-04-10 | Neil Simon
NQS-02 | NQS-02 | PI00504 | Verified | Paint over arc strike at West horizontal support at top of Blast Wall. | A | S | Robert Risher | McD | 2019-04-05 | Robert Risher | Const | 2019-04-12 | Neil Simon | 2019-04-12 | Neil Simon
NQS-02 | NQS-02 | PI00505 | Verified | Bolts missing at 1st support on A phase IPB saddle North of Blast walls. | A | S | Sheri Fritz | NCC | 2019-04-05 | Sheri Fritz | Const | 2019-04-05 | Jason Marshik | 2019-04-10 | Neil Simon
NQS-02 | NQS-02 | PI00506 | Verified | Remove wires and exposed rebar chairs and rub down side of foundation at SFC Transformer foundation. | A | C | Jessie Pipes | McD | 2019-04-05 | Jessie Pipes | Const | 2019-04-08 | Jessie Pipes | 2019-04-16 | Neil Simon
NQS-02 | NQS-02 | PI00508 | Verified | Grout column bases at SFC Transformer | A | C | Jessie Pipes | McD | 2019-04-05 | Jessie Pipes | Const | 2019-04-11 | Jessie Pipes | 2019-04-12 | Neil Simon
NQS-02 | NQS-02 | PI00509 | Verified | Remove exposed rebar chairs and rub down side of foundation at IPB support foundation. | A | C | Jessie Pipes | McD | 2019-04-05 | Jessie Pipes | Const | 2019-04-08 | Jessie Pipes | 2019-04-12 | Neil Simon
NQS-02 | NQS-02 | PI00510 | Verified | Caulk expansion joint between IPB support foundation and SFC foundation. | A | C | Jessie Pipes | McD | 2019-04-05 | Jessie Pipes | Const | 2019-04-11 | Jessie Pipes | 2019-04-12 | Neil Simon
NQS-02 | NQS-02 | PI00511 | Verified | Loose Bolts at Kicker west side of IPB support structure | A | S | Sheri Fritz | NCC | 2019-04-05 | Sheri Fritz | Const | 2019-04-05 | Jason Marshik | 2019-04-12 | Neil Simon
NQS-02 | NQS-02 | PI00512 | Verified | Missing Bolts in X bracing at IPB support North of Blast walls both horizontal and vertical bracing. | A | S | Sheri Fritz | NCC | 2019-04-05 | Sheri Fritz | Const | 2019-04-05 | Jason Marshik | 2019-04-16 | Neil Simon
NQS-02 | NQS-02 | PI00513 | Verified | remove wires and Guard rail from around Excitation transformer foundation and rub down sides. | A | C | Jessie Pipes | McD | 2019-04-05 | Jessie Pipes | Const | 2019-04-08 | Jessie Pipes | 2019-04-12 | Neil Simon
NQS-02 | NQS-02 | PI00515 | Verified | Caulk all expansion joints at Excitation Transformer | A | C | Jessie Pipes | McD | 2019-04-05 | Jessie Pipes | Const | 2019-04-11 | Jessie Pipes | 2019-04-12 | Neil Simon
NQS-02 | NQS-02 | PI00516 | Verified | Extend Grade Beam up to elevation 500' between column pad X2- XA and GT foundation. | A | C | Jessie Pipes | McD | 2019-04-05 | Jessie Pipes | Const | 2019-04-11 | Jessie Pipes | 2019-04-12 | Neil Simon
NQS-02 | NQS-02 | PI00517 | Verified | Install Handrail at IPB Platform. | A | S | Robert Risher | McD | 2019-04-05 | Robert Risher | Const | 2019-04-12 | Robert Risher | 2019-04-16 | Neil Simon
NQS-02 | NQS-02 | PI00533 | Verified | Provide all test reports needed for subsystem turnover. | B | E | Sheri Fritz | NCC | 2019-04-10 | Sheri Fritz | Const | 2019-07-24 | Ed Gober | 2019-07-24 | Ed Gober
NQS-02 | NQS-02 | PI00629 | Verified | Verify braid installation. | A | E | Sheri Fritz | NCC | 2019-04-15 | Sheri Fritz | Const | 2019-04-17 | Mike Tabbert | 2019-04-17 | Mike Tabbert
NQS-02 | NQS-02 | PI00630 | Verified | Perform enclosure isolation check. | A | E | Luis Cantu | NCC | 2019-04-15 | Luis Cantu | Const | 2019-04-30 | Shannon Savoy | 2019-06-14 | Mike Tabbert
NQS-02 | NQS-02 | PI00637 | Verified | Replace GCB 1B Cover. | C | E | Chris Colvin | McD | 2019-04-17 | Chris Colvin | Const | 2020-01-14 | Mike Tabbert | 2020-01-14 | Mike Tabbert
NQS-02 | NQS-02 | PI15040 | Verified | Clean up inside 1B-NQS-PNL-1000A, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-02-27 | Fred Michael
NQS-02 | NQS-02 | PI15041 | Verified | Seal cable floor penetrations inside 1B-NQS-PNL-1000A, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-02-27 | Fred Michael
NQS-02 | NQS-02 | PI15042 | Verified | Replace wiring duct covers inside 1B-NQS-PNL-1000A , Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-02-27 | Fred Michael
NQS-02 | NQS-02 | PI15043 | Verified | Heat shrink cable/wire tags inside 1B-NQS-PNL-1000A, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NQS-02 | NQS-02 | PI15044 | Verified | Replace cable tags that are too big to heat shrink inside 1B-NQS-PNL-1000A , Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NQS-02 | NQS-02 | PI15045 | Verified | Need phenolic label for tag no. 1B-NQS-PNL-1000A (backside), Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-27 | Fred Michael
NQS-02 | NQS-02 | PI15046 | Verified | Clean up inside 1B-NQS-PNL-1000B, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NQS-02 | NQS-02 | PI15047 | Verified | Seal cable floor penetrations inside 1B-NQS-PNL-1000B, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-04-07 | Bernard Stasse
NQS-02 | NQS-02 | PI15048 | Verified | Replace wiring duct covers inside 1B-NQS-PNL-1000B , Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NQS-02 | NQS-02 | PI15049 | Verified | Heat shrink cable/wire tags inside 1B-NQS-PNL-1000B, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NQS-02 | NQS-02 | PI15050 | Verified | Replace cable tags that are too big to heat shrink inside 1B-NQS-PNL-1000B , Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NQS-02 | NQS-02 | PI15051 | Verified | Need phenolic label for tag no. 1B-NQS-PNL-1000B (backside), Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-10 | Frank Lopez | 2020-04-07 | Bernard Stasse
NQS-02 | NQS-02 | PI15052 | Verified | Cables not terminated, verify and identify as spares or terminate at 1B-NQS-PNL-1000B, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
NQS-02 | NQS-02 | PI15053 | Verified | Two factory ground cables disconnected from relay at 1B-NQS-PNL-1000B, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-26 | Chris Colvin | 2020-04-07 | Bernard Stasse
NQS-02 | NQS-02 | PI15126 | Verified | NQS-02 boundary scoping is currently incorrect, revise drawings to identify correct boundaries | B | E | Eric Policarpio | McD | 2020-01-02 | Eric Policarpio | Comm | 2020-01-13 | Eric Policarpio | 2020-03-31 | Randy Carpenter
NQS-02 | NQS-02 | PI15127 | Verified | NQS-02 cable list is incorrect, should be total of 133 cables, revise cable list as necessary | B | E | Eric Policarpio | McD | 2020-01-02 | Eric Policarpio | Comm | 2020-01-13 | Eric Policarpio | 2020-03-31 | Randy Carpenter
NQS-02 | NQS-02 | PI15128 | Verified | Touch up paint on Unit B Generator Circuit Breaker Control Panel; 1B-NQS-BKR-0001 | C | X | Jerry Smith | McD | 2020-01-02 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-06-02 | Randy Carpenter
NQS-02 | NQS-02 | PI15129 | Verified | Missing bolt at Unit B Isophase connection to Generator Circuit Breaker | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2020-06-02 | Randy Carpenter
NQS-02 | NQS-02 | PI15130 | Verified | Need general cleanup around Unit B Generator Circuit Breaker platform | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-06-02 | Randy Carpenter
NQS-02 | NQS-02 | PI15131 | Verified | Unit B Generator Circuit Breaker actuator spring load and discharge sight glass is broken | C | E | Mike Tabbert | McD | 2020-01-02 | Mike Tabbert | Comm | 2020-05-15 | Mike Tabbert | 2020-06-02 | Randy Carpenter
NQS-02 | NQS-02 | PI15132 | Verified | Unit B Generator Circuit Breaker covers have missing and loose bolts | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-06-02 | Randy Carpenter
NQS-02 | NQS-02 | PI15133 | Verified | Clean off top of Unit B Generator Circuit Breaker covers | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-06-02 | Randy Carpenter
NQS-02 | NQS-02 | PI15134 | Verified | Cables under Unit B Generator Circuit Breaker Control Panel; 1B-NQS-BKR-0001 need support | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-04-08 | Chris Colvin | 2020-06-02 | Randy Carpenter
NQS-02 | NQS-02 | PI15135 | Verified | Remove blue tarp from behind Unit B Generator Circuit Breaker Control Panel; 1B-NQS-BKR-0001 | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-04-14 | Chris Colvin | 2020-06-02 | Randy Carpenter
NQS-02 | NQS-02 | PI15136 | Verified | Tighten loose bolts on Unit B Generator Circuit Breaker Control Panel; 1B-NQS-BKR-0001 mounting frame | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2020-06-02 | Randy Carpenter
NQS-02 | NQS-02 | PI15137 | Verified | Unit B Isophase Bus Duct heater flex connections are broken | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-02-26 | Randy Carpenter
NQS-02 | NQS-02 | PI15138 | Verified | Covers on Unit B Isophase Bus Duct heater conduit covers not installed | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2020-06-02 | Randy Carpenter
NQS-02 | NQS-02 | PI15139 | Verified | Install permanent support for Calibration Gas Bottle at Unit B Aux Transformer | C | P | Tim Green | McD | 2020-01-02 | Tim Green | Comm | 2020-05-29 | James Beech | 2021-01-05 | Keith Pollock
NQS-02 | NQS-02 | PI15140 | Verified | Need general cleanup around Unit B Aux Transformer | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2020-05-13 | Randy Carpenter
NQS-02 | NQS-02 | PI15141 | Verified | Install hold down anchor for grounding cable at Unit B Aux Transformer southwest side | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
NQS-02 | NQS-02 | PI15142 | Verified | Tighten loose bolts on Unit B Aux Transformer primary cover (cable termination enclosure) | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-31 | Chris Colvin | 2021-01-05 | Keith Pollock
NQS-02 | NQS-02 | PI15569 | Verified | 1B-NQS-IPB-0001 - Broken conduit connection and exposed wire | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-04-06 | Michael Law | 2020-04-07 | Bernard Stasse
NQS-02 | NQS-02 | PI15570 | Verified | 1B-NQS-BKR-0001 - There are several loose bolts (more than ten (10) all around on all three (3) hoods) and several missing bolts (approximately four (4)). This needs to be fixed before the unit goes online. | C | E | Jonathan Donham | McD | 2020-01-08 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2020-04-07 | Bernard Stasse
NQS-02 | NQS-02 | PI17675 | Verified | 10-NOS-XFM-0001B - The dynamic ratings HMI screen is showing lines and not displaying anything. | C | E | Jonathan Donham | ABB | 2020-03-04 | Jonathan Donham | Comm | 2020-05-12 | Mike Tabbert | 2020-05-12 | Randy Carpenter
NQS-02 | NQS-02 | PI17828 | Verified | 87GSUT-1B-2, 87UAT-1B-2, 87U-1B - Repair 'IRIG OK' (and any other) issues on all SEL-487E relays in the Main PDC. | C | E | Jonathan Donham | McD | 2020-03-16 | Jonathan Donham | Const | 2020-03-31 | Jonathan Donham | 2020-06-04 | Cintrel Spears
NQS-02 | NQS-02 | PI17834 | Verified | 1B-NQS-BKR-0001 - 125 volt power failure on 1B GCB | C | E | Jonathan Donham | McD | 2020-03-16 | Jonathan Donham | Const | 2020-03-17 | Jonathan Donham | 2020-06-03 | Chase Courtade
NQS-02 | NQS-02 | PI18013 | Open | 1B-NQS-GSUT-0001 - Lumasmart winding/oil temp monitor is not communicating with the dynamic ratings monitor. It's causing nuisance alarms. | C | E | Mike Tabbert | McD | 2020-03-17 | Mike Tabbert | Comm
NQS-02 | NQS-02 | PI18026 | Verified | 1B-NQS-GSUT-0001 - There's a small amount of oil leaking from the top of 1B GSU. Signs of the oil leak can be seen on the plant southwest corner of the GSU. | C | E | Jonathan Donham | McD | 2020-03-17 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2021-05-27 | John Watts
NQS-02 | NQS-02 | PI18166 | Verified | Calisto not operating properly Unit B Aux Transfromer | C | E | Jonathan Donham | McD | 2020-03-20 | Jonathan Donham | Const | 2020-05-28 | Jonathan Donham | 2021-05-06 | ABB
OWS-01 | OWS-01 | PI01537 | Verified | Ground the Oil/Water Separator 10-OWS-OWS-0010. | A | E | Luis Cantu | McD | 2019-06-21 | Luis Cantu | Const | 2019-07-23 | Mike Tabbert | 2019-07-23 | Mike Tabbert
OWS-01 | OWS-01 | PI01538 | Verified | There is a hand clearance issue on the Oil/Water Separator ladder. Ladder offset distance from platform/handrail does not meet OSHA requirements. Resulting in hand grab between ladder rail and handrail. 7" min clearance required | C | S | Bobby Williams | McD | 2019-06-21 | Bobby Williams | Const | 2020-03-16 | Tim Gallegos | 2020-04-07 | Bernard Stasse
OWS-01 | OWS-01 | PI01539 | Verified | Perform clean & close on 10-OWS-OWS-0010, 10-OWS-SUMP-0001 & 0002, 1A/B/C-OWS-SUMP-0001. | A | P | Damon Turner | McD | 2019-06-21 | Damon Turner | Const | 2019-07-24 | Damon Turner | 2019-07-24 | Joshua Sturgeon
OWS-01 | OWS-01 | PI01540 | Verified | Tag all valves. | C | P | Kelvin Cook | McD | 2019-06-21 | Kelvin Cook | Const |  |  | 2020-02-07 | Kelvin Cook
OWS-01 | OWS-01 | PI01541 | Verified | Confirm 7" HG vacuum on the Oil/Water Separator. | A | M | Shane Crowe | McD | 2019-06-21 | Shane Crowe | Const | 2019-07-18 | Joshua Sturgeon | 2019-07-19 | Shannon Scott
OWS-01 | OWS-01 | PI01542 | Verified | Tubing tray at 1C-OWS-SUMP-0001 interferes with piping flange - northeast corner of STG bldg. | A | I | Gonzalo Pena | McD | 2019-06-21 | Gonzalo Pena | Const | 2019-06-22 | Gonzalo Pena | 2019-08-06 | Billy Williams
OWS-01 | OWS-01 | PI01657 | Verified | Valve not lockable. 2" valve (PS International) 10-OWS-V-0010 | D | P | Michael Law | McD | 2019-06-27 | Michael Law | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
OWS-01 | OWS-01 | PI01658 | Verified | Valve not lockable. 2" valve (PS International) 10-OWS-V-0011 | D | P | Michael Law | McD | 2019-06-27 | Michael Law | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
OWS-01 | OWS-01 | PI01659 | Verified | Valve not lockable. 2" valve (PS International) 10-OWS-V-0012 | D | P | Michael Law | McD | 2019-06-27 | Michael Law | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
OWS-01 | OWS-01 | PI01660 | Verified | Toe plate required around deck penetrations (both access manways). Platform above tank | C | P | Bobby Williams | McD | 2019-06-27 | Bobby Williams | Const | 2020-01-25 | Tim Gallegos | 2020-02-10 | Nelson Eichelberger
OWS-01 | OWS-01 | PI01661 | Verified | PIDs - 10-OWS-V-0005. Vendor Valve # does not Match CBI Valve # on PID (vendor vs. CBI) at TP-006 | C | P | Tim Green | McD | 2019-06-27 | Tim Green | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
OWS-01 | OWS-01 | PI02129 | Verified | 10OWSC0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-15 | Luis Cantu | 2019-07-22 | Mike Tabbert
OWS-01 | OWS-01 | PI02130 | Verified | 10OWSC0002, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-15 | Luis Cantu | 2019-07-22 | Mike Tabbert
OWS-01 | OWS-01 | PI02131 | Verified | 10OWSC0003, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-15 | Luis Cantu | 2019-07-22 | Mike Tabbert
OWS-01 | OWS-01 | PI02132 | Verified | 10OWSC0004, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
OWS-01 | OWS-01 | PI02133 | Verified | 10OWSC0005, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
OWS-01 | OWS-01 | PI02134 | Verified | 10OWSC0006, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
OWS-01 | OWS-01 | PI02135 | Verified | 10OWSC0007, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
OWS-01 | OWS-01 | PI02136 | Verified | 10OWSC0008, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-15 | Luis Cantu | 2019-07-22 | Mike Tabbert
OWS-01 | OWS-01 | PI02137 | Verified | 10OWSC0009, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
OWS-01 | OWS-01 | PI02138 | Verified | 10OWSK0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
OWS-01 | OWS-01 | PI02139 | Verified | 10OWSK0002, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
OWS-01 | OWS-01 | PI02140 | Verified | 10OWSK0003, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-15 | Luis Cantu | 2019-07-22 | Mike Tabbert
OWS-01 | OWS-01 | PI02141 | Verified | 10-OWS-LAH-0010, Not installed | A | I | Mike Tabbert | McD | 2019-07-03 | Mike Tabbert | Const | 2019-07-22 | Mike Tabbert | 2019-07-22 | Mike Tabbert
OWS-01 | OWS-01 | PI02142 | Verified | 10-OWS-LAH-0011, Not Installed | A | I | Gonzalo Pena | McD | 2019-07-03 | Gonzalo Pena | Const | 2019-07-19 | Gonzalo Pena | 2019-07-22 | Mike Tabbert
OWS-01 | OWS-01 | PI02143 | Verified | 1C-OWS-LE-0001, Not Installed | A | I | Gonzalo Pena | McD | 2019-07-03 | Gonzalo Pena | Const | 2019-07-19 | Gonzalo Pena | 2019-07-22 | Mike Tabbert
OWS-01 | OWS-01 | PI02144 | Verified | Install all conduit for electrical devises and instruments | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-16 | Ken Mundy | 2019-07-22 | Mike Tabbert
OWS-01 | OWS-01 | PI02145 | Verified | 1AOWSC0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
OWS-01 | OWS-01 | PI02146 | Verified | 1AOWSC0002, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
OWS-01 | OWS-01 | PI02147 | Verified | 1AOWSC0003, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
OWS-01 | OWS-01 | PI02148 | Verified | 1AOWSK0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
OWS-01 | OWS-01 | PI02149 | Verified | 1BOWSC0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
OWS-01 | OWS-01 | PI02150 | Verified | 1BOWSC0002, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
OWS-01 | OWS-01 | PI02151 | Verified | 1BOWSC0003, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
OWS-01 | OWS-01 | PI02152 | Verified | 1BOWSK0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
OWS-01 | OWS-01 | PI02153 | Verified | 1COWSC0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
OWS-01 | OWS-01 | PI02154 | Verified | 1COWSC0002, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
OWS-01 | OWS-01 | PI02155 | Verified | 1COWSC0003, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-15 | Luis Cantu | 2019-07-22 | Terry Deaton
OWS-01 | OWS-01 | PI02156 | Verified | 1COWSK0001, Pull and Terminate Cable | A | I | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-15 | Luis Cantu | 2019-07-22 | Mike Tabbert
OWS-01 | OWS-01 | PI02157 | Verified | Oily water Sump Pump 1A-OWS-P-0001 Air Regulator 1A-OWS-PVC-0001 needs instrument air tied in | A | I | Gonzalo Pena | McD | 2019-07-03 | Gonzalo Pena | Const | 2019-07-10 | Gonzalo Pena | 2019-07-19 | Joshua Sturgeon
OWS-01 | OWS-01 | PI02158 | Verified | Oily water Sump Pump 1B-OWS-P-0001 Air Regulator 1B-OWS-PVC-0001 needs instrument air tied in | A | I | Gonzalo Pena | McD | 2019-07-03 | Gonzalo Pena | Const | 2019-07-10 | Gonzalo Pena | 2019-07-19 | Joshua Sturgeon
OWS-01 | OWS-01 | PI02159 | Verified | Oily water Sump Pump 1C-OWS-P-0001 Air Regulator 1C-OWS-PVC-0001 needs instrument air tied in | A | I | Gonzalo Pena | McD | 2019-07-03 | Gonzalo Pena | Const | 2019-07-10 | Gonzalo Pena | 2019-07-19 | Joshua Sturgeon
OWS-01 | OWS-01 | PI02160 | Verified | Oily water Sump Pump 10-OWS-P-0001 Air Regulator 10-OWS-PVC-0001 needs instrument air tied in | A | I | Gonzalo Pena | McD | 2019-07-03 | Gonzalo Pena | Const | 2019-07-10 | Gonzalo Pena | 2019-07-19 | Joshua Sturgeon
OWS-01 | OWS-01 | PI02161 | Verified | Oily water Sump Pump 10-OWS-P-0002 Air Regulator 10-OWS-PVC-0002 needs instrument air tied in | B | I | Gonzalo Pena | McD | 2019-07-03 | Gonzalo Pena | Const | 2019-08-06 | Gonzalo Pena | 2019-10-04 | Joshua Sturgeon
OWS-01 | OWS-01 | PI02162 | Verified | Oily Water Seperator 10-OS-OWS-0010 needs to be grouted | A | C | Johnny Campbell | McD | 2019-07-03 | Johnny Campbell | Const | 2019-07-22 | Johnny Campbell | 2019-07-22 | Joshua Sturgeon
OWS-01 | OWS-01 | PI02163 | Verified | Ground Oily Water Seperator Tank | A | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-26 | Logan Holland
OWS-01 | OWS-01 | PI02164 | Verified | Condulet cover under 10-CWS-LC-0001 | B | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-23 | Mike Tabbert | 2019-07-23 | Mike Tabbert
OWS-01 | OWS-01 | PI02165 | Verified | Tag on 10-CWS-LC-0001 | C | E | Dustin Futrell | McD | 2019-07-03 | Dustin Futrell | Const | 2019-07-30 | Luis Cantu | 2019-08-07 | Mike Tabbert
OWS-01 | OWS-01 | PI02166 | Verified | Low point drains on conduit in Demin Building | B | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-23 | Mike Tabbert
OWS-01 | OWS-01 | PI02167 | Verified | Permanent suction plug in 1C-OWS-LC-0001 | A | I | Gonzalo Pena | McD | 2019-07-03 | Gonzalo Pena | Const | 2019-07-23 | Gonzalo Pena | 2019-07-26 | C_AC03
OWS-01 | OWS-01 | PI02168 | Verified | Tag on 1C-CWS-LE-0001 | C | E | Dustin Futrell | McD | 2019-07-03 | Dustin Futrell | Const | 2019-07-30 | Luis Cantu | 2019-08-07 | Mike Tabbert
OWS-01 | OWS-01 | PI02169 | Verified | Low point drain on conduit by 1C-OWS-LE-0001 | B | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-23 | Mike Tabbert
OWS-01 | OWS-01 | PI02170 | Verified | Tag on 1A-OWS-LC-0001 | C | E | Dustin Futrell | McD | 2019-07-03 | Dustin Futrell | Const | 2019-07-30 | Luis Cantu | 2019-08-07 | Mike Tabbert
OWS-01 | OWS-01 | PI02171 | Verified | Low point drain on conduit by 1B Level Indicator | B | E | Luis Cantu | McD | 2019-07-03 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-23 | Mike Tabbert
OWS-01 | OWS-01 | PI02172 | Verified | Suction plug on 1B-OWS-LC-0001 | A | I | Gonzalo Pena | McD | 2019-07-03 | Gonzalo Pena | Const | 2019-07-23 | Gonzalo Pena | 2019-07-26 | C_AC03
OWS-01 | OWS-01 | PI02173 | Verified | Missing RESET button cover on 10-OWS-LC-0002 | B | E | Mike Tabbert | McD | 2019-07-03 | Mike Tabbert | Const | 2019-08-14 | Mike Tabbert | 2019-08-26 | Albert Burge
OWS-01 | OWS-01 | PI02174 | Verified | Tie in Instrument Air for pump | A | P | Damon Turner | McD | 2019-07-03 | Damon Turner | Const | 2019-07-19 | Gonzalo Pena | 2019-07-19 | Gonzalo Pena
OWS-01 | OWS-01 | PI02175 | Verified | Instrument Air Header for 10-OWS-P-0002 | A | P | Terry Deaton | McD | 2019-07-03 | Terry Deaton | Const | 2019-07-19 | Gonzalo Pena | 2019-07-19 | Gonzalo Pena
OWS-01 | OWS-01 | PI02256 | Verified | 1-10-OWS-0010-151X1-FP-2.0-ET - Sample Point (tap from 8inch outfall) - Unlikely a required sample can be drawn from the design location. Relocate sample point piping to underside of 8inch outfall piping from OWS vessel. (155126-LK-10-OWS-ME-PID-0002). | D | P | Michael Law | McD | 2019-07-10 | Michael Law | Const | 2019-07-30 | Michael Law | 2019-08-06 | Dave Goldak
OWS-01 | OWS-01 | PI14557 | Verified | Tag all system components with permanent tags, including vendor supplied equipment | C | P | Kelvin Cook | McD | 2019-12-07 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2021-01-15 | Dave Goldak
OWS-01 | OWS-01 | PI14558 | Verified | Instrument Air Pressure Regulator not installed at 1A CTG Oily Water Sump | B | I | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Comm | 2020-02-11 | Gonzalo Pena | 2020-02-24 | Keith Pollock
OWS-01 | OWS-01 | PI14559 | Verified | 1A-OWS-FY-0001; Flow Solenoid Valve not installed at 1A CTG Oily Water Sump | B | I | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Comm | 2020-02-11 | Gonzalo Pena | 2020-02-24 | Keith Pollock
OWS-01 | OWS-01 | PI14560 | Verified | Touch-up paint all system piping where necessary | C | X | Jerry Smith | McD | 2019-12-07 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
OWS-01 | OWS-01 | PI14561 | Verified | Remove pipe wrench marks from 1A CTG Oily Water Sump Pump discharge and paint | C | X | Jerry Smith | McD | 2019-12-07 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
OWS-01 | OWS-01 | PI14562 | Verified | Remove tape, wire, rope, old tags, and tie wraps from all system piping and components | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-04-28 | Michael Law | 2020-06-16 | Dave Goldak
OWS-01 | OWS-01 | PI14563 | Verified | Rework fish mouthed flange at 1B CTG Oily Water Sump Pump discharge (flex to hard pipe flange) | C | P | Kelvin Cook | McD | 2019-12-07 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-03-12 | John Watts
OWS-01 | OWS-01 | PI14564 | Verified | Remove rust and cold gal rusted pipe supports at 1B CTG Oily Water Sump discharge | C | X | Jerry Smith | McD | 2019-12-07 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
OWS-01 | OWS-01 | PI14565 | Verified | Finish painting 1B CTG Oily Water Sump Pump discharge piping | C | X | Jerry Smith | McD | 2019-12-07 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
OWS-01 | OWS-01 | PI14566 | Verified | Back fill around 1B CTG Oily Water Sump Pump discharge to underground | C | C | Alan Huntsman | McD | 2019-12-07 | Alan Huntsman | Comm | 2020-01-20 | Alan Huntsman | 2020-01-23 | Shannon Scott
OWS-01 | OWS-01 | PI14567 | Verified | Clean and close verification of all sumps required, to be verified by Entergy - Form M06C Clean and Close was signed by Blake B. on 7/2 | D | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
OWS-01 | OWS-01 | PI14568 | Verified | 1B CTG Oily Water Sump cover plates do not match up, large gaps between plates | C | P | Shane Crowe | McD | 2019-12-07 | Shane Crowe | Comm | 2020-01-24 | Shane Crowe | 2020-02-11 | Dave Goldak
OWS-01 | OWS-01 | PI14569 | Verified | Instrument Air Pressure Regulator not installed at 1C CTG Oily Water Sump | B | I | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Comm | 2020-02-11 | Gonzalo Pena | 2020-02-24 | Keith Pollock
OWS-01 | OWS-01 | PI14570 | Verified | 1C-OWS-FY-0001; Flow Solenoid Valve not installed at 1C STG Oily Water Sump | B | I | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Comm | 2020-02-11 | Gonzalo Pena | 2020-02-24 | Keith Pollock
OWS-01 | OWS-01 | PI14571 | Verified | West side diaphragm has small leak at 1C STG Oily Water Sump Pump | B | M | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Comm | 2020-03-07 | Tim Green | 2020-11-11 | Dave Goldak
OWS-01 | OWS-01 | PI14572 | Verified | 1C STG Oily Water Sump system and valves not installed per ISO. Piping and location of supports to be verified by Engineering, see LK-1C-OWS-PD-P40-0011 (extensive vibration of piping while pump is running) | C | P | Tim Green | McD | 2019-12-07 | Tim Green | Comm | 2020-06-30 | Mike Tabbert | 2020-11-11 | Dave Goldak
OWS-01 | OWS-01 | PI14573 | Verified | Missing top to Instrumenht Air Pressure Regulator at 1C STG Oily Water Sump | B | I | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Comm | 2020-02-13 | James Tanner | 2020-02-26 | Keith Pollock
OWS-01 | OWS-01 | PI14574 | Verified | Grout 1C STG Oily Water Sump conduit supports | C | C | Johnny Campbell | McD | 2019-12-07 | Johnny Campbell | Comm |  |  | 2019-12-14 | Jack White
OWS-01 | OWS-01 | PI14575 | Verified | Condolets missing at at 1C STG Oily Water Sump Pump Control Panel | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-03-04 | Dave Goldak
OWS-01 | OWS-01 | PI14576 | Verified | 1C STG Oily Water Sump Pump missing ground cable | D | E | Michael Law | McD | 2019-12-07 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
OWS-01 | OWS-01 | PI14577 | Verified | IA tubing to Pressure Regulator and 10-CWS-FY-0001; Flow Solenoid valve is plastic, spec call for SS | C | I | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Comm | 2020-01-31 | Gonzalo Pena | 2020-02-12 | Dave Goldak
OWS-01 | OWS-01 | PI14578 | Verified | Replace broken Instrument Air Pressure Regulator at Raw Water Treatment Area Oily Water Sump | B | I | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Comm | 2020-02-11 | Gonzalo Pena | 2020-02-24 | Keith Pollock
OWS-01 | OWS-01 | PI14579 | Verified | Back fill around Raw Water Treatment Area Oily Water Sump Pump discharge piping to underground | C | C | Alan Huntsman | McD | 2019-12-07 | Alan Huntsman | Comm | 2020-01-20 | Alan Huntsman | 2020-01-23 | Shannon Scott
OWS-01 | OWS-01 | PI14580 | Verified | Oil/Water Separator has Vacuum Truck Connection at both ends and N side, Redline P&ID to indicate all three connections | C | P | Mike Tabbert | McD | 2019-12-07 | Mike Tabbert | Comm | 2020-06-18 | Mike Tabbert | 2020-06-22 | Dave Goldak
OWS-01 | OWS-01 | PI14581 | Verified | Remove rust and paint all three Vacuum Truck Connection extensions at OWS vessel | C | X | Jerry Smith | McD | 2019-12-07 | Jerry Smith | Comm | 2020-02-20 | Alan Huntsman | 2020-03-04 | Dave Goldak
OWS-01 | OWS-01 | PI14583 | Verified | Verify support locations at discharge and penetration through Demin Water Building, pipe seems loose | C | P | Kelvin Cook | McD | 2019-12-07 | Kelvin Cook | Comm |  |  | 2020-01-10 | Michael Law
PCS-01 | PCS-01 | PI17363 | Verified | Seal conduits in panel - south side of cooling tower. | C | E | Chris Colvin | McD | 2020-02-28 | Chris Colvin | Const | 2020-04-29 | Matt Gilmore | 2020-04-30 | Mike Tabbert
RWS-01 | RWS-01 | PI02471 | Verified | LK-10-RWS-P40-0090-01 Need welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-08-03 | Terry Deaton | 2019-08-03 | Tom Noble
RWS-01 | RWS-01 | PI04551 | Verified | ISO 10-RWS-PD-P40-0010-05 is not installed | B | P | Terry Deaton | McD | 2019-08-21 | Terry Deaton | Const | 2019-08-27 | Terry Deaton | 2019-08-27 | Kelvin Cook
RWS-01 | RWS-01 | PI04552 | Verified | On ISO 10-RWS-PD-P40-0090-01 pipe support 10-RWS-PD-HGR-0033 is not installed | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-05 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04553 | Verified | On ISO 10-RWS-PD-P40-0090-01 specialty item 10-RWS-QUIL-0090 is not installed | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-09-09 | Gonzalo Pena | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04554 | Verified | On ISO 10-RWS-PD-P40-0090-01 cold galve all supports | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const |  |  | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04555 | Verified | On ISO 10-RWS-PD-P40-0090-01 spool 0090-1 flange connecting to 10-RWS-MXR-0090 has loose bolts | A | P | Terry Deaton | McD | 2019-08-21 | Terry Deaton | Const | 2019-08-27 | Terry Deaton | 2019-08-27 | Kelvin Cook
RWS-01 | RWS-01 | PI04556 | Verified | On ISO 10-RWS-PD-P40-0098-01 is not installed | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-11 | Damon Turner | 2019-09-12 | Kelvin Cook
RWS-01 | RWS-01 | PI04557 | Verified | On ISO 10-RWS-PD-P41-0007-01 is not installed | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-11 | Damon Turner | 2019-09-12 | Kelvin Cook
RWS-01 | RWS-01 | PI04558 | Verified | On ISO 10-RWS-PD-P41-0008-01 is not installed | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-12 | Kelvin Cook
RWS-01 | RWS-01 | PI04559 | Verified | On ISO 10-RWS-PD-P41-0095-01 pipe support 10-RWS-PD-HGR-0056 remove 2nd set of nuts. Install per iso | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04560 | Verified | On ISO 10-RWS-PD-P41-0095-01 flanges connecting to 10-RWS-FXH-0095 bolts are to short by 3/4" and missing gasket. | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04561 | Verified | On ISO 10-RWS-PD-P41-0097-01 is not installed | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-12 | Kelvin Cook
RWS-01 | RWS-01 | PI04562 | Verified | On ISO 10-RWS-PD-P41-0200-01 pipe support 10-RWS-PD-HGR-0080 is not installed | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04563 | Verified | On ISO 10-RWS-PD-P41-0200-01 flange connecting to valve 10-RWS-V-0122 need bolts to be even up | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-10-03 | Kelvin Cook
RWS-01 | RWS-01 | PI04564 | Verified | On ISO 10-RWS-PD-P41-0200-02 pipe support 10-RWS-PD-HGR-0073 nuts at top and bottom of anchor | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04565 | Verified | On ISO 10-RWS-PD-P41-0200-03 pipe support 10-RWS-PD-HGR-0071 & 0072 missing ubolt | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04566 | Verified | On ISO 10-RWS-PD-P41-0200-03 pipe support 10-RWS-PD-HGR-0068 need anchor ubolt | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-10-03 | Kelvin Cook
RWS-01 | RWS-01 | PI04567 | Verified | On ISO 10-RWS-PD-P41-0200-03 flange connection to 10-RWS-SKD-0200/x2 need anti seige bolts | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04568 | Verified | On ISO 10-RWS-PD-P41-0201-01 pipe support 10-RWS-PD-HGR-0067 has loose ubolt | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04569 | Verified | On ISO 10-RWS-PD-P41-0201-02 pipe support 10-RWS-PD-HGR-0077 ubolt is not installed | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04570 | Verified | On ISO 10-RWS-PD-P41-0201-02 pipe support 10-RWS-PD-HGR-0075 missing ubolt | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04571 | Verified | On ISO 10-RWS-PD-P41-0201-02 flange connection to 10-RWS-SKD-0200/x1 need anti seige bolts | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04572 | Verified | On ISO 10-MWS-PD-P40-0010-01 connection to the UG missing gasket & bolts | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-27 | Gonzalo Pena | 2019-08-27 | Kelvin Cook
RWS-01 | RWS-01 | PI04573 | Verified | On ISO 10-MWS-PD-P40-0010-01 instrument 10-MWS-AE-0011 is not installed | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04574 | Verified | On ISO 10-MWS-PD-P40-0010-01 instrument 10-MWS-AE-0012 is not install | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04575 | Verified | On ISO 10-MWS-PD-P40-0010-01 valve 10-MWS-V-0010 is not installed | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04576 | Verified | On ISO 10-MWS-PD-P41-0200-01 Specialty item 10-MWS-QUIL-0200 is not installed | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-27 | Damon Turner | 2019-09-04 | Kelvin Cook
RWS-01 | RWS-01 | PI04577 | Verified | On ISO 10-MWS-PD-P40-0110-03 is not installed | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-11 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04578 | Verified | On ISO 10-MWS-PD-P40-0554-01 is not installed | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-27 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04579 | Verified | On ISO 10-MWS-PD-P41-0170-01 Specialty item 10-MWS-QUIL-0170 is not installed | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-27 | Damon Turner | 2019-09-04 | Kelvin Cook
RWS-01 | RWS-01 | PI04580 | Verified | On ISO 10-MWS-PD-P41-0470-01 Specialty item 10-MWS-QUIL-0470 is not installed | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-27 | Damon Turner | 2019-09-04 | Kelvin Cook
RWS-01 | RWS-01 | PI04581 | Verified | On ISO 10-MWS-PD-P40-0010-02 instrument 10-MWS-AE-0014 is not installed | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04582 | Verified | On ISO 10-MWS-PD-P41-0010-02 is not installled | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-27 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04605 | Verified | Install stilling well for 10-RWS-LIT-0103A & 0103B at raw water pump intake structure | A | I | Gonzalo Pena | McD | 2019-08-24 | Gonzalo Pena | Const | 2019-09-06 | Gonzalo Pena | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04622 | Verified | Grout vacuum priming pumps 10-RWS-P-0200A & B. | A | C | Johnny Campbell | McD | 2019-08-27 | Johnny Campbell | Const | 2019-09-04 | Johnny Campbell | 2019-09-23 | Joshua Sturgeon
RWS-01 | RWS-01 | PI04623 | Verified | Grout all supports at the raw water pumps and pipe supports at the clarifier. | C | C | Johnny Campbell | McD | 2019-08-27 | Johnny Campbell | Const | 2019-09-06 | Johnny Campbell | 2019-10-16 | Javier Buelvas
RWS-01 | RWS-01 | PI04624 | Verified | Grout electrical equipment in the raw water electrical enclosure. | B | C | Johnny Campbell | McD | 2019-08-27 | Johnny Campbell | Const | 2019-09-06 | Johnny Campbell | 2019-10-16 | Javier Buelvas
RWS-01 | RWS-01 | PI04625 | Verified | Trim up excess thread on bolts of cable tray suport inside RWS electrical enclosure | B | E | Chris Colvin | McD | 2019-08-27 | Chris Colvin | Const | 2019-09-06 | Dustin Futrell | 2019-12-06 | Jack White
RWS-01 | RWS-01 | PI04626 | Verified | 1-RWS-CP-0006A raceay cover on top not fit | B | E | Chris Colvin | McD | 2019-08-27 | Chris Colvin | Const | 2019-09-09 | Richard Cruz | 2019-12-06 | Fred Michael
RWS-01 | RWS-01 | PI04627 | Verified | 120/208 panel place wiring tag and wiring schedule | B | E | Mike Tabbert | McD | 2019-08-27 | Mike Tabbert | Const | 2019-12-07 | Mike Tabbert | 2020-01-13 | Fred Michael
RWS-01 | RWS-01 | PI04628 | Verified | 277/480 panel place wiring tag and wiring schedule | B | E | Mike Tabbert | EAT | 2019-08-27 | Mike Tabbert | Const | 2019-12-07 | Mike Tabbert | 2020-01-13 | Fred Michael
RWS-01 | RWS-01 | PI04629 | Verified | Install 10-RWS-ARV-0103, 0109, 0116 at the raw water pumps. | B | P | Eddie Vannoy | McD | 2019-08-27 | Eddie Vannoy | Const | 2019-09-05 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04630 | Verified | MCC-0007A/B breaker linkage to adjust. Not fuly engage to 'ON' position | B | E | Mike Tabbert | EAT | 2019-08-27 | Mike Tabbert | Const | 2019-12-07 | Michael Law | 2019-12-14 | J.L. Bickham
RWS-01 | RWS-01 | PI04631 | Verified | Install flange bolt at 10-RWS-V-0111 at raw water pump B. | B | P | Damon Turner | McD | 2019-08-27 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-10-03 | Kelvin Cook
RWS-01 | RWS-01 | PI04632 | Verified | Grout all conduit stands | C | E | Johnny Campbell | McD | 2019-08-27 | Johnny Campbell | Const | 2019-09-06 | Johnny Campbell | 2019-10-05 | Mike Tabbert
RWS-01 | RWS-01 | PI04633 | Verified | Perform clean & close on sump 10-RWS-SUMP-0001. | A | M | Carlos Wallen | McD | 2019-08-27 | Carlos Wallen | Const | 2019-09-06 | Carlos Wallen | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04634 | Verified | Tag all valves. | C | P | James Beech | McD | 2019-08-27 | James Beech | Const | 2020-02-27 | James Beech | 2020-02-27 | Kelvin Cook
RWS-01 | RWS-01 | PI04635 | Verified | 10-RWS-JB-0200A and CP-0200 remove rust on top of panel | C | E | Chris Colvin | McD | 2019-08-27 | Chris Colvin | Const | 2019-12-06 | Jack White | 2019-12-06 | Fred Michael
RWS-01 | RWS-01 | PI04636 | Verified | Install 10-RWS-0220 - priming skid drain line. ISO 220. | A | P | Damon Turner | McD | 2019-08-27 | Damon Turner | Const | 2019-09-11 | Damon Turner | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04637 | Verified | 10-RWS-CP-0200 panel to be grounded and ground bushing missing on th epower conduit | A | E | Dustin Futrell | McD | 2019-08-27 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-09-17 | Mike Tabbert
RWS-01 | RWS-01 | PI04638 | Verified | Install 10-RWS-LSH-0021. | A | I | Gonzalo Pena | McD | 2019-08-27 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04639 | Verified | Replace B7 bolts with PTFE bolts at the U/G flange at the clarifier. Line 10-MWS-0010. | B | P | James Beech | McD | 2019-08-27 | James Beech | Const | 2019-10-10 | James Beech | 2019-10-19 | Kelvin Cook
RWS-01 | RWS-01 | PI04640 | Verified | Replace rusty plug on 10-RWS-FY-2014B | B | I | Gonzalo Pena | McD | 2019-08-27 | Gonzalo Pena | Const | 2019-09-11 | Gonzalo Pena | 2019-09-11 | Fred Michael
RWS-01 | RWS-01 | PI04641 | Verified | Replace rusty bolts on top of fan housing 10-RWS-M-0201A/B | B | E | Dustin Futrell | McD | 2019-08-27 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-11 | Fred Michael
RWS-01 | RWS-01 | PI04642 | Verified | Ground motors 10-RWS-M-0001A/B | A | E | Dustin Futrell | McD | 2019-08-27 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-10 | Mike Tabbert
RWS-01 | RWS-01 | PI04643 | Verified | 10-RWS-M-0001A/B bearing temp RTD broken | B | E | Mike Tabbert | McD | 2019-08-27 | Mike Tabbert | Const | 2019-09-11 | Gonzalo Pena | 2019-09-11 | Fred Michael
RWS-01 | RWS-01 | PI04644 | Verified | 10-RWS-PIT-0118 no metal ID tag | B | I | Gonzalo Pena | McD | 2019-08-27 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-20 | Martin Perry
RWS-01 | RWS-01 | PI04645 | Verified | Need phenolic tags on 10-ESL-XFM-0007, HTS-XFM-0007, EHS-XFM-0007, RWS-M-0201A/B | B | E | Dustin Futrell | McD | 2019-08-27 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Fred Michael
RWS-01 | RWS-01 | PI04647 | Verified | Panel 0005B phenolic tag missing | B | E | Dustin Futrell | McD | 2019-08-27 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Fred Michael
RWS-01 | RWS-01 | PI04648 | Verified | 10-RWS-PNL-0240 wire tags not labelled according to drawing (LK-10-RWS-EE-WIR-0009 | A | I | Dustin Futrell | McD | 2019-08-27 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-20 | Martin Perry
RWS-01 | RWS-01 | PI04649 | Verified | Cab 10 RWS-0014 pair 2 not labelled accdng to dwg 10-RWS-EE-WIR-0010-0009 | A | I | Dustin Futrell | McD | 2019-08-27 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-20 | Martin Perry
RWS-01 | RWS-01 | PI04650 | Verified | 10-RWS-FIT-0112 Inst ground cables not landed to the body of element | A | I | Dustin Futrell | McD | 2019-08-27 | Dustin Futrell | Const | 2019-09-09 | Richard Cruz | 2019-09-10 | Mike Tabbert
RWS-01 | RWS-01 | PI04651 | Verified | DCS-CAB-204 grounding not complete | A | I | Dustin Futrell | McD | 2019-08-27 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-09-03 | Martin Perry
RWS-01 | RWS-01 | PI04652 | Verified | Remove embeded rebar and abandoned anchors from the concrete wall on top of the intake sump and around of the top of the sump walls. | B | C | Johnny Campbell | McD | 2019-08-27 | Johnny Campbell | Const | 2019-09-04 | Johnny Campbell | 2019-10-16 | Javier Buelvas
RWS-01 | RWS-01 | PI04653 | Verified | Band grating around electrical support. See intake sump. | B | S | Tim Gallegos | McD | 2019-08-27 | Tim Gallegos | Const | 2019-09-06 | Tim Gallegos | 2019-10-16 | Javier Buelvas
RWS-01 | RWS-01 | PI04654 | Verified | Remove pencil rods and patch concrete inside the intake sump. | A | C | Johnny Campbell | McD | 2019-08-27 | Johnny Campbell | Const | 2019-09-04 | Johnny Campbell | 2019-09-23 | Javier Buelvas
RWS-01 | RWS-01 | PI04655 | Verified | Grout base plates of chemical feed steel structure. | C | C | Johnny Campbell | McD | 2019-08-27 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2020-01-15 | Michael Law
RWS-01 | RWS-01 | PI04656 | Verified | Trim anchor bolts of the electrical enclosure. | B | S | Tim Gallegos | McD | 2019-08-27 | Tim Gallegos | Const | 2019-09-06 | Tim Gallegos | 2019-10-16 | Javier Buelvas
RWS-01 | RWS-01 | PI04657 | Verified | Install permanent handrail around penetration of the intake pipe to the sump. | B | S | Bobby Williams | McD | 2019-08-27 | Bobby Williams | Const | 2019-10-01 | Tim Gallegos | 2019-10-16 | Javier Buelvas
RWS-01 | RWS-01 | PI04658 | Verified | Seal botom of electrical enclosure. | B | S | Tim Gallegos | McD | 2019-08-27 | Tim Gallegos | Const | 2019-09-06 | Tim Gallegos | 2019-10-16 | Javier Buelvas
RWS-01 | RWS-01 | PI04659 | Verified | Repair damaged lagging of 30" intake pipe insulation and cap southern end. | B | Q | Jorge Alexander | PCI | 2019-08-27 | Jorge Alexander | Const | 2019-12-08 | Jack White | 2019-12-08 | Jorge Alexander
RWS-01 | RWS-01 | PI04721 | Verified | 10-RWS-V-0208 & 10-RWS-V-0096 are not accessible. | D | P | Michael Law | McD | 2019-09-03 | Michael Law | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
RWS-01 | RWS-01 | PI04966 | Verified | Complete pipe tests & submit paperwork. | A | P | Damon Turner | McD | 2019-09-11 | Damon Turner | Const | 2019-09-17 | Eric Policarpio | 2019-09-17 | Eric Policarpio
RWS-01 | RWS-01 | PI04967 | Verified | ISO 10-RWS-PD-P41-0093-01 pipe support 10-RWS-PD-HGR-0049 is not intalled. | B | P | James Beech | McD | 2019-09-12 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-19 | Kelvin Cook
RWS-01 | RWS-01 | PI04968 | Verified | ISO 10-RWS-PD-P41-0094-01 pipe support 10-RWS-PD-HGR-0053 is not intalled. | B | P | James Beech | McD | 2019-09-12 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-10-19 | Kelvin Cook
RWS-01 | RWS-01 | PI04969 | Verified | ISO 10-RWS-PD-P41-0095-01 add support at veritical riser attach to existing unistrut. | B | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-07 | Kelvin Cook
RWS-01 | RWS-01 | PI04970 | Verified | ISO 10-RWS-PD-P41-0095-01 add support to pipe close to noozle at Tank. | B | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-07 | Kelvin Cook
RWS-01 | RWS-01 | PI04971 | Verified | ISO 10-RWS-PD-P41-0097-01 pipe support 10-RWS-PD-HGR-0047 is not intalled. | B | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const |  |  | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04972 | Verified | Grout supports at Floccant tank. | C | C | Johnny Campbell | McD | 2019-09-12 | Johnny Campbell | Const | 2019-11-21 | Johnny Campbell | 2019-11-23 | Kelvin Cook
RWS-01 | RWS-01 | PI04973 | Verified | Grout supports at Floccant containment wall. | C | C | Johnny Campbell | McD | 2019-09-12 | Johnny Campbell | Const | 2019-11-21 | Johnny Campbell | 2019-11-23 | Kelvin Cook
RWS-01 | RWS-01 | PI04974 | Verified | Remove all plastic from floccuant tank. | B | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const |  |  | 2019-09-17 | Kelvin Cook
RWS-01 | RWS-01 | PI04975 | Verified | Lash down tank (Floccuant). | A | M | Shane Crowe | McD | 2019-09-12 | Shane Crowe | Const | 2019-09-13 | Joshua Sturgeon | 2019-09-18 | Kelvin Cook
RWS-01 | RWS-01 | PI04976 | Verified | 10-RWS-LIT-0240 not installed. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-09-13 | Gonzalo Pena | 2019-09-20 | Martin Perry
RWS-01 | RWS-01 | PI04977 | Verified | 10-RWS-LIT-0240 replace plastic plug. | A | I | Gonzalo Pena | McD | 2019-09-12 | Gonzalo Pena | Const | 2019-09-13 | Gonzalo Pena | 2019-09-20 | Martin Perry
RWS-01 | RWS-01 | PI04978 | Verified | 10-RWS-LSHH -0240- wiring is too tight between conduit and switch. | A | E | Dustin Futrell | McD | 2019-09-12 | Dustin Futrell | Const | 2019-09-18 | Mike Tabbert | 2019-09-23 | Albert Burge
RWS-01 | RWS-01 | PI04979 | Verified | Floccuant containment valve not installed - moved to cat B 18-Sep | A | P | Damon Turner | McD | 2019-09-12 | Damon Turner | Const | 2019-10-07 | Damon Turner | 2019-10-07 | Kelvin Cook
RWS-01 | RWS-01 | PI04981 | Verified | Re-attach ground to clamp on backwash comp. B (clamp broken). | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-12-06 | Jack White | 2019-12-06 | Fred Michael
RWS-01 | RWS-01 | PI04982 | Verified | Install floccuant tank manway cover. | A | M | Shane Crowe | McD | 2019-09-12 | Shane Crowe | Const | 2019-09-13 | Shane Crowe | 2019-09-18 | Kelvin Cook
RWS-01 | RWS-01 | PI04983 | Verified | Straighten out ground on backwash comp. A. | B | E | Chris Colvin | McD | 2019-09-12 | Chris Colvin | Const | 2019-12-06 | Jack White | 2019-12-06 | Fred Michael
RWS-01 | RWS-01 | PI04984 | Verified | Need to re-seal electrical bldg. | C | C | Bobby Williams | McD | 2019-09-12 | Bobby Williams | Const | 2020-01-06 | Tim Gallegos | 2020-01-15 | Nelson Eichelberger
RWS-01 | RWS-01 | PI07241 | Verified | 10-RWS-LSH-0121 - switch is broken & needs replacing. Weldolet has obstruction. | A | I | Mike Tabbert | McD | 2019-09-25 | Mike Tabbert | Const | 2019-11-19 | James Tanner | 2019-11-21 | Albert Burge
RWS-01 | RWS-01 | PI08453 | Verified | Complete heat trace installation raw water area. | C | E | Jorge Alexander | McD | 2019-10-02 | Jorge Alexander | Const | 2019-12-17 | Jorge Alexander | 2019-12-23 | Michael Law
RWS-01 | RWS-01 | PI08454 | Verified | Complete insulation raw water area. | C | Q | Sheri Fritz | PCI | 2019-10-02 | Sheri Fritz | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
RWS-01 | RWS-01 | PI08455 | Verified | Complete pipe paint touchup raw water area. | C | C | Alan Huntsman | McD | 2019-10-02 | Alan Huntsman | Const | 2019-11-12 | Carlos Wallen | 2019-12-12 | Michael Law
RWS-01 | RWS-01 | PI08456 | Verified | Complete structural steel paint touchup raw water area. | C | C | Alan Huntsman | McD | 2019-10-02 | Alan Huntsman | Const | 2019-11-12 | Carlos Wallen | 2019-12-12 | Michael Law
RWS-01 | RWS-01 | PI08457 | Verified | Remove all un used materials from raw water area. | C | C | Alan Huntsman | McD | 2019-10-02 | Alan Huntsman | Const | 2019-11-11 | Carlos Wallen | 2019-12-06 | Fred Michael
RWS-01 | RWS-01 | PI08799 | Verified | 10-RWS-CP-0240 panel prevents room door from opening, not enough clearance. | D | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Comm | 2020-06-11 | Mike Tabbert | 2021-06-17 | John Watts
RWS-01 | RWS-01 | PI08800 | Verified | 10-RWS-CP-0002 panel door cannot open due to interference with Cationic Flocculant Skid. | D | E | Chris Colvin | McD | 2019-10-04 | Chris Colvin | Comm | 2020-06-11 | Mike Tabbert | 2021-06-17 | John Watts
RWS-01 | RWS-01 | PI12803 | Verified | 10-RWS-PD-P41-0095-01 install a 1" check valve per new detail. | A | P | James Beech | McD | 2019-11-06 | James Beech | Comm |  |  | 2019-11-12 | Michael Law
RWS-01 | RWS-01 | PI14797 | Verified | 10-RWS-ARV-0084; Raw Water Discharge Header Air Release Valve is not installed | B | P | William Mitchell | McD | 2019-12-14 | William Mitchell | Comm | 2020-03-17 | William Mitchell | 2020-04-07 | Bernard Stasse
RWS-01 | RWS-01 | PI14849 | Verified | Install 6" riser clamp and shim accordingly to make the flange level 10-RWS-LIT-0103A | B | P | James Beech | McD | 2019-12-20 | James Beech | Comm | 2020-01-14 | Tim Green | 2020-01-14 | Ethan Byrd
RWS-01 | RWS-01 | PI14850 | Verified | Install 6" riser clamp and shim accordingly to make the flange level 10-RWS-LIT-0103B | B | P | James Beech | McD | 2019-12-20 | James Beech | Comm | 2020-01-14 | Tim Green | 2020-01-14 | Ethan Byrd
RWS-01 | RWS-01 | PI14855 | Verified | Install 6" riser clamp and shim accordingly to make the flange level | B | P | James Beech | McD | 2019-12-20 | James Beech | Comm |  |  | 2020-01-14 | Ethan Byrd
RWS-01 | RWS-01 | PI13880 | Verified | 10-RWS-PI-0241A - replace gauge with silicone filled diaphragm gauge combo. | B | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Comm | 2020-03-09 | Tim Green | 2020-04-02 | Michael Law
RWS-01 | RWS-01 | PI13881 | Verified | 10-RWS-PI-0241B - replace gauge with silicone filled diaphragm gauge combo. | B | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Comm | 2020-03-09 | Tim Green | 2020-04-02 | Michael Law
RWS-01 | RWS-01 | PI15571 | Verified | 10-RWS-M-0001A/B - Broken metallic flex, exposed wiring on the equipment. | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-05-13 | Chris Colvin | 2021-05-24 | Keith Pollock
RWS-01 | RWS-01 | PI15572 | Verified | 10-RWS-P-0200B - Pump/Motor has a broken coupling | C | M | William Mitchell | McD | 2020-01-08 | William Mitchell | Comm | 2020-01-14 | Shannon Scott | 2020-01-14 | Shannon Scott
RWS-01 | RWS-01 | PI15573 | Verified | 10-RWS-COM-0006A - needs equip tag replaced, wrong tag no. installed | C | E | Mike Tabbert | McD | 2020-01-08 | Mike Tabbert | Comm | 2020-05-04 | Mike Tabbert | 2020-10-06 | Dave Goldak
RWS-01 | RWS-01 | PI16208 | Verified | 10-RWS-M-0201A & 10-RWS-M-0201B - Need guard around the packing gland for rotating equipment | B | M | Shane Crowe | McD | 2020-01-20 | Shane Crowe | Comm | 2020-02-24 | Shane Crowe | 2020-02-25 | John Watts
RWS-01 | RWS-01 | PI16249 | Verified | Tighten condulet cover in the raw water flocculant room. | C | E | Chris Colvin | McD | 2020-01-21 | Chris Colvin | Comm | 2020-01-23 | Jared Stimpson | 2020-01-28 | Fred Michael
RWS-01 | RWS-01 | PI16259 | Verified | Raw water pump area - pipe supports at the southwest corner - tighten anchor bolts. | C | P | James Beech | McD | 2020-01-21 | James Beech | Comm | 2020-03-05 | James Beech | 2020-03-05 | Dave Goldak
RWS-01 | RWS-01 | PI16686 | Verified | 10-RWS-ARV-0103 & 10-RWS-ARV-0109 - Need to install the missing caps. | B | M | James Beech | McD | 2020-02-07 | James Beech | Comm | 2020-03-27 | James Beech | 2020-04-07 | Bernard Stasse
RWS-01 | RWS-01 | PI17664 | Verified | 10-RWS-P-0200B - The Raw Water Priming System Vacuum Pump B has a broken coupling. | B | M | William Mitchell | McD | 2020-03-04 | William Mitchell | Comm | 2020-03-10 | William Mitchell | 2020-12-16 | Dave Goldak
RWS-01 | RWS-01 | PI17751 | Verified | Valve 10-RWS-V-0107: Insulation and cladding not installed properly. Prohibits valve operation. | C | X | Sheri Fritz | PCI | 2020-03-10 | Sheri Fritz | Const | 2020-04-29 | Michael Law | 2020-05-27 | Dave Goldak
RWS-01 | RWS-01 | PI18124 | Verified | 10-RWS-P-0001B - There's a seal leak at Raw Water Pump Bravo. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-20 | William Mitchell | 2021-02-01 | Dave Goldak
RWS-01 | RWS-01 | PI18157 | Verified | RWS Flocculant System has no AUTO control from the PLC. | D | I | Charles Worthington | McD | 2020-03-20 | Charles Worthington | Comm | 2020-06-10 | Charles Worthington | 2020-06-18 | John Watts
RWS-01 | RWS-01 | PI16223 | Verified | Flocculant tank containment drain valve is not lockable. | D | P | Charles Worthington | McD | 2020-01-21 | Charles Worthington | Comm | 2020-07-20 | Mike Tabbert | 2020-08-14 | Nelson Eichelberger
SAS-01 | SAS-01 | PI01259 | Verified | Service Air Receiver Information Tag painted over | B | M | Joshua Sturgeon | ACS | 2019-05-28 | Joshua Sturgeon | Const | 2019-08-08 | Joshua Sturgeon | 2019-08-08 | Joshua Sturgeon
SAS-01 | SAS-01 | PI02638 | Verified | LK-10-SAS-PD-P40-0102-04 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-26 | Damon Turner | 2019-09-17 | Tom Noble
SAS-01 | SAS-01 | PI02641 | Verified | LK-10-SAS-PD-P42-0118-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-05 | Damon Turner | 2019-08-13 | Tom Noble
SAS-01 | SAS-01 | PI02642 | Verified | LK-1A-SAS-PD-P41-0235-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-16 | Terry Deaton | 2019-08-16 | Tom Noble
SAS-01 | SAS-01 | PI02643 | Verified | LK-1A-SAS-PD-P41-0235-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-20 | Tom Noble
SAS-01 | SAS-01 | PI02644 | Verified | LK-1A-SAS-PD-P41-0247-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-09-04 | Damon Turner | 2019-09-04 | Lucas Foster
SAS-01 | SAS-01 | PI02645 | Verified | LK-1B-SAS-PD-P41-0235-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-20 | Tom Noble
SAS-01 | SAS-01 | PI02646 | Verified | LK-1B-SAS-PD-P41-0235-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-20 | Tom Noble
SAS-01 | SAS-01 | PI02647 | Verified | LK-1B-SAS-PD-P41-0235-03 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-06 | Tom Noble
SAS-01 | SAS-01 | PI02648 | Verified | LK-1B-SAS-PD-P41-0238-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-28 | Bijo Varghese | 2019-08-28 | Bijo Varghese
SAS-01 | SAS-01 | PI02649 | Verified | LK-1B-SAS-PD-P41-0238-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-09-03 | Damon Turner | 2019-09-03 | Bijo Varghese
SAS-01 | SAS-01 | PI02650 | Verified | LK-1B-SAS-PD-P41-0247-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-06 | Tom Noble
SAS-01 | SAS-01 | PI02651 | Verified | LK-1C-SAS-PD-P41-0107-03 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-05 | Damon Turner | 2019-08-12 | Tom Noble
SAS-01 | SAS-01 | PI02652 | Verified | LK-1C-SAS-PD-P41-0203-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-05 | Damon Turner | 2019-08-12 | Tom Noble
SAS-01 | SAS-01 | PI02653 | Verified | LK-1C-SAS-PD-P41-0222-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-05 | Damon Turner | 2019-08-12 | Tom Noble
SAS-01 | SAS-01 | PI02654 | Verified | LK-1C-SAS-PD-P41-0224-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-05 | Damon Turner | 2019-08-12 | Tom Noble
SAS-01 | SAS-01 | PI02655 | Verified | LK-1C-SAS-PD-P41-0227-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-05 | Damon Turner | 2019-08-12 | Tom Noble
SAS-01 | SAS-01 | PI04889 | Verified | Tag all valves. | C | P | James Beech | McD | 2019-09-10 | James Beech | Const | 2020-02-27 | James Beech | 2020-02-27 | Kelvin Cook
SAS-01 | SAS-01 | PI04891 | Verified | On ISO 10-SAS-PD-P40-0102-04 valve 10-SAS-V-0111 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04892 | Verified | On ISO 10-SAS-PD-P41-0104-01 valve handle stop is missing at 10-SAS-V-0105 | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SAS-01 | SAS-01 | PI04896 | Verified | On ISO 10-SAS-PD-P41-0220-01 on pipe support 10-SAS-PD-HGR-0027 drill new holes and plumb up pipe | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-18 | Damon Turner | 2019-10-07 | Kelvin Cook
SAS-01 | SAS-01 | PI04897 | Verified | On ISO 10-SAS-PD-P41-0221-01 pipe support 10-SAS-PD-HGR-0030 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-10-07 | Kelvin Cook
SAS-01 | SAS-01 | PI04898 | Verified | On ISO 10-SAS-PD-P41-0233-01 rotate 10-SAS-V-237 stem to west for operator friendly | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-24 | Kelvin Cook
SAS-01 | SAS-01 | PI04899 | Verified | On ISO 10-SAS-PD-P41-0252-01 missing valve handle stop at 10-SAS-V-0252 | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-24 | Kelvin Cook
SAS-01 | SAS-01 | PI04900 | Verified | On ISO 10-SAS-PD-P41-0253-01 missing valve handle stop at 10-SAS-V-0253 | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-24 | Kelvin Cook
SAS-01 | SAS-01 | PI04901 | Verified | On ISO 10-SAS-PD-P41-0254-01 installl proper gasket at flange connection to UG | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-07 | Kelvin Cook
SAS-01 | SAS-01 | PI04902 | Verified | On 1A-SAS-PD-P41-0209-01 quick connect 10-SAS-QC-0209 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04903 | Verified | On 1A-SAS-PD-P41-0209-01 install proper gasket at flange connection to UG | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-24 | Kelvin Cook
SAS-01 | SAS-01 | PI04904 | Verified | On ISO 1A-SAS-PD-P41-0211-01 pipe support 10-SAS-PD-HGR-0002 has loose ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04905 | Verified | On ISO 1A-SAS-PD-P41-0211-01 install proper gasket at flange connection to UG | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-18 | Damon Turner | 2019-09-24 | Kelvin Cook
SAS-01 | SAS-01 | PI04906 | Verified | On ISO 1A-SAS-PD-P41-0235-01 quick connect 10-SAS-QC-0235 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-11 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04907 | Verified | On ISO 1A-SAS-PD-P41-0235-02 pipe support 1A-SAS-PD-HGR-0123 has a loose ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-24 | Damon Turner | 2019-10-07 | Kelvin Cook
SAS-01 | SAS-01 | PI04908 | Verified | On ISO 1A-SAS-PD-P41-0235-03 pipe support 1A-SAS-PD-HGR-0129 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-03 | Bobby Williams | 2019-10-05 | Kelvin Cook
SAS-01 | SAS-01 | PI04909 | Verified | On ISO 1A-SAS-PD-P41-0235-03 pipe support 1A-SAS-PD-HGR-0126 has loose ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04910 | Verified | On ISO 1A-SAS-PD-P41-0235-03 quick connect 10-SAS-QC-0265 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04911 | Verified | On ISO 1A-SAS-PD-P41-0238-01 pipe support 1A-SAS-PD-HGR-0150 & 0152 are not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-24 | Damon Turner | 2019-10-07 | Kelvin Cook
SAS-01 | SAS-01 | PI04912 | Verified | On ISO 1A-SAS-PD-P41-0238-02 pipe support 1A-SAS-PD-HGR-0157 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-24 | Damon Turner | 2019-10-07 | Kelvin Cook
SAS-01 | SAS-01 | PI04913 | Verified | On ISO 1A-SAS-PD-P41-0238-02 spool 0238-2 is not intalled | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-24 | Damon Turner | 2019-10-07 | Kelvin Cook
SAS-01 | SAS-01 | PI04914 | Verified | On ISO 1A-SAS-PD-P41-0243-01 quick connect 1A-SAS-QC-0243 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-11 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04915 | Verified | On ISO 1A-SAS-PD-P41-0243-01 pipe support 1A-SAS-PD-HGR-0009 has loose ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-17 | Nelson Eichelberger | 2019-09-24 | Kelvin Cook
SAS-01 | SAS-01 | PI04916 | Verified | On ISO 1A-SAS-PD-P41-0243-01 install proper gasket at flange connection to UG | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-11 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04917 | Verified | On ISO 1A-SAS-PD-P41-0244-01 install proper gasket at flange connection to UG | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04918 | Verified | On ISO 1A-SAS-PD-P41-0247-01 rotate valve 10-SAS-V-0247 stem to east | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04919 | Verified | On ISO 1A-SAS-PD-P41-0247-02 quick connect 1A-SAS-QC-0248 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04920 | Verified | On ISO 1A-SAS-PD-P41-0247-02 loose ubolt on spool 0247-1 | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-24 | Damon Turner | 2019-10-07 | Kelvin Cook
SAS-01 | SAS-01 | PI04921 | Verified | On ISO 1A-SAS-PD-P41-0247-02 field rev is not complete | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-08 | Damon Turner | 2019-10-08 | Kelvin Cook
SAS-01 | SAS-01 | PI04922 | Verified | On ISO 1A-SAS-PD-P41-0247-02 just off pipe support 1A-SAS-PD-HGR-0109 above feed water pump house pipe out of plumb cut pipe and fix | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-30 | Bobby Williams | 2019-10-03 | Kelvin Cook
SAS-01 | SAS-01 | PI04923 | Verified | On ISO 1B-SAS-PD-P41-0209-01 quick connect 1B-SAS-QC-0209 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-11 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04924 | Verified | On ISO 1B-SAS-PD-P41-0209-01 pipe support 1B-SAS-PD-HGR-0005 has loose ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04925 | Verified | On ISO 1B-SAS-PD-P41-0209-01 install proper gasket at flange connection to UG | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-11 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04926 | Verified | On ISO 1B-SAS-PD-P41-0211-01 quick connect 1B-SAS-QC-0211 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04927 | Verified | On ISO 1B-SAS-PD-P41-0211-01 pipe support 1B-SAS-PD-HGR-0006 has loose ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04928 | Verified | On ISO 1B-SAS-PD-P41-0211-01 install proper gasket at flange connection to UG | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04929 | Verified | On ISO 1B-SAS-PD-P41-0235-01 quick connect 1B-SAS-QC-0235 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04930 | Verified | On ISO 1B-SAS-PD-P41-0235-01 install proper gasket at flange connection to UG | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-24 | Kelvin Cook
SAS-01 | SAS-01 | PI04931 | Verified | On ISO 1B-SAS-PD-P41-0235-02 pipe support 1B-SAS-PD-HGR-0136 & 0134 & 0133 are not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-30 | Bobby Williams | 2019-10-03 | Kelvin Cook
SAS-01 | SAS-01 | PI04932 | Verified | On ISO 1B-SAS-PD-P41-0235-03 spools 0235-2 & 0235-3 are not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-17 | Damon Turner | 2019-09-24 | Kelvin Cook
SAS-01 | SAS-01 | PI04933 | Verified | On ISO 1B-SAS-PD-P41-0238-01 pipe supports 1B-SAS-PD-HGR-0164 & 0163 | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-03 | Bobby Williams | 2019-10-05 | Kelvin Cook
SAS-01 | SAS-01 | PI04934 | Verified | On ISO 1B-SAS-PD-P41-0238-01 valve 1B-SAS-V-0239 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04935 | Verified | On ISO 1B-SAS-PD-P41-0238-01 quick connect 1B-SAS-QC-0236 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04936 | Verified | ISO 1B-SAS-PD-P41-0238-02 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-17 | Damon Turner | 2019-09-24 | Kelvin Cook
SAS-01 | SAS-01 | PI04937 | Verified | On ISO 1B-SAS-PD-P41-0242-01 pipe support 10-SAS-PD-HGR-0007 has loose ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04938 | Verified | On ISO 1B-SAS-PD-P41-0242-01 Install proper gasket at flange connection to UG | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-24 | Kelvin Cook
SAS-01 | SAS-01 | PI04939 | Verified | On ISO 1B-SAS-PD-P41-0243-01 quick connect 1B-SAS-QC-0243 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04940 | Verified | On ISO 1B-SAS-PD-P41-0244-01 quick connect 1B-SAS-QC-0244 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04941 | Verified | On ISO 1B-SAS-PD-P41-0244-01 pipe support 10-SAS-PD-HGR-0008 has loose ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04942 | Verified | On ISO 1B-SAS-PD-P41-0244-01 Install proper gasket at flange connection to UG | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-24 | Kelvin Cook
SAS-01 | SAS-01 | PI04943 | Verified | On ISO 1B-SAS-PD-P41-0247-01 quick connect 1B-SAS-QC-0247 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-12 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04944 | Verified | On ISO 1B-SAS-PD-P41-0247-01 bolts tool long at UG | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-17 | Damon Turner | 2019-09-24 | Kelvin Cook
SAS-01 | SAS-01 | PI04945 | Verified | On ISO 1B-SAS-PD-P41-0247-02 spools 0247-2 & 0247-03 are not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04946 | Verified | On ISO 1B-SAS-PD-P41-0247-02 pipe support 1B-SAS-PD-HGR-0112 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04947 | Verified | On ISO 1B-SAS-PD-P41-0247-02 valve 1B-SAS-V-0249 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04948 | Verified | On ISO 1C-SAS-PD-P41-0107-02 pipe support 1C-SAS-PD-HGR-0084 has loose ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-07 | Kelvin Cook
SAS-01 | SAS-01 | PI04949 | Verified | On ISO 1C-SAS-PD-P41-0107-03 pipe support 1C-SAS-PD-HGR-0094 3 bolt clamp up side down | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-18 | Damon Turner | 2019-09-24 | Kelvin Cook
SAS-01 | SAS-01 | PI04950 | Verified | On ISO 1C-SAS-PD-P41-0222-02 pipe support 1C-SAS-PD-HGR-0043 install nut to top of eye bolt and tighten it down | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SAS-01 | SAS-01 | PI04951 | Verified | On ISO 1C-SAS-PD-P41-0222-02 pipe support 1C-SAS-PD-HGR-0049 plumb up ubolt and tighten it down | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SAS-01 | SAS-01 | PI04952 | Verified | On ISO 1C-SAS-PD-P41-0222-03 pipe support 1C-SAS-PD-HGR-0058 is loose | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SAS-01 | SAS-01 | PI04953 | Verified | On ISO 1C-SAS-PD-P41-0222-03 pipe support 1C-SAS-PD-HGR-0059 is not intalled | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-07 | Kelvin Cook
SAS-01 | SAS-01 | PI04954 | Verified | On ISO 1C-SAS-PD-P41-0222-03 pipe support 1C-SAS-PD-HGR-0062 & 0063 & 0064 loose nut at ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SAS-01 | SAS-01 | PI04955 | Verified | On ISO 1C-SAS-PD-P41-0222-03 pipe support 1C-SAS-PD-HGR-0065 has loose nut at turnbuckle | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SAS-01 | SAS-01 | PI04956 | Verified | On ISO 1C-SAS-PD-P41-0222-03 pipe support 1C-SAS-PD-HGR-0066 missing nut at turnbuckle | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SAS-01 | SAS-01 | PI04957 | Verified | On ISO 1C-SAS-PD-P41-0226-01 pipe support 1C-SAS-PD-HGR-0071 has loose ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SAS-01 | SAS-01 | PI04958 | Verified | 10-SAS-PCV-0106 facing wrong direction. | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const |  |  | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04959 | Verified | Adjust blind flange bolts (threads) on service air tank. | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SAS-01 | SAS-01 | PI04960 | Verified | Rotate valve handle (interference) - south side of STG Lube Oil. | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SAS-01 | SAS-01 | PI04961 | Verified | 10-P41-SAS-0220 - rotate valve handle - NW corner of circ. water pumps. | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SAS-01 | SAS-01 | PI04962 | Verified | Replace plastic plug in service air tank with proper plug. | A | M | Shane Crowe | McD | 2019-09-10 | Shane Crowe | Const | 2019-09-13 | Shane Crowe | 2019-09-20 | Martin Perry
SAS-01 | SAS-01 | PI06095 | Verified | LK-10-SAS-PD-P40-0102-04 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Tom Noble
SAS-01 | SAS-01 | PI06096 | Verified | LK-10-SAS-PD-P41-0218-01 - Needs Welds Cleared - duplicate punch | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Tom Noble
SAS-01 | SAS-01 | PI06097 | Verified | LK-10-SAS-PD-P41-0219-02 - Needs Welds Cleared - duplicate punch | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Tom Noble
SAS-01 | SAS-01 | PI06098 | Verified | LK-10-SAS-PD-P42-0118-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Tom Noble
SAS-01 | SAS-01 | PI09732 | Verified | Tag all system components | C | P | Tim Green | McD | 2019-10-22 | Tim Green | Comm | 2021-05-24 | Eric Policarpio | 2021-05-24 | Keith Pollock
SAS-01 | SAS-01 | PI09733 | Verified | Touch up paint throughout entire system | C | X | Jerry Smith | McD | 2019-10-22 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09734 | Verified | Grout all system supports as required | C | C | Johnny Campbell | McD | 2019-10-22 | Johnny Campbell | Comm | 2019-12-18 | Blake Boudreaux | 2019-12-18 | Blake Boudreaux
SAS-01 | SAS-01 | PI09735 | Verified | Remove tape, wire, rope and old tags from system piping and components | C | P | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-04-28 | Michael Law | 2020-10-06 | Dave Goldak
SAS-01 | SAS-01 | PI09736 | Verified | Turn 10-SAS-PI-0100; Service Air Receiver Pressure Indicator to the North for better operator visual contact | C | I | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-01-29 | James Tanner | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09737 | Verified | Install drain line on 10-SAS-SRV-0100; Service Air Receiver Safety Relief Valve | C | P | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-02-10 | Kelvin Cook | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09738 | Verified | Tubing and tubing tray is bent at 10-SAS-PIT-0106; Service Air Discharge Pressure Indicating Transmitter | C | I | Gonzalo Pena | McD | 2019-10-22 | Gonzalo Pena | Comm | 2019-12-31 | Gonzalo Pena | 2020-01-08 | Blake Boudreaux
SAS-01 | SAS-01 | PI09739 | Verified | Loose U-Bolt at Service Air discharge header downstream of 10-SAS-PCV-0106; Pressure Control Valve Line No. 3-10-SAS-0102 | C | P | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09740 | Verified | Remove nails stuck in concrete at North side of Service Air Receiver base foundation | C | C | Johnny Campbell | McD | 2019-10-22 | Johnny Campbell | Comm | 2019-12-18 | Blake Boudreaux | 2019-12-18 | Blake Boudreaux
SAS-01 | SAS-01 | PI09741 | Verified | Reroute Service Air Receiver ground cable between conduit and base foundation at E side, similar to 2nd ground cable on West side, currently installed over top of conduit | C | E | Chris Colvin | McD | 2019-10-22 | Chris Colvin | Comm | 2020-05-04 | Matt Gilmore | 2020-07-10 | Dave Goldak
SAS-01 | SAS-01 | PI09742 | Verified | Tighten ground cable connections at East and West side of Service Air Receiver Tank | C | E | Chris Colvin | McD | 2019-10-22 | Chris Colvin | Comm | 2020-04-29 | Mike Tabbert | 2020-07-10 | Dave Goldak
SAS-01 | SAS-01 | PI09743 | Verified | Route .25 inch Service Air Receiver drain tubing to floor drain as indicated on P&ID LK-10-SAS-ME-PID-0001 | C | P | Tim Green | McD | 2019-10-22 | Tim Green | Comm | 2020-10-06 | Eric Policarpio | 2020-10-06 | Dave Goldak
SAS-01 | SAS-01 | PI09745 | Verified | 1 inch Service Air supply line to 1C-SAS-V-0206; Isolation Valve needs additional support, NW side of STG Operating Deck, | C | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Comm | 2020-02-07 | Kelvin Cook | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09746 | Verified | Cut hold down anchors at 1C-SAS-V-0225; Isolation Valve support, SE side of STG Operational Deck, Line No. 1-1C-SAS-0225 | C | P | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-01-17 | Tim Green | 2020-01-31 | Blake Boudreaux
SAS-01 | SAS-01 | PI09747 | Verified | Vertical support is blocking hose connection at 1C-SAS-QC-0228; Quick Disconnect fitting, SW side of STG Opertional Deck, Line No. 1C-SAS-0228 | C | P | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-31 | Blake Boudreaux
SAS-01 | SAS-01 | PI09748 | Verified | Tighten U-Bolt upstream of 1C-SAS-V-0224; Isolation Valve, SE side of STG Mezzanine Level, Line No. 1-1C-SAS-0224 | C | P | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-31 | Blake Boudreaux
SAS-01 | SAS-01 | PI09749 | Verified | 1C-SAS-QC-0204; Quick Disconnect fitting missing, NW side of STG Ground Floor, Line No. 1-1C-SAS-0204 | C | P | Bobby Williams | McD | 2019-10-22 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09750 | Verified | 1C-SAS-QC-0229; Quick Disconnect fitting missing, Closed Cooling Water Pump Area STG Ground Floor, Line No. 1-1C-SAS-0229 | C | P | Bobby Williams | McD | 2019-10-22 | Bobby Williams | Comm | 2020-02-14 | Bobby Williams | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09751 | Verified | Gasket not installed at 2 inch Service Air stub up flange at Demin Water Storage Tank and Pump Area, Line No. 2-10-SAS-0151 | C | P | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-31 | Blake Boudreaux
SAS-01 | SAS-01 | PI09752 | Verified | Remove concrete splatter from 2 inch stub up flange at Makeup Water Area & Raw Water Treatment Area, Line No. 2-10-SAS-0150 | C | C | Johnny Campbell | McD | 2019-10-22 | Johnny Campbell | Comm | 2020-02-20 | Alan Huntsman | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09753 | Verified | 10-SAS-V-0218; 1 inch Service Air Isolation Valve is different from the rest of the Service Air System, Piping should evaluate, Filter Press Equipment Area, Line No. 2-10-SAS-0218 | C | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09754 | Verified | Remove double gaskets from 2 inch stub up flange and replace with required single gasket at Filter Press House, Line No. 2-10-SAS-0119 | C | P | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-31 | Blake Boudreaux
SAS-01 | SAS-01 | PI09755 | Verified | Verify level of final grade around 2 inch stub up flange at NE side of Filter Press Building foundation to determine if permanent support is needed, Line No. 2-10-SAS-0119 | C | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Comm | 2020-02-07 | Kelvin Cook | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09756 | Verified | Verify if existing Service Air pipe support is permanent at Circ Water Pump Area, Line No. 1-10-SAS-0220 | C | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Comm | 2020-02-07 | Kelvin Cook | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09757 | Verified | Verify if existing Service Air pipe support is permanent at Cooling Tower Chemical Injection Area, Line No. 1-10-SAS-0206 | C | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09758 | Verified | Loose U-Bolt at 10-SAS-V-0221; 1 inch Service Air Isolation Valve, North side of Cooling Tower, Line No. 1-10-SAS-0221 | C | P | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-31 | Blake Boudreaux
SAS-01 | SAS-01 | PI09759 | Verified | Plastic valve handle cover is missing at 10-SAS-V-0253; 1 inch Service Air Isolation, Fire Protection /Service Water Pumps, Line No. 1-10-SAS-0253 | C | P | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-31 | Blake Boudreaux
SAS-01 | SAS-01 | PI09760 | Verified | Seal Service Air pipe penetration at North side of Demin/Water Treatment Building, Line No. 1-10-SAS-0254 | C | C | Johnny Campbell | McD | 2019-10-22 | Johnny Campbell | Comm |  |  | 2019-12-14 | Jack Fields
SAS-01 | SAS-01 | PI09761 | Verified | Service Air Line No. 1-10-SAS-0233 at Batch Neutralization Area needs support, North West side of Demin/Water Treatment Building | C | P | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-05-01 | James Beech | 2020-07-10 | Dave Goldak
SAS-01 | SAS-01 | PI09762 | Verified | Valve operation results in pinch point between valve and I-Beam at 10-SAS-V-0237; 1 inch Service Air Isolation Valve, Batch Neutralization Area, North West side of Demin/Water Treatment Building | C | P | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-01-17 | Tim Green | 2020-01-31 | Blake Boudreaux
SAS-01 | SAS-01 | PI09763 | Verified | 1 inch Service Air supply line needs support at 1A-SAS-V-0247; 1 inch Service Air Isolation Valve, 1A HRSG Boiler Feed Pumps Area Floor Elevation, Line No. 2-1A-SAS-0120 | C | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Comm | 2020-02-07 | Kelvin Cook | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09764 | Verified | 1 inch Service Air supply line needs support at 1A-SAS-V-0248; 1 inch Service Air Isolation Valve, Mezzanine Elevation 1A HRSG Boiler Feed Pumps Area, Line No. 1-1A-SAS-0120 | C | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Comm | 2020-02-07 | Kelvin Cook | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09765 | Verified | Quick Disconnect fitting missing at 1A-SAS-V-0265; 1 inch Service Air Isolation Valve, E side Top of 1A HRSG | C | P | Bobby Williams | McD | 2019-10-22 | Bobby Williams | Comm | 2020-02-19 | Bobby Williams | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09766 | Verified | 1 inch Service Air supply line needs support at 1B-SAS-V-0247; 1 inch Service Air Isolation Valve, 1B HRSG Boiler Feed Pumps Area Floor Elevation, Line No. 2-1B-SAS-0120 | D | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Comm | 2020-02-07 | Kelvin Cook | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09767 | Verified | 1 inch Service Air supply line needs support at 1B-SAS-V-0248; 1 inch Service Air Isolation Valve, Mezzanine Elevation 1B HRSG Boiler Feed Pumps Area, Line No. 1-1B-SAS-0120 | D | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Comm | 2020-02-07 | Kelvin Cook | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09768 | Verified | Quick Disconnect fitting missing at 1B-SAS-V-0268; 1 inch Service Air Isolation Valve, W side Top of 1B HRSG | C | P | Bobby Williams | McD | 2019-10-22 | Bobby Williams | Comm | 2020-02-19 | Bobby Williams | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09769 | Verified | Quick Disconnect fitting missing at 1B-SAS-V-0265; 1 inch Service Air Isolation Valve, E side Top of 1B HRSG | C | P | Bobby Williams | McD | 2019-10-22 | Bobby Williams | Comm | 2020-02-19 | Bobby Williams | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI09770 | Verified | Loose nut on valve handle at 1B-SAS-0265; 1 inch Service Air Isolation Valve, E side Top of 1B HRSG | C | P | James Beech | McD | 2019-10-22 | James Beech | Comm | 2020-01-17 | Tim Green | 2020-04-08 | Bernard Stasse
SAS-01 | SAS-01 | PI16209 | Verified | 10-SAS-V-0437 - The service air line outside the demin building on the plant north side does not blow adequate pressure, it is clogged with something. The tap right before it inside the building blows adequate pressure. | B | P | William Mitchell | McD | 2020-01-20 | William Mitchell | Comm | 2020-03-06 | William Mitchell | 2020-03-09 | Nelson Eichelberger
SAS-01 | SAS-01 | PI18897 | Verified | Support Ubolts coming loose - Elev 532 Service Air and Instrument air riser, northwest corner of HRSG | C | P | Tim Green | McD | 2020-07-08 | Tim Green | Const | 2020-07-24 | Tim Green | 2020-11-11 | Dave Goldak
SAS-01 | SAS-01 | PI18898 | Verified | Support Ubolts coming loose - Elev 555 Service Air and Instrument air riser, northwest corner of HRSG | C | P | Tim Green | McD | 2020-07-08 | Tim Green | Const | 2020-07-24 | Tim Green | 2020-11-11 | Dave Goldak
SDS-01 | SDS-01 | PI09492 | Verified | ISO 1C-SDS-PD-P40-0010-01 | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-11-23 | Kelvin Cook
SDS-01 | SDS-01 | PI09493 | Verified | On ISO 1C-SDS-PD-P41-0017-03 pipe support 1C-SDS-PD-HGR-0069 has loose nuts at eyebolt & turnbuckle | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09494 | Verified | On ISO 1C-SDS-PD-P41-0017-03 pipe support 1C-SDS-PD-HGR-0068 replace bolta all threaded rod, loose nuts | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09495 | Verified | On ISO 1C-SDS-PD-P41-0017-03 spool that supports HGR-0068 & 0069 are located pipe to be reworked due to not being square | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09496 | Verified | On ISO 1C-SDS-PD-P41-0017-02 pipe support 1C-SDS-PD-HGR-0064 need to center shoe support roll plumb. Item 1 not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-04 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09497 | Verified | On ISO 1C-SDS-PD-P41-0017-02 pipe support 1C-SDS-PD-HGR-0062 center shoe on support item 1 not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09498 | Verified | On ISO 1C-SDS-PD-P41-0017-02 pipe support 1C-SDS-PD-HGR-0063 center shoe on support item 1 is not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-04 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09499 | Verified | On ISO 1C-SDS-PD-P41-0017-02 spool 0017-2 remove rope debri from pipe | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09500 | Verified | On ISO 1C-SDS-PD-P41-0017-02 pipe support 1C-SDS-PD-HGR-0061 is not installed properly | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-06 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09501 | Verified | On ISO 1C-SDS-PD-P41-0017-02 pipe support 1C-SDS-PD-HGR-0065 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09502 | Verified | On ISO 1C-SDS-PD-P41-0017-02 pipe support 1C-SDS-PD-HGR-0066 place shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09503 | Verified | On ISO 1C-SDS-PD-P41-0017-02 pipe support 1C-SDS-PD-HGR-0067 place shoe on support seat | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09504 | Verified | On ISO 1C-SDS-PD-P41-0017-01 pipe support 1C-SDS-PD-HGR-0060 item 3 is not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-06 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09505 | Verified | On ISO 1C-SDS-PD-P41-0017-01 pipe support 1C-SDS-PD-HGR-0060 rework support ( NO 2.75" gap) | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09506 | Verified | On ISO 1C-SDS-PD-P41-0017-01 pipe support 1C-SDS-PD-HGR-0060 shoe not on center of support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09507 | Verified | On ISO 1C-SDS-PD-P41-0011-03 pipe support 1C-SDS-PD-HGR-0057 & 0058 is incomplete | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09508 | Verified | On ISO 1C-SDS-PD-P41-0011-03 spool that supports HGR-0057 & 0058 are located pipe to be reworked due to not being square | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09509 | Verified | On ISO 1C-SDS-PD-P41-0011-02 remove insulation from spool 0011-2 | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09510 | Verified | On ISO 1C-SDS-PD-P41-0011-02 pipe support 1C-SDS-PD-HGR-0050 item 4 not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09511 | Verified | On ISO 1C-SDS-PD-P41-0011-02 pipe support 1C-SDS-PD-HGR-0051 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09512 | Verified | On ISO 1C-SDS-PD-P41-0011-02 pipe support 1C-SDS-PD-HGR-0051 item 1 is not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09513 | Verified | On ISO 1C-SDS-PD-P41-0011-02 pipe support 1C-SDS-PD-HGR-0051 top half of pipe clamp missing | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09514 | Verified | On ISO 1C-SDS-PD-P41-0011-02 pipe support 1C-SDS-PD-HGR-0051 bolt for top half of existing clamp missing | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09515 | Verified | On ISO 1C-SDS-PD-P41-0011-02 pipe support 1C-SDS-PD-HGR-0052 center shoe on support. Item 1 is not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09516 | Verified | On ISO 1C-SDS-PD-P41-0011-02 pipe support 1C-SDS-PD-HGR-0053 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09517 | Verified | On ISO 1C-SDS-PD-P41-0011-02 pipe support 1C-SDS-PD-HGR-0054 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09518 | Verified | On ISO 1C-SDS-PD-P41-0011-02 pipe support 1C-SDS-PD-HGR-0055 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09519 | Verified | On ISO 1C-SDS-PD-P41-0011-02 pipe support 1C-SDS-PD-HGR-0056 center shoe on support, elevation is to long of gap from shoe to support. | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09520 | Verified | On ISO 1C-SDS-PD-P41-0011-01 pipe support 1C-SDS-PD-HGR-048 has loose bolts on pipe clamp | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09521 | Verified | On ISO 1C-SDS-PD-P41-0011-01 pipe support 1C-SDS-PD-HGR-049 item 3 not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09522 | Verified | On ISO 1C-SDS-PD-P41-0011-01 pipe support 1C-SDS-PD-HGR-049 item 3 rework support fro no 2.75 gap. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-13 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09523 | Verified | On ISO 1C-MSS-PD-P41-0026-02 pipe support 1C-MSS-PD-HGR-0062 has loose nut at eyebolt and turnbuckle. | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09524 | Verified | On ISO 1C-MSS-PD-P41-0026-02 pipe support 1C-MSS-PD-HGR-0062 item 1 & 10 are not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09525 | Verified | On ISO 1C-MSS-PD-P41-0026-02 pipe support 1C-MSS-PD-HGR-0065 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09526 | Verified | On ISO 1C-MSS-PD-P41-0026-02 pipe support 1C-MSS-PD-HGR-0068 loose nut at eyebolt and turnbuckle | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09527 | Verified | On ISO 1C-MSS-PD-P41-0026-02 pipe support 1C-MSS-PD-HGR-0068 replace bent all threaded rods | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09528 | Verified | On ISO 1C-MSS-PD-P41-0026-02 pipe support 1C-MSS-PD-HGR-0069 loose nuts at eyebolt and turnbuckle | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09529 | Verified | On ISO 1C-MSS-PD-P41-0026-01 spool 0026-2 remove dunnage from under pipe | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09530 | Verified | On ISO 1C-MSS-PD-P41-0026-01 pipe support 1C-MSS-PD-HGR-0061 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09531 | Verified | On ISO 1C-MSS-PD-P41-0026-01 pipe support 1C-MSS-PD-HGR-0118 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09532 | Verified | On ISO 1C-MSS-PD-P41-0026-01 pipe support 1C-MSS-PD-HGR-0119 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09533 | Verified | On ISO 1C-MSS-PD-P41-0016-02 pipe support 1C-MSS-PD-HGR-0072 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09534 | Verified | On ISO 1C-MSS-PD-P41-0016-02 pipe support 1C-MSS-PD-HGR-0073 is out of plumb. Item 1 not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09535 | Verified | On ISO 1C-MSS-PD-P41-0016-02 pipe support 1C-MSS-PD-HGR-0074 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09536 | Verified | On ISO 1C-MSS-PD-P41-0016-02 pipe support 1C-MSS-PD-HGR-0076 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09537 | Verified | On ISO 1C-MSS-PD-P41-0016-02 pipe support 1C-MSS-PD-HGR-0077 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09538 | Verified | On ISO 1C-MSS-PD-P41-0016-02 pipe support 1C-MSS-PD-HGR-0078 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09539 | Verified | On ISO 1C-MSS-PD-P41-0016-02 pipe support 1C-MSS-PD-HGR-0079 replace bent all thread rod | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09540 | Verified | On ISO 1C-MSS-PD-P41-0016-02 pipe support 1C-MSS-PD-HGR-0079 full thread engagement +2 minimum required at turnbuckle and eyebolt | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09541 | Verified | On ISO 1C-MSS-PD-P41-0016-02 pipe support 1C-MSS-PD-HGR-0079 loose clamp | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09542 | Verified | On ISO 1C-MSS-PD-P41-0016-02 pipe support 1C-MSS-PD-HGR-0080 loose clamp | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09543 | Verified | On ISO 1C-MSS-PD-P41-0016-02 pipe support 1C-MSS-PD-HGR-0080 full thread engagement +2 minimum required at turnbuckle & eye bolt. Nut required at eyebolt. | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09544 | Verified | On ISO 1C-MSS-PD-P41-0016-01 remove wire from spool 0016-3 | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09545 | Verified | On ISO 1C-MSS-PD-P41-0016-01 just of valve 1C-MSS-V-0043 sloping issue. | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-11 | Ethan Byrd
SDS-01 | SDS-01 | PI09546 | Verified | On ISO 1C-MSS-PD-P41-0016-01 pipe support 1C-MSS-PD-HGR-0070 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09547 | Verified | On ISO 1C-MSS-PD-P41-0016-01 pipe support 1C-MSS-PD-HGR-0071 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09548 | Verified | On ISO 1C-MSS-PD-P41-0016-01 pipe support 1C-MSS-PD-HGR-0116 has loose clamp | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09549 | Verified | On ISO 1C-MSS-PD-P41-0016-01 pipe support 1C-MSS-PD-HGR-0117 has loose clamp & loose nuts | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09550 | Verified | On ISO 1C-MSS-PD-P41-0016-01 pipe support 1C-MSS-PD-HGR-0117 set spring can at stem blow | A | P | James Beech | McD | 2019-10-15 | James Beech | Const |  |  | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI09551 | Verified | On ISO 1C-MSS-PD-P41-0016-01 pipe support 1C-MSS-PD-HGR-0120 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09552 | Verified | On ISO 1B-MSS-PD-P41-0016-01 remove rigging | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09553 | Verified | On ISO 1B-MSS-PD-P41-0016-01 pipe support 1B-MSS-PD-HGR-0096 has no offset | A | P | James Beech | McD | 2019-10-15 | James Beech | Const |  |  | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI09554 | Verified | On ISO 1B-MSS-PD-P41-0016-01 pipe support 1B-MSS-PD-HGR-0096 bolt missing in 3 bolt clamp | A | P | James Beech | McD | 2019-10-15 | James Beech | Const |  |  | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI09555 | Verified | On ISO 1B-MSS-PD-P41-0016-01 pipe support 1B-MSS-PD-HGR-0096 has loose nuts | A | P | James Beech | McD | 2019-10-15 | James Beech | Const |  |  | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI09556 | Verified | On ISO 1B-MSS-PD-P41-0016-01 pipe support 1B-MSS-PD-HGR-0098 item 1 is not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-11 | Ethan Byrd
SDS-01 | SDS-01 | PI09557 | Verified | On ISO 1B-MSS-PD-P41-0016-01 pipe support 1B-MSS-PD-HGR-0099 item 1 is not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-11 | Ethan Byrd
SDS-01 | SDS-01 | PI09558 | Verified | On ISO 1B-MSS-PD-P41-0016-02 pipe support 1B-MSS-PD-HGR-0101 full thread enagement +2 thread minimum required at bottom of eyebolt | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09559 | Verified | On ISO 1B-MSS-PD-P41-0016-02 pipe support 1B-MSS-PD-HGR-0103 has no offset & a loose nut | A | P | James Beech | McD | 2019-10-15 | James Beech | Const |  |  | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI09560 | Verified | On ISO 1B-MSS-PD-P41-0016-02 pipe support 1B-MSS-PD-HGR-0104 set per offset | A | P | James Beech | McD | 2019-10-15 | James Beech | Const |  |  | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI09561 | Verified | On ISO 1B-MSS-PD-P41-0016-02 pipe support 1B-MSS-PD-HGR-0105 item 1 not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09562 | Verified | On ISO 1B-MSS-PD-P41-0016-02 pipe support 1B-MSS-PD-HGR-0109 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09563 | Verified | On ISO 1B-MSS-PD-P41-0016-02 pipe support 1B-MSS-PD-HGR-0111 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09564 | Verified | On ISO 1B-MSS-PD-P41-0036-02 remove rigging | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09565 | Verified | On ISO 1B-MSS-PD-P41-0036-01 remove rigging | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09566 | Verified | On ISO 1B-MSS-PD-P41-0036-01 pipe support 1B-MSS-PD-HGR-0084 is no installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09567 | Verified | On ISO 1B-MSS-PD-P41-0036-01 pipe support 1B-MSS-PD-HGR-0085 is no installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09568 | Verified | On ISO 1B-MSS-PD-P41-0036-01 pipe support 1B-MSS-PD-HGR-0086 is no installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09569 | Verified | On ISO 1B-MSS-PD-P41-0036-01 pipe support 1B-MSS-PD-HGR-0087 is no installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09570 | Verified | On ISO 1B-MSS-PD-P41-0036-01 pipe support 1B-MSS-PD-HGR-0088 is no installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09571 | Verified | On ISO 1B-MSS-PD-P41-0036-01 pipe support 1B-MSS-PD-HGR-0115 is no installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09572 | Verified | On ISO 1A-MSS-PD-P41-0036-01 remove rigging | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09573 | Verified | On ISO 1A-MSS-PD-P41-0036-01 remove rope from spool 0036-2 | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09574 | Verified | On ISO 1A-MSS-PD-P41-0036-01 pipe support 1A-MSS-PD-HGR-0081 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09575 | Verified | On ISO 1A-MSS-PD-P41-0036-01 pipe support 1A-MSS-PD-HGR-0082 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09576 | Verified | On ISO 1A-MSS-PD-P41-0036-01 pipe support 1A-MSS-PD-HGR-0083 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-04 | Ethan Byrd
SDS-01 | SDS-01 | PI09577 | Verified | On ISO 1A-MSS-PD-P41-0016-01 pipe support 1A-MSS-PD-HGR-0089 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const |  |  | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI09578 | Verified | On ISO 1A-MSS-PD-P41-0016-01 pipe support 1A-MSS-PD-HGR-0090 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09579 | Verified | On ISO 1A-MSS-PD-P41-0016-01 pipe support 1A-MSS-PD-HGR-0091 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09580 | Verified | On ISO 1B-LPS-PD-P41-0036-01 pipe support 1B-LPS-PD-HGR-0045 installed in the wrong location, relocate per ISO | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09581 | Verified | On ISO 1B-LPS-PD-P41-0036-01 pipe support 1B-LPS-PD-HGR-0046 supports should be leveled per detail rework | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-12-03 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09582 | Verified | On ISO 1B-LPS-PD-P41-0036-01 pipe support 1B-LPS-PD-HGR-0047 shoe is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09583 | Verified | On ISO 1B-LPS-PD-P41-0036-02 pipe support 1B-LPS-PD-HGR-0053 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-11 | Ethan Byrd
SDS-01 | SDS-01 | PI09584 | Verified | On ISO 1B-LPS-PD-P41-0036-02 pipe support 1B-LPS-PD-HGR-0054 center shoe on support. | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09585 | Verified | On ISO 1B-LPS-PD-P41-0036-02 pipe support 1B-LPS-PD-HGR-0054 item 2 is not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09586 | Verified | On ISO 1B-LPS-PD-P41-0036-02 pipe support 1B-LPS-PD-HGR-0055 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09587 | Verified | On ISO 1A-LPS-PD-P41-0036-01 pipe support 1A-LPS-PD-HGR-0036 plumb support per detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09588 | Verified | On ISO 1A-LPS-PD-P41-0036-02 pipe support 1A-LPS-PD-HGR-0041 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09589 | Verified | On ISO 1A-LPS-PD-P41-0036-02 pipe support 1A-LPS-PD-HGR-0042 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09590 | Verified | On ISO 1A-LPS-PD-P41-0036-02 pipe support 1A-LPS-PD-HGR-0043 roll shoe flat to top of beam | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09591 | Verified | On ISO 1B-LPS-PD-P41-0016-02 pipe support 1B-LPS-PD-HGR-0025 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09592 | Verified | On ISO 1B-LPS-PD-P41-0016-02 pipe support 1B-LPS-PD-HGR-0026 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09593 | Verified | On ISO 1B-LPS-PD-P41-0016-03 pipe support 1B-LPS-PD-HGR-0031 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09594 | Verified | On ISO 1B-LPS-PD-P41-0016-03 pipe support 1B-LPS-PD-HGR-0032 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09595 | Verified | On ISO 1B-LPS-PD-P41-0016-03 pipe support 1B-LPS-PD-HGR-0033 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09596 | Verified | On ISO 1B-LPS-PD-P41-0016-03 pipe support 1B-LPS-PD-HGR-0034 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09597 | Verified | On ISO 1A-LPS-PD-P41-0016-03 pipe support 1A-LPS-PD-HGR-0011 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09598 | Verified | On ISO 1A-LPS-PD-P41-0016-03 pipe support 1A-LPS-PD-HGR-0012 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09599 | Verified | On ISO 1A-LPS-PD-P41-0016-03 pipe support 1A-LPS-PD-HGR-0013 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09600 | Verified | On ISO 1A-LPS-PD-P41-0016-02 pipe support 1A-LPS-PD-HGR-0005 verify that support is level | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-12-05 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09601 | Verified | On ISO 1A-LPS-PD-P41-0016-02 pipe support 1A-LPS-PD-HGR-0008 rotate shoes per detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09602 | Verified | On ISO 1A-LPS-PD-P41-0016-02 pipe support 1A-LPS-PD-HGR-0009 rotate shoe per detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09603 | Verified | On ISO 1A-LPS-PD-P41-0016-02 pipe support 1A-LPS-PD-HGR-0010 rotate shoes per detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09604 | Verified | On ISO 1A-LPS-PD-P41-0016-01 pipe support 1A-LPS-PD-HGR-0001 center shoe on support. Item 4 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09605 | Verified | On ISO 1A-LPS-PD-P41-0016-01 pipe support 1A-LPS-PD-HGR-0002 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09606 | Verified | On ISO 1A-LPS-PD-P41-0016-01 pipe support 1A-LPS-PD-HGR-0003 remove wire from support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09607 | Verified | On ISO 1C-ASF-PD-P41-0062-03 remove rope from spool 0062-2 | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09608 | Verified | On ISO 1C-ASF-PD-P41-0062-03 pipe support 1C-ASF-PD-HGR-0043 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-04 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09609 | Verified | On ISO 1C-ASF-PD-P41-0062-03 pipe support 1C-ASF-PD-HGR-0044 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-04 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09610 | Verified | On ISO 1C-ASF-PD-P41-0062-03 pipe support 1C-ASF-PD-HGR-0045 center shoe on support | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-04 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09611 | Verified | On ISO 1C-ASF-PD-P41-0062-02 relocate/rework spool & set support proper. Pipe needs to go south | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-24 | James Beech | 2019-12-10 | Ethan Byrd
SDS-01 | SDS-01 | PI09612 | Verified | On ISO 1C-ASF-PD-P41-0062-02 pipe support 1C-ASF-PD-HGR-0036 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-04 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09613 | Verified | On ISO 1C-ASF-PD-P41-0062-02 pipe support 1C-ASF-PD-HGR-0038 center shoe on support. Item 4 is not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09614 | Verified | On ISO 1C-ASF-PD-P41-0062-02 pipe support 1C-ASF-PD-HGR-0039 center shoe on support. Item 2 is not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09615 | Verified | On ISO 1C-ASF-PD-P41-0062-02 pipe support 1C-ASF-PD-HGR-0040 center shoe on support. Item 1 is not installed. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09616 | Verified | On ISO 1C-ASF-PD-P41-0062-02 pipe support 1C-ASF-PD-HGR-0042 loose clamp & out of plumb N/S | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-04 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09617 | Verified | On ISO 1C-ASF-PD-P41-0062-02 pipe support 1C-ASF-PD-HGR-0042 pipe run N/S too short | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09618 | Verified | On ISO 1C-ASF-PD-P41-0062-01 pipe support 1C-ASF-PD-HGR-0035 support can is not plumb per detail cut Item 4 and move north reweld. Look at support detail | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-05 | Ethan Byrd
SDS-01 | SDS-01 | PI09619 | Verified | On ISO 1C-SDS-0056-01 FW to Drains Tank Incomplete | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-12-15 | Michael Law | 2019-12-16 | Kelvin Cook
SDS-01 | SDS-01 | PI09620 | Verified | On ISO 1C- SDS-P41-0103 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2020-01-02 | Ethan Byrd
SDS-01 | SDS-01 | PI09621 | Verified | On ISO 1C- SDS-P41-0102 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-15 | Kelvin Cook
SDS-01 | SDS-01 | PI09622 | Verified | On ISO 1C- SDS-P41-0101 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2019-12-15 | Kelvin Cook
SDS-01 | SDS-01 | PI09623 | Verified | On ISO 1C- SDS-P41-0100 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-11-18 | James Beech | 2020-01-02 | Ethan Byrd
SDS-01 | SDS-01 | PI09624 | Verified | On ISO 1C-SDS-P41-0065 is not installed | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-12-03 | James Beech | 2020-01-02 | Ethan Byrd
SDS-01 | SDS-01 | PI09625 | Verified | On ISO 1C-SDS-P40-0066 bolts are missing at 1C-SDS-V-0115 | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-12-11 | James Beech | 2019-12-11 | Ethan Byrd
SDS-01 | SDS-01 | PI09626 | Verified | On ISO 1C-SDS-P40-0066 bolts are missing at 1C-SDS-AOV-0114 | A | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2019-12-11 | James Beech | 2019-12-11 | Ethan Byrd
SDS-01 | SDS-01 | PI09627 | Verified | Grout all supports. | C | C | Johnny Campbell | McD | 2019-10-15 | Johnny Campbell | Const |  |  | 2019-12-14 | Jack Fields
SDS-01 | SDS-01 | PI09628 | Verified | Tag all components. | C | P | James Beech | McD | 2019-10-15 | James Beech | Const | 2020-04-15 | Michael Law | 2020-04-15 | Michael Law
SDS-01 | SDS-01 | PI09629 | Verified | Perform clean & close on tank 1C-SDS-T-0001. | A | M | Shane Crowe | McD | 2019-10-15 | Shane Crowe | Const | 2019-11-26 | Michael Law | 2019-12-10 | Joshua Sturgeon
SDS-01 | SDS-01 | PI09819 | Verified | Test Package SDS-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-14 | Eric Policarpio
SDS-01 | SDS-01 | PI13675 | Verified | Complete wiring for 1C-SDS-AOV-0114 to solenoid. | A | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Const | 2020-01-10 | Chris Caywood | 2020-01-15 | Albert Burge
SDS-01 | SDS-01 | PI13676 | Verified | Grout supports at the STG Drains Tank. | C | C | Johnny Campbell | McD | 2019-11-27 | Johnny Campbell | Const |  |  | 2019-12-14 | Jack Fields
SDS-01 | SDS-01 | PI13677 | Verified | Install conduit & wirng to 1C-SDS-LIT-0100 at the STG Drains Tank. | A | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Const | 2020-01-10 | Chris Caywood | 2020-01-15 | Albert Burge
SDS-01 | SDS-01 | PI13678 | Verified | Install conduit & wirng to 1C-SDS-LSH-0100 at the STG Drains Tank. | A | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Const | 2020-01-10 | Chris Caywood | 2020-01-15 | Albert Burge
SDS-01 | SDS-01 | PI13679 | Verified | Pull & terminate cable for 1C-SDS-LV-0100. | A | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
SDS-01 | SDS-01 | PI13680 | Verified | Grout support at 1C-SDS-LV-0100. | C | C | Alan Huntsman | McD | 2019-11-27 | Alan Huntsman | Const | 2020-03-13 | Johnny Campbell | 2020-04-07 | Bernard Stasse
SDS-01 | SDS-01 | PI13681 | Verified | 1C-SDS-AOV-0114 - tubing needs "candy cane". | A | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2019-12-19 | Albert Burge
SDS-01 | SDS-01 | PI13682 | Verified | 1C-SDS-AOV-0114 - pull & terminate cable. | A | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Const | 2019-12-10 | Chris Colvin | 2020-01-15 | Albert Burge
SDS-01 | SDS-01 | PI14067 | Verified | 1CSDSC0007, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
SDS-01 | SDS-01 | PI14068 | Verified | 1CSDSC0009, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
SDS-01 | SDS-01 | PI14069 | Verified | 1CSDSC0011, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14070 | Verified | 1CSDSC0012, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14071 | Verified | 1CSDSC0013, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14072 | Verified | 1CSDSC0014, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14076 | Verified | 1CSDSC0018, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14077 | Verified | 1CSDSC0019, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14084 | Verified | 1CSDSC0028, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
SDS-01 | SDS-01 | PI14085 | Verified | 1CSDSC0029, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
SDS-01 | SDS-01 | PI14086 | Verified | 1CSDSC0030, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14087 | Verified | 1CSDSC0033, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14088 | Verified | 1CSDSK0001, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
SDS-01 | SDS-01 | PI14095 | Verified | 1CSDSK0008, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
SDS-01 | SDS-01 | PI14096 | Verified | 1CSDSK0009, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
SDS-01 | SDS-01 | PI14097 | Verified | 1CSDSX0001, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14098 | Verified | 1CSDSX0002, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14099 | Verified | 1CSDSC0001, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14100 | Verified | 1CSDSC0003, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14101 | Verified | 1CSDSC0005, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14102 | Verified | 1CSDSC0007, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14103 | Verified | 1CSDSC0009, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-31 | Mike Tabbert
SDS-01 | SDS-01 | PI14104 | Verified | 1CSDSC0011, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14105 | Verified | 1CSDSC0012, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14106 | Verified | 1CSDSC0013, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14107 | Verified | 1CSDSC0014, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14108 | Verified | 1CSDSC0015, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14109 | Verified | 1CSDSC0016, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14110 | Verified | 1CSDSC0017, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14111 | Verified | 1CSDSC0018, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14112 | Verified | 1CSDSC0019, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14113 | Verified | 1CSDSC0020, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
SDS-01 | SDS-01 | PI14114 | Verified | 1CSDSC0021, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14115 | Verified | 1CSDSC0022, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14116 | Verified | 1CSDSC0023, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14117 | Verified | 1CSDSC0025, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14118 | Verified | 1CSDSC0027, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14119 | Verified | 1CSDSC0028, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14120 | Verified | 1CSDSC0029, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14121 | Verified | 1CSDSC0030, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14122 | Verified | 1CSDSC0033, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14123 | Verified | 1CSDSK0001, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
SDS-01 | SDS-01 | PI14124 | Verified | 1CSDSK0002, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-30 | Mike Tabbert
SDS-01 | SDS-01 | PI14125 | Verified | 1CSDSK0003, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-30 | Mike Tabbert
SDS-01 | SDS-01 | PI14126 | Verified | 1CSDSK0004, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-30 | Mike Tabbert
SDS-01 | SDS-01 | PI14127 | Verified | 1CSDSK0005, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-30 | Mike Tabbert
SDS-01 | SDS-01 | PI14128 | Verified | 1CSDSK0006, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-30 | Mike Tabbert
SDS-01 | SDS-01 | PI14129 | Verified | 1CSDSK0007, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-30 | Mike Tabbert
SDS-01 | SDS-01 | PI14130 | Verified | 1CSDSK0008, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-30 | Mike Tabbert
SDS-01 | SDS-01 | PI14131 | Verified | 1CSDSK0009, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-30 | Mike Tabbert
SDS-01 | SDS-01 | PI14132 | Verified | 1CSDSX0001, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14133 | Verified | 1CSDSX0002, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14134 | Verified | 1CCRSX0005, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-09 | Chris Caywood
SDS-01 | SDS-01 | PI14135 | Verified | 1CCRSX0007, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-09 | Chris Caywood
SDS-01 | SDS-01 | PI14136 | Verified | 1CSDSC0001, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14137 | Verified | 1CSDSC0003, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14138 | Verified | 1CSDSC0005, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14139 | Verified | 1CSDSC0007, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14140 | Verified | 1CSDSC0009, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
SDS-01 | SDS-01 | PI14141 | Verified | 1CSDSC0011, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14142 | Verified | 1CSDSC0012, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14143 | Verified | 1CSDSC0013, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14144 | Verified | 1CSDSC0014, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14145 | Verified | 1CSDSC0015, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14146 | Verified | 1CSDSC0016, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14147 | Verified | 1CSDSC0017, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14148 | Verified | 1CSDSC0018, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14149 | Verified | 1CSDSC0019, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-31 | Mike Tabbert
SDS-01 | SDS-01 | PI14150 | Verified | 1CSDSC0020, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14151 | Verified | 1CSDSC0021, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14152 | Verified | 1CSDSC0022, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14153 | Verified | 1CSDSC0023, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14154 | Verified | 1CSDSC0025, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14155 | Verified | 1CSDSC0027, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14156 | Verified | 1CSDSC0028, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14157 | Verified | 1CSDSC0029, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14158 | Verified | 1CSDSC0030, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14159 | Verified | 1CSDSC0033, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14160 | Verified | 1CSDSK0001, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
SDS-01 | SDS-01 | PI14161 | Verified | 1CSDSK0002, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14162 | Verified | 1CSDSK0003, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14163 | Verified | 1CSDSK0004, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14164 | Verified | 1CSDSK0005, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-30 | Mike Tabbert
SDS-01 | SDS-01 | PI14165 | Verified | 1CSDSK0006, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-30 | Mike Tabbert
SDS-01 | SDS-01 | PI14166 | Verified | 1CSDSK0007, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14167 | Verified | 1CSDSK0008, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14168 | Verified | 1CSDSK0009, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
SDS-01 | SDS-01 | PI14169 | Verified | 1CSDSX0001, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
SDS-01 | SDS-01 | PI14170 | Verified | 1CSDSX0002, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
SDS-01 | SDS-01 | PI14368 | Verified | Remove gag from spring can on HGR-904 on Isometric LK-1C-SDS-PD-P40-0050-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI14369 | Verified | Pipe support HRS-PD-HGR-0036 is needs to be plumb per Isometic 1C-HRS-PD-P40-0046-02 also needs full thread engagement on 3 bolt pipe clamp | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-09 | James Tanner | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI14370 | Verified | Tighten bolts in Pipe support HRS-PD-HGR-0033 and adjust so that the pipe shoe is centered on steel per Isometric-1C-HRS-PD-P40-0046-02 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI14371 | Verified | Remove rope from piping located near HRS-PD-HGR-0036 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI14372 | Verified | Need full thread engagement on 3 bolt pipe clamp and adjustable strut needs to be adjusted per ISO on HRS-PD-HGR-0031 Isometric 1C-HRS-PD-P40-0046-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI14373 | Verified | Set pipe shoe to proper offset and needs full thread engagement on clamps 1C-HRS-HGR-0029 Isometric 1C-HRS-PD-P40-0046-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI14374 | Verified | Adjust shoe to center of steel and tighten all bolts HRS-PD-HGR-0028 Isometric 1C-HRS-PD-P40-0046-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI14375 | Verified | Missing pipe supports HRS-PD-HGR-0027 on Isometric 1C-HRS-PD-P40-0046-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-13 | James Beech | 2019-12-13 | Ethan Byrd
SDS-01 | SDS-01 | PI14376 | Verified | Missing pipe supports HRS-PD-HGR-0026 on Isometric 1C-HRS-PD-P40-0046-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-13 | James Beech | 2019-12-13 | Ethan Byrd
SDS-01 | SDS-01 | PI14377 | Verified | Missing pipe supports HRS-PD-HGR-0025 on Isometric 1C-HRS-PD-P40-0046-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-13 | James Beech | 2019-12-13 | Ethan Byrd
SDS-01 | SDS-01 | PI14378 | Verified | Missing pipe supports HRS-PD-HGR-0024 on Isometric 1C-HRS-PD-P40-0046-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const |  |  | 2019-12-13 | Ethan Byrd
SDS-01 | SDS-01 | PI14379 | Verified | Adjust shoe to center of steel and tighten all bolts and remove gags from spring can HRS-PD-HGR-0022 on Isometric 1C-HRS-PD-P40-0046-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-13 | James Beech | 2019-12-13 | Ethan Byrd
SDS-01 | SDS-01 | PI14380 | Verified | Remove wire and rigging from pipe located near pipe support HRS-HGR-0022 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-13 | Ethan Byrd
SDS-01 | SDS-01 | PI14381 | Verified | Incomplete welds and missing spools on Isometric LK-1C-CRS-PD-P41-0086-02 THRU LK-1C-CRS-PD-P41-0086-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI14382 | Verified | Remove wire from Pipe support 1B- HRS-PD-HGR-0006 shoe also has to much gap per detail on Isometric 1B-HRS-PD-P40-0036-02 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI14383 | Verified | Tighten bolts in Pipe support 1B-HRS-HGR-0005 and remove gags from spring can Isometric 1B-HRS-PD-P41-0036-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI14384 | Verified | Need full thread engagement on HRS-HGR-0004 Isometric 1B-HRS-PD-P41-0036-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const |  |  | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI14385 | Verified | Remove unistrut from tubing tray and add angle for support on valve 1B-HRS-AOV-0040 on Isometric 1B-HRS-PD-P41-0036-01 | A | I | Gonzalo Pena | McD | 2019-12-05 | Gonzalo Pena | Const |  |  | 2019-12-13 | Ethan Byrd
SDS-01 | SDS-01 | PI14386 | Verified | Valve handle is missing on 1B-HRS-V-0032 on Isometric 1B-HRS-PD-P41-0036-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-16 | Bobby Williams | 2019-12-31 | Ethan Byrd
SDS-01 | SDS-01 | PI14387 | Verified | To much gap according to iso on pipe support 1A-HRS-PD-HGR-0010 Isometric 1A-HRS-PD-P41-0036-02 also remove wire from shoe when installed correctly | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-12 | Ethan Byrd
SDS-01 | SDS-01 | PI14388 | Verified | All supports need to be hanging plumb according to Isometric 1C-CRS-PD-P41-0036-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const |  |  | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI14389 | Verified | Need full thread engagement on hanger rod and adjustable strut CRS-PD-HGR-0003 Isometric 1C-CRS-PD-P41-0036-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI14390 | Verified | Remove wire and rope from pipe near HGR-0002 Isometric 1C-CRS-PD-P41-0036-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-13 | Ethan Byrd
SDS-01 | SDS-01 | PI14391 | Verified | Plate needs to be turned square with pipe and tightened CRS-HGR-0001 1C-CRS-PD-P41-0036-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-13 | Ethan Byrd
SDS-01 | SDS-01 | PI14392 | Verified | Tighten bolts on clamps hanger also needs to be plumb HRS-HGR-0020 Isometric 1C-HRS-PD-P41-0016-02 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI14393 | Verified | Adjustable strut item #2 needs to be hanging plumb HGR-0017 Isometric 1C-HRS-PD-P41-0016-02 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-13 | Ethan Byrd
SDS-01 | SDS-01 | PI14394 | Verified | Remove rope and Move scaffold plank so that support will hang plumb and tighten bolts HGR-0016 Isometric 1C-HRS-PD-P41-0016-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-13 | Ethan Byrd
SDS-01 | SDS-01 | PI14395 | Verified | Remove rope near HGR-0012 on Isometric 1C-HRS-PD-P41-0016-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-13 | Ethan Byrd
SDS-01 | SDS-01 | PI14396 | Verified | Item #2 and Item#3 are not installed on HGR-0015 Isometric 1C-HRS-PD-P41-0016-01 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-13 | James Beech | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI14397 | Verified | All pipe shoes needs to be centered on steel per Isometric LK-1B-LPS-PD-P41-0016-03 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-13 | James Beech | 2019-12-13 | Ethan Byrd
SDS-01 | SDS-01 | PI14398 | Verified | Center shoe on support and rotate clamps as shown in Isometric 1B-LPS-PD-P41-0016 Support LPS-PD-HGR-0033 | A | P | James Beech | McD | 2019-12-05 | James Beech | Const | 2019-12-13 | James Beech | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI13700 | Verified | 1C-SDS-MOV-9630 - move flex away from pipe (line may move, resting on beam). | A | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Const | 2019-12-10 | Chris Colvin | 2019-12-19 | John Sullivan
SDS-01 | SDS-01 | PI14716 | Verified | 1B-HRS-PD-P41-0036-01: 1B-HRS-HGR-0005 was located on 12/7/2019. Verify the installed spring can is correct | A | P | James Beech | McD | 2019-12-12 | James Beech | Const |  |  | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI14717 | Verified | 1C-HRS-PD-P41-0016-01: 1C-HRS-HGR-0011 was located on 12/7/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const |  |  | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI14718 | Verified | 1C-HRS-PD-P41-0016-01: 1C-HRS-HGR-0014 was located on 12/7/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const |  |  | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI14720 | Verified | 1C-SDS-PD-P41-0007-01: 1C-SDS-HGR-0070 was located on 12/7/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-13 | Bobby Williams | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI14721 | Verified | 1C-SDS-PD-P41-0015-01: 1C-SDS-HGR-0083 was located on 12/7/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-13 | Bobby Williams | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI14723 | Verified | 1C-SDS-PD-P41-0015-01: 1C-SDS-HGR-0097 was located on 12/7/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const |  |  | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI14729 | Verified | 1C-SDS-PD-P41-0065-01: 1C-SDS-HGR-0009 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const |  |  | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI14734 | Verified | 1C-SDS-PD-P41-0051-02: 1C-SDS-HGR-0304 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-13 | Bobby Williams | 2019-12-15 | Ethan Byrd
SDS-01 | SDS-01 | PI14737 | Verified | 1C-SDS-PD-P41-0007-02: 1C-SDS-HGR-0072 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const | 2019-12-15 | Bobby Williams | 2019-12-15 | Ethan Byrd
SDS-01 | SDS-01 | PI14739 | Verified | 1C-SDS-PD-P41-0009-01: 1C-SDS-HGR-0117 Located on 12/9/19 and needs to be installed | A | P | James Beech | McD | 2019-12-12 | James Beech | Const |  |  | 2019-12-14 | Ethan Byrd
SDS-01 | SDS-01 | PI17453 | Verified | Install threaded cap at end of drain line 2-1C-SDS-0065. | C | P | Tim Green | McD | 2020-03-02 | Tim Green | Comm | 2020-06-11 | Tim Green | 2020-06-16 | Dave Goldak
SDS-01 | SDS-01 | PI17454 | Verified | Missing ground jumper at 1C-SDS-AOV-014 electrical flex connection. | D | E | Chris Colvin | McD | 2020-03-02 | Chris Colvin | Comm | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
SEC-01 | SEC-01 | PI18221 | Verified | Cat 6 cable to terminate and label at the Control building | C | I | Sheri Fritz | ITS | 2020-04-22 | Sheri Fritz | Comm | 2020-04-30 | Mike Tabbert | 2020-04-30 | Mike Tabbert
SEC-01 | SEC-01 | PI18222 | Verified | Tag missing on SEC CP at the Control building | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18223 | Verified | Hand hole cover missing on South pole camera | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18224 | Verified | Tag missing on SEC CP at South pole | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18225 | Verified | Tag missing on SEC CP at 1B GT Control package building | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18226 | Verified | Tag missing on SEC CP at 1A GT Control package building | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18227 | Verified | Tag missing on SEC CP at 1A Excitation building | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18228 | Verified | Tag missing on SEC CP at 1B Excitation building | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18229 | Verified | Tag missing on SEC CP at Main PDC building | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18230 | Verified | Tag missing on SEC CP at Thyristor building | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18231 | Verified | Tag missing on SEC CP at Demin building | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18232 | Verified | Ground missing on SEC CP at Demin building, ground the grounding bushing | C | E | Josh Koerner | ITS | 2020-04-22 | Josh Koerner | Comm | 2020-06-11 | Mike Tabbert | 2020-06-11 | Mike Tabbert
SEC-01 | SEC-01 | PI18233 | Verified | Low point drain missing SEC CP at Demin building | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18234 | Verified | CP for camrea at Filter press missing tag | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18235 | Verified | Tag missing on SEC CP at Cooling Tower PDC building | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18237 | Verified | Tag missing on SEC CP at 1A HRSG PDC building | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18238 | Verified | Tag missing on SEC CP at 1B HRSG PDC building | C | E | Mike Tabbert | McD | 2020-04-22 | Mike Tabbert | Comm | 2020-04-28 | Mike Tabbert | 2020-04-28 | Mike Tabbert
SEC-01 | SEC-01 | PI18239 | Verified | 10SECK0001 cable to terminate during outage | C | E | Chris Colvin | McD | 2020-04-28 | Chris Colvin | Comm | 2020-04-30 | Chris Colvin | 2020-05-04 | Mike Tabbert
SEC-01 | SEC-01 | PI18240 | Verified | 10SECK0004 cable to terminate during outage | C | E | Chris Colvin | McD | 2020-04-28 | Chris Colvin | Comm | 2020-04-30 | Chris Corken | 2020-05-04 | Mike Tabbert
SSS-01 | SSS-01 | PI09820 | Verified | Test Package SSS-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-05 | Kelvin Cook
SSS-01 | SSS-01 | PI09821 | Verified | Test Package SSS-T-02 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-05 | Kelvin Cook
SSS-01 | SSS-01 | PI09822 | Verified | Test Package SSS-T-03 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-05 | Kelvin Cook
SSS-01 | SSS-01 | PI09823 | Verified | Test Package SSS-T-04 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-05 | Kelvin Cook
SSS-01 | SSS-01 | PI09824 | Verified | Test Package SSS-T-05 | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-16 | Kelvin Cook
SSS-01 | SSS-01 | PI09825 | Verified | Test Package SSS-T-06 | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-20 | Kelvin Cook
SSS-01 | SSS-01 | PI09826 | Verified | Test Package SSS-T-07 | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2020-01-07 | Kelvin Cook
SSS-01 | SSS-01 | PI10114 | Verified | 1ASSSK0002 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10115 | Verified | 1ASSSX0004 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10116 | Verified | 1ASSSX0007 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10134 | Verified | 1BSSSC0002 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10135 | Verified | 1BSSSX0003 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10136 | Verified | 1BSSSX0007 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10177 | Verified | 1ASSSC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10178 | Verified | 1ASSSC0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10179 | Verified | 1ASSSK0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10180 | Verified | 1ASSSK0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10181 | Verified | 1ASSSX0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10182 | Verified | 1ASSSX0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10183 | Verified | 1ASSSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10184 | Verified | 1ASSSX0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10185 | Verified | 1ASSSX0005 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10186 | Verified | 1ASSSX0006 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10187 | Verified | 1ASSSX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10219 | Verified | 1BSSSC0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10220 | Verified | 1BSSSC0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10221 | Verified | 1BSSSK0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10222 | Verified | 1BSSSX0001 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10223 | Verified | 1BSSSX0002 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10224 | Verified | 1BSSSX0003 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10225 | Verified | 1BSSSX0004 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10226 | Verified | 1BSSSX0005 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10227 | Verified | 1BSSSX0006 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI10228 | Verified | 1BSSSX0007 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
SSS-01 | SSS-01 | PI13917 | Verified | HVAC not installed on 1B bldg | A | M | Joshua Sturgeon | McD | 2019-12-04 | Joshua Sturgeon | Const | 2019-12-16 | Bobby Williams | 2019-12-18 | Mike Tabbert
SSS-01 | SSS-01 | PI13918 | Verified | Use proper size lugs and bolts on the building ground - All sample buildings | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2019-12-09 | Frank Lopez | 2019-12-10 | Mike Tabbert
SSS-01 | SSS-01 | PI13919 | Verified | Cold gal conduit on the main disconnect pabel at 1B bldg | C | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-02 | Mike Tabbert
SSS-01 | SSS-01 | PI13920 | Verified | Condulet cover missing at the chiller at 1B bldg | B | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-10 | Mike Tabbert
SSS-01 | SSS-01 | PI13921 | Verified | Clean up all electrical spare materials around 1B bldg | B | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-10 | Mike Tabbert
SSS-01 | SSS-01 | PI13922 | Verified | Install all sample tubing line to 1B bldg | A | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2019-12-16 | James Tanner | 2020-01-01 | Albert Burge
SSS-01 | SSS-01 | PI13923 | Verified | Drain pipe to drain funnel too short. To complete drain line up to the funnel | A | P | James Beech | McD | 2019-12-04 | James Beech | Const |  |  | 2019-12-20 | Michael Law
SSS-01 | SSS-01 | PI13924 | Verified | Cables 1BSSSXC0001, 2, 4, 5, 6 wire cable label are incorrect | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2019-12-10 | Chris Colvin | 2019-12-10 | Fred Michael
SSS-01 | SSS-01 | PI13925 | Verified | Cables 1ASSSXC0001, 2, 3, 4, 5, 6 wire cable label are incorrect | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2019-12-10 | Chris Colvin | 2019-12-10 | Fred Michael
SSS-01 | SSS-01 | PI13926 | Verified | Clean up panel 1B-SSS-SMP-0100 | B | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2019-12-09 | Frank Lopez | 2019-12-10 | Mike Hebert
SSS-01 | SSS-01 | PI13927 | Verified | Clean up inside 1B bldg | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2019-12-10 | Mike Tabbert | 2019-12-10 | Mike Tabbert
SSS-01 | SSS-01 | PI13928 | Verified | Install fire extinguishers at Sample building | C | M | Jerry Smith | McD | 2019-12-04 | Jerry Smith | Const | 2020-03-09 | Jerry Smith | 2020-03-11 | Mike Tabbert
SSS-01 | SSS-01 | PI13929 | Verified | HVAC wiring to complete at 1B bldg | B | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2020-01-28 | Jared Stimpson | 2020-01-28 | Mike Tabbert
SSS-01 | SSS-01 | PI13930 | Verified | Myers hub loose at DSW panel | B | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-20 | Fred Michael
SSS-01 | SSS-01 | PI13931 | Verified | Chiller Control Panel to be grounded on all buildings | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-11 | Mike Tabbert
SSS-01 | SSS-01 | PI13932 | Verified | Thermostat missing on 1A bldg | B | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2020-01-28 | Jared Stimpson | 2020-01-28 | Mike Tabbert
SSS-01 | SSS-01 | PI13933 | Verified | Disconnect switch @ 1A bldg to clean up panel | B | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2020-03-10 | Chris Colvin | 2020-03-11 | Mike Tabbert
SSS-01 | SSS-01 | PI13934 | Verified | DWS @ 1A bldg cold gal conduit to panel | C | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2020-04-16 | Chris Colvin | 2020-04-29 | Mike Tabbert
SSS-01 | SSS-01 | PI13935 | Verified | Disconnect switch @ 1A bldg wire labels are not insalled | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-11 | Mike Tabbert
SSS-01 | SSS-01 | PI13936 | Verified | All panel from 3 buildings need to be tagged | C | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2020-03-31 | Matt Gilmore | 2020-04-02 | Mike Tabbert
SSS-01 | SSS-01 | PI13937 | Verified | Condulet cover missing at west side og 1C bldg | B | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-20 | Fred Michael
SSS-01 | SSS-01 | PI13938 | Verified | PVC pipe outside of 1C bldg need supports. Pipe just airborne of about 2 inches from ground | C | P | James Beech | McD | 2019-12-04 | James Beech | Const | 2020-03-27 | James Beech | 2020-04-02 | Mike Tabbert
SSS-01 | SSS-01 | PI13939 | Verified | Grout all conduit supports around the 1C building | C | C | Johnny Campbell | McD | 2019-12-04 | Johnny Campbell | Const |  |  | 2019-12-14 | Jack Fields
SSS-01 | SSS-01 | PI13940 | Verified | Potable water connection to reinstate @ bldg 1C | B | P | James Beech | McD | 2019-12-04 | James Beech | Const | 2020-01-13 | Tim Green | 2020-01-15 | Albert Burge
SSS-01 | SSS-01 | PI13941 | Verified | Conduit need support at southside of 1C bldg | C | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2020-05-04 | Matt Gilmore | 2020-05-19 | Mike Tabbert
SSS-01 | SSS-01 | PI13942 | Verified | Main steam sample line at 1C bldg, fitting missing and not yet hooked up | A | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const | 2020-02-10 | James Tanner | 2020-02-19 | Albert Burge
SSS-01 | SSS-01 | PI13943 | Verified | LP exonomizer sample tubing bundle not connected to 1A bldg | A | I | Gonzalo Pena | McD | 2019-12-04 | Gonzalo Pena | Const |  |  | 2019-12-14 | Ethan Byrd
SSS-01 | SSS-01 | PI16218 | Verified | 1C Sample Lab (Plant North Door) - The door is broken & the brackets are loose | C | S | Tim Gallegos | McD | 2020-01-20 | Tim Gallegos | Comm | 2020-06-15 | Tim Gallegos | 2020-07-10 | Dave Goldak
SSS-01 | SSS-01 | PI17728 | Verified | Sample Buiding: north door - missing panic hardware | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Comm | 2020-06-15 | Tim Gallegos | 2020-07-10 | Dave Goldak
SSS-01 | SSS-01 | PI17729 | Verified | Sample Buiding: South door - adjust door closer to allow for door to open completely | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Comm | 2020-05-13 | Tim Gallegos | 2020-06-03 | Dave Goldak
SSS-01 | SSS-01 | PI17730 | Verified | Sample Buiding: South door - Missing cover over door latch | C | S | Tim Gallegos | McD | 2020-03-06 | Tim Gallegos | Comm | 2020-06-15 | Tim Gallegos | 2020-07-10 | Dave Goldak
SSS-01 | SSS-01 | PI18010 | Verified | 1B-SSS-AT-0042/1B-SSS-AT-0066 - The analyzer will not stay running. Suspect: The issue is the analytical board. | C | E | Albert Burge | McD | 2020-03-17 | Albert Burge | Comm | 2020-03-19 | Albert Burge | 2021-05-24 | Keith Pollock
STE-01 | STE-01 | PI09827 | Verified | Test Package STE-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const | 2019-12-09 | Michael Law | 2019-12-12 | Kelvin Cook
STE-01 | STE-01 | PI09828 | Verified | Test Package STE-T-02 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-11 | Eric Policarpio
STE-01 | STE-01 | PI10229 | Verified | 1CSTEC0013 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STE-01 | STE-01 | PI13683 | Verified | 1C-ASF-AOV-0075 - flex too short. | A | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Const | 2019-12-09 | Alex Morin | 2019-12-10 | John Sullivan
STE-01 | STE-01 | PI13684 | Verified | 1C-ASF-0075 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2020-01-01 | Albert Burge
STE-01 | STE-01 | PI13685 | Verified | 1C-STE-MOV-9505 - rework flex. | A | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Const | 2019-12-07 | Brad Stanford | 2019-12-11 | Shannon Scott
STE-01 | STE-01 | PI13686 | Verified | 1C-STE-PV-9503 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Const | 2019-12-05 | James Tanner | 2020-01-22 | Albert Burge
STE-01 | STE-01 | PI13687 | Verified | 1C-STE-MOV-9501 - conduit support bolts at grating are too short. | B | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Const | 2019-12-07 | Brad Stanford | 2019-12-11 | Shannon Scott
STE-01 | STE-01 | PI13688 | Verified | 1C-STE-MOV-9501 - missing serval condulet covers under grating. | B | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Const | 2019-12-09 | Alex Morin | 2019-12-11 | Shannon Scott
STE-01 | STE-01 | PI13689 | Verified | Tag all components with proper tag wiring. | C | P | James Beech | McD | 2019-11-27 | James Beech | Const | 2020-05-01 | James Beech | 2021-01-22 | Eric Policarpio
STE-01 | STE-01 | PI13690 | Verified | 1C-HTS-CAB-0203 needs bracing / support. | B | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Const | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
STE-01 | STE-01 | PI13691 | Verified | Clean all instrument boxes inside & outside. | C | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Const | 2019-12-31 | Gonzalo Pena | 2020-01-30 | Fred Michael
STE-01 | STE-01 | PI13692 | Verified | 1C-STE-PIT-9560 - complete tubing. | A | I | Gonzalo Pena | McD | 2019-11-27 | Gonzalo Pena | Const | 2019-12-06 | James Tanner | 2020-01-22 | Albert Burge
STE-01 | STE-01 | PI13693 | Verified | Complete 1" balance line tie-in to gland steam condenser. ISO 1C-STE-PD-P41-0024-01. | A | P | James Beech | McD | 2019-11-27 | James Beech | Const |  |  | 2019-12-11 | James Beech
STE-01 | STE-01 | PI13694 | Verified | Complete flange bolting at the gland steam exhausters. | A | P | James Beech | McD | 2019-11-27 | James Beech | Const |  |  | 2019-12-11 | James Beech
STE-01 | STE-01 | PI13695 | Verified | Remove wood under the gland steam exhausters. | A | M | Shane Crowe | McD | 2019-11-27 | Shane Crowe | Const | 2019-12-10 | Shane Crowe | 2019-12-18 | Shannon Scott
STE-01 | STE-01 | PI13696 | Verified | Install handles on valves at the gland steam exhausters. | A | P | James Beech | McD | 2019-11-27 | James Beech | Const |  |  | 2019-12-11 | James Beech
STE-01 | STE-01 | PI13697 | Verified | Install valve 1C-STE-V-9560 at the gland steam exhauster. | A | P | James Beech | McD | 2019-11-27 | James Beech | Const |  |  | 2019-12-11 | James Beech
STE-01 | STE-01 | PI13698 | Verified | 1C-STE-PV-9507 - flex too short. | A | E | Chris Colvin | McD | 2019-11-27 | Chris Colvin | Const | 2019-12-09 | Frank Lopez | 2020-01-22 | Albert Burge
STE-01 | STE-01 | PI13699 | Verified | Tighen flange bolts on line DDKW2713-6 - east end of turbine. | A | P | James Beech | McD | 2019-11-27 | James Beech | Const |  |  | 2019-12-11 | James Beech
STE-01 | STE-01 | PI13701 | Verified | 1C-STE-MOV-9630 - line resting on beam. | A | P | James Beech | McD | 2019-11-27 | James Beech | Const |  |  | 2019-12-11 | James Beech
STE-01 | STE-01 | PI13702 | Verified | Remove shipping bands on expansion joints & valves at the gland steam exhausters. | A | P | James Beech | McD | 2019-11-27 | James Beech | Const |  |  | 2019-12-11 | James Beech
STE-01 | STE-01 | PI13703 | Verified | 1C-STE-V-0022 not installed. | A | P | James Beech | McD | 2019-11-27 | James Beech | Const | 2019-12-12 | James Beech | 2019-12-13 | Blake Boudreaux
STE-01 | STE-01 | PI13704 | Verified | 1C-STE-P41-0030-01-202 - tighten u-bolt. | B | P | James Beech | McD | 2019-11-27 | James Beech | Const | 2020-02-10 | Tim Green | 2020-03-06 | Nelson Eichelberger
STE-01 | STE-01 | PI13705 | Verified | 1C-STE-0034 - lines needs support - ground level north. | C | P | Kelvin Cook | McD | 2019-11-27 | Kelvin Cook | Const | 2020-02-28 | Kelvin Cook | 2020-04-08 | Bernard Stasse
STE-01 | STE-01 | PI14171 | Verified | 1CSTEX0001, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STE-01 | STE-01 | PI14172 | Verified | 1CSTEX0007, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STE-01 | STE-01 | PI14173 | Verified | 1CSTEC0018, From termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-10 | Chris Colvin | 2019-12-12 | Mike Tabbert
STE-01 | STE-01 | PI14174 | Verified | 1CSTEX0001, From termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STE-01 | STE-01 | PI14175 | Verified | 1CSTEX0007, From termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STE-01 | STE-01 | PI14176 | Verified | 1CSTEC0013, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-10 | Chris Colvin | 2019-12-12 | Mike Tabbert
STE-01 | STE-01 | PI14177 | Verified | 1CSTEX0001, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STE-01 | STE-01 | PI14178 | Verified | 1CSTEX0007, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STE-01 | STE-01 | PI14672 | Verified | Complete tubing connection 1C-STE-PIT-9560 | A | I | James Tanner | McD | 2019-12-10 | James Tanner | Const | 2019-12-11 | James Tanner | 2019-12-12 | Michael Law
STE-01 | STE-01 | PI14712 | Verified | 1C-STE-PIT-9560-NEED TO SHRINK BOOT ON TUBE BUNDLE. | B | I | James Tanner | McD | 2019-12-11 | James Tanner | Const |  |  | 2019-12-13 | John Sullivan
STE-01 | STE-01 | PI17010 | Verified | Ground cables not secure, need to be reworked at STE-BLW-9560A; Gland Steam Exhauster A, STG mezzanine | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
STE-01 | STE-01 | PI17011 | Verified | Ground cables not secure, need to be reworked at STE-BLW-9560B; Gland Steam Exhauster B | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
STE-01 | STE-01 | PI17012 | Verified | STE-BLW-9560A; Gland Steam Exhauster A Motor not grounded, STG Bldg. mezzanine, Northeast side | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
STE-01 | STE-01 | PI17013 | Verified | STE-BLW-9560B; Gland Steam Exhauster A Motor not grounded, STG Bldg. mezzanine, Northeast side | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-03-11 | John Watts
STE-01 | STE-01 | PI17014 | Verified | Clean and paint STE-BLW-9560A; Gland Steam Exhauster A Motor and base plate, STG Bldg. mezzanine, Northeast side | C | X | Johnny Campbell | McD | 2020-02-18 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-07 | Bernard Stasse
STE-01 | STE-01 | PI17015 | Verified | Clean and paint STE-BLW-9560B; Gland Steam Exhauster B Motor and base plate, STG Bldg. mezzanine, Northeast side | C | X | Johnny Campbell | McD | 2020-02-18 | Johnny Campbell | Comm | 2020-04-01 | Johnny Campbell | 2020-04-07 | Bernard Stasse
STE-01 | STE-01 | PI17016 | Verified | Cover opening under STE-BLW-9560A; Gland Steam Exhauster A with grating, STG Bldg. mezzanine, Northeast side | C | C | Tim Gallegos | McD | 2020-02-18 | Tim Gallegos | Comm | 2020-04-23 | Tim Gallegos | 2020-06-03 | Nelson Eichelberger
STE-01 | STE-01 | PI17017 | Verified | Cover opening under STE-BLW-9560B; Gland Steam Exhauster B with grating, STG Bldg. mezzanine, Northeast side | C | C | Tim Gallegos | McD | 2020-02-18 | Tim Gallegos | Comm | 2020-04-23 | Tim Gallegos | 2020-06-03 | Nelson Eichelberger
STE-01 | STE-01 | PI17018 | Verified | STE-BLW-9560A&B; Gland Steam Exhauster A&B drain loop seal fill lines penetrate upward through grating and create trip hazard, South side of STE-BLW-9560B; Gland Steam Exhauster B, STG Bldg. mezzanine Northeast side | D | P | Michael Law | McD | 2020-02-18 | Michael Law | Comm | 2020-06-03 | Nelson Eichelberger | 2020-06-03 | Nelson Eichelberger
STE-01 | STE-01 | PI17019 | Verified | STE-BLW-9560A&B; Gland Steam Exhauster A&B outlet loop seal drain is not routed to floor drain as detailed on P&ID LK-1C-STE-ME-PID-0001, STG Bldg. mezzanine Northeast side, near hand rail | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-04-22 | James Beech | 2020-06-03 | Nelson Eichelberger
STE-01 | STE-01 | PI17020 | Verified | Vertical support baseplate anchor bolt nuts under flush and loose at 1C-HTS-CAB-0203, STG Bldg. mezzanine, South side and adjacent to Gland Steam Condenser | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-01 | James Beech | 2020-10-06 | Dave Goldak
STE-01 | STE-01 | PI17021 | Verified | Power cable conduit missing condolet cover at 1C-STE-PIT-9560, STG Bldg. mezzanine, South side and adjacent to Gland Steam Condenser | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-04-29 | Matt Gilmore | 2020-10-06 | Dave Goldak
STE-01 | STE-01 | PI17022 | Verified | Clean up area around Gland Steam Condenser and Gland Steam Exhauster skids | C | C | Johnny Campbell | McD | 2020-02-18 | Johnny Campbell | Comm | 2020-04-08 | Johnny Campbell | 2020-06-03 | Nelson Eichelberger
STE-01 | STE-01 | PI17023 | Verified | Under flush nut at rod hanger clamp bottom bolt, Gland Steam Exhauster A & B outlet 4 inch line, adjacent to 1C-STE-TI-0030, STG Bldg. mezzanine, Northeast side | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-05-01 | James Beech | 2020-06-03 | Nelson Eichelberger
STE-01 | STE-01 | PI17024 | Verified | STE-BLW-9560A; Gland Steam Exhauster A loop seal drain is not routed to drain at ground level, Line No. 0.75-1C-STE-0032 | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-04-22 | James Beech | 2020-06-03 | Nelson Eichelberger
STE-01 | STE-01 | PI17025 | Verified | STE-BLW-9560B; Gland Steam Exhauster B loop seal drain is not routed to drain at ground level, Line No. 0.75-1C-STE-0034 | C | P | James Beech | McD | 2020-02-18 | James Beech | Comm | 2020-04-22 | James Beech | 2020-06-03 | Nelson Eichelberger
STE-01 | STE-01 | PI17027 | Verified | Finish insulation on both sides of STE-MOV-9540, STG Bldg. operating deck, East end of STG | C | Q | Josh Koerner | PCI | 2020-02-18 | Josh Koerner | Comm | 2020-06-03 | Nelson Eichelberger | 2020-06-03 | Nelson Eichelberger
STE-01 | STE-01 | PI17028 | Verified | Power cable conduit missing condolet at STE-MOV-9540, STG Bldg. operating deck, East end of STG | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-04-29 | Matt Gilmore | 2021-04-26 | Keith Pollock
STE-01 | STE-01 | PI17029 | Verified | Power cable conduit to STE-MOV-9510 needs additional support, STG Bldg. operating deck, East end of STG | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-04-29 | Matt Gilmore | 2021-04-26 | Keith Pollock
STE-01 | STE-01 | PI17030 | Verified | Clean up STE-AOV-9512, STG Bldg. operating deck, East end of STG | C | C | Johnny Campbell | McD | 2020-02-18 | Johnny Campbell | Comm | 2020-04-08 | Johnny Campbell | 2020-10-06 | Dave Goldak
STE-01 | STE-01 | PI17031 | Verified | Power cable conduit condolet loose at STE-MOV-9505, STG Bldg. mezzanine, East side | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2020-06-03 | Nelson Eichelberger
STE-01 | STE-01 | PI17032 | Verified | Clean up STE-PV-9507, STG Bldg. mezzanine, East side | C | C | Johnny Campbell | McD | 2020-02-18 | Johnny Campbell | Comm | 2020-04-14 | Johnny Campbell | 2020-10-06 | Dave Goldak
STE-01 | STE-01 | PI17033 | Verified | Clean up STE-PV-9509, STG Bldg. mezzanine, East side | C | C | Johnny Campbell | McD | 2020-02-18 | Johnny Campbell | Comm | 2020-04-08 | Johnny Campbell | 2020-10-06 | Dave Goldak
STE-01 | STE-01 | PI17193 | Verified | Replace 3 TE's 1C-LPS-TE-0083 A/B/C | A | I | Gonzalo Pena | McD | 2020-02-25 | Gonzalo Pena | Const | 2020-03-07 | Tim Green | 2020-03-09 | Michael Law
STE-01 | STE-01 | PI17452 | Verified | 1C-STE-PV-9507: Instrumentation air tubing and support bent/damaged. Mezz deck. | B | I | James Beech | McD | 2020-03-02 | James Beech | Comm | 2020-03-07 | Tim Green | 2020-03-09 | Dave Goldak
STH-01 | STH-01 | PI01637 | Verified | Install low point drains for both motors | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Fred Michael | 2019-07-26 | Logan Holland
STH-01 | STH-01 | PI01638 | Verified | Install low point drains for heater | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Fred Michael | 2019-07-26 | Logan Holland
STH-01 | STH-01 | PI01639 | Verified | Install supports for conduits in oil skid enclosure | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Fred Michael | 2019-07-26 | Logan Holland
STH-01 | STH-01 | PI01640 | Verified | Grout skid enclosure | B | C | Johnny Campbell | McD | 2019-06-27 | Johnny Campbell | Const | 2019-07-25 | Jack Fields | 2019-09-04 | Stuart Herring
STH-01 | STH-01 | PI01641 | Verified | Clean and close for oil skid | B | M | Shane Crowe | McD | 2019-06-27 | Shane Crowe | Const | 2019-07-18 | Shane Crowe | 2019-09-04 | Stuart Herring
STH-01 | STH-01 | PI01642 | Verified | Finish installing pipe | A | P | Damon Turner | McD | 2019-06-27 | Damon Turner | Const | 2019-07-25 | Kelvin Cook | 2019-07-25 | Kelvin Cook
STH-01 | STH-01 | PI01643 | Verified | Ground motors to grid | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Fred Michael | 2019-07-19 | Logan Holland
STH-01 | STH-01 | PI01644 | Verified | External grounding on control conduits | A | E | Luis Cantu | McD | 2019-06-27 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-19 | Logan Holland
STH-01 | STH-01 | PI01645 | Verified | Seal conduits of 10-NJS-MCC-0004A and 4B | C | E | Chris Colvin | McD | 2019-06-27 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-04-21 | Michael Law
STH-01 | STH-01 | PI01662 | Verified | ISO 1C-STH-PD-P41-0010-01 is not installed | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-26 | Kelvin Cook
STH-01 | STH-01 | PI01663 | Verified | ISO 1C-STH-PD-P41-0010-01 is not installed | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-01 | Kelvin Cook
STH-01 | STH-01 | PI01664 | Verified | ISO DDKW27141-C sheet 3 pipe spool FAS-1 coming off from EHC oil unit 1C-STH-T-9200 has no slope | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI01665 | Verified | ISO DDKW27141-C sheet 5 pipe spool FAS-24 is not installed | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-01 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI01666 | Verified | ISO DDKW27141-C sheet 5 pipe spool FAS-23 is not installed | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI01667 | Verified | ISO DDKW27141-C sheet 6 pipe spool FAS-35 is not installed | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI01668 | Verified | ISO DDKW27141-C sheet 6 pipe spool FAS-36 is not installed | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI01669 | Verified | ISO DDKW27141-C sheet 6 pipe spool FAS-30 is not installed | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-01 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI01670 | Verified | ISO DDKW27141-C sheet 6 pipe spool FAS-31 is not installed | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-01 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI01671 | Verified | ISO DDKW27141-C sheet 7 line connecting to EHC oil unit 1C-STH-T-9200 the Oring gasket not installed | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI01672 | Verified | ISO DDKW27141-C sheet 9 line connecting to EHC oil unit 1C-STH-T-9200 Oring gasket is not intalled | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI01673 | Verified | ISO DDKW27141-C sheet 9 pipe spools FCD-24 is not installed | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-01 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI01674 | Verified | ISO DDKW27141-C sheet 9 pipe spools FCD-23 is not installed | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-01 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI01675 | Verified | ISO DDKW27141-C sheet 10 pipe spools FCD-30 is not installed | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-01 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI01676 | Verified | ISO DDKW27141-C sheet 10 pipe spools FCD-31 is not installed | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-01 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI01677 | Verified | Complete all Raceway | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-22 | Mike Tabbert
STH-01 | STH-01 | PI01678 | Verified | Complete all equipment ground connections to grid | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-06-28 | Mike Tabbert
STH-01 | STH-01 | PI01679 | Verified | Complete all raceway grounding | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-22 | Mike Tabbert
STH-01 | STH-01 | PI01680 | Verified | Complete all completion paperwork | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-26 | Ken Mundy | 2019-08-01 | Mike Tabbert
STH-01 | STH-01 | PI01681 | Verified | Confirm all cables are pulled in correct trays as per cable pull routing. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-07-22 | Mike Tabbert
STH-01 | STH-01 | PI01682 | Verified | Confirm cables are neat and orderly in cable trays, and secured to cable tray rungs, ty-raps tails trimmed. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-06-28 | Luis Cantu | 2019-08-01 | Mike Tabbert
STH-01 | STH-01 | PI01683 | Verified | Clean and close all Motor Control Buckets, and all equipment control panels. | A | E | Luis Cantu | McD | 2019-06-28 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-22 | Mike Tabbert
STH-01 | STH-01 | PI01684 | Verified | ISO DDKW27141-C sheet 3 pipe support T30-04H missing nuts | B | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-01 | Kelvin Cook
STH-01 | STH-01 | PI01685 | Verified | ISO DDKW27141-C sheet 3 pipe support T30-01H loose nuts, support not anchored. | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-01 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI01686 | Verified | ISO DDKW27141-C sheet 9 pipe support T30-32H missing bolts at clam | A | P | Damon Turner | McD | 2019-06-28 | Damon Turner | Const | 2019-07-01 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02244 | Verified | ISO DDKW27141-C sheet 5 pipe support T30-35H has loose bolts & nuts | A | P | Damon Turner | McD | 2019-07-10 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02245 | Verified | ISO DDKW27141-C sheet 5 pipe support T30-32H needs double nuts | A | P | Damon Turner | McD | 2019-07-10 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02246 | Verified | ISO DDKW27141-C sheet 5 pipe support T30-34H remove steel wire from pipe | A | P | Damon Turner | McD | 2019-07-10 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02247 | Verified | ISO DDKW27141-C sheet 5 pipe support T30-35 needs to be double nutted | A | P | Damon Turner | McD | 2019-07-10 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02248 | Verified | ISO DDKW27141-C sheet 5 pipe spool FAS-25 need steel wire remove from pipe | A | P | Damon Turner | McD | 2019-07-10 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02249 | Verified | ISO DDKW27141-C sheet 6 pipe support T30-40H 1 ft. too high Install support | A | P | Damon Turner | McD | 2019-07-10 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02250 | Verified | ISO DDKW27141-C sheet 6 pipe support T30-26H has loose nuts & touch up cold galv | A | P | Damon Turner | McD | 2019-07-10 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02251 | Verified | ISO DDKW27141-C sheet 6 pipe support T30-24H is out of square | A | P | Damon Turner | McD | 2019-07-10 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02252 | Verified | ISO DDKW27141-C sheet 9 pipe support T30-35H has loose bolts & nuts | A | P | Damon Turner | McD | 2019-07-10 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02253 | Verified | ISO DDKW27141-C sheet 9 pipe spool FCD-25 remove steel wire | A | P | Damon Turner | McD | 2019-07-10 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02254 | Verified | ISO DDKW27141-C sheet 10 pipe support T30-42H is not welded | A | P | Damon Turner | McD | 2019-07-10 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02255 | Verified | ISO DDKW27141-C sheet 10 pipe support T30-40H floating single nut 1 ft. too high | A | P | Damon Turner | McD | 2019-07-10 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02374 | Verified | DDKW27141 (155126-110101-01-SD-000117) Page 3/11 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STH-01 | STH-01 | PI02375 | Verified | DDKW27141 (155126-110101-01-SD-000117) Page 4/11 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STH-01 | STH-01 | PI02376 | Verified | DDKW27141 (155126-110101-01-SD-000117) Page 5/11 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STH-01 | STH-01 | PI02377 | Verified | DDKW27141 (155126-110101-01-SD-000117) Page 6/11 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STH-01 | STH-01 | PI02378 | Verified | DDKW27141 (155126-110101-01-SD-000117) Page 7/11 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STH-01 | STH-01 | PI02379 | Verified | DDKW27141 (155126-110101-01-SD-000117) Page 8/11 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STH-01 | STH-01 | PI02380 | Verified | DDKW27141 (155126-110101-01-SD-000117) Page 9/11 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STH-01 | STH-01 | PI02381 | Verified | DDKW27141 (155126-110101-01-SD-000117) Page 10/11 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STH-01 | STH-01 | PI02395 | Verified | ISO DDKW27141-C sheet 3 pipe support T30-02H needs to be painted. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02396 | Verified | ISO DDKW27141-C sheet 3 pipe support T30-05H verify support is floater or needs beam support | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02397 | Verified | ISO DDKW27141-C sheet 3 pipe support T30-18H is not installed. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02398 | Verified | ISO DDKW27141-C sheet 3 pipe support T30-13H out of square by 5/8". | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02399 | Verified | ISO DDKW27141-C sheet 4 pipe support T30-06H out of square by 1.5". | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02400 | Verified | ISO DDKW27141-C sheet 4 pipe support T30-11H is not installed. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02401 | Verified | ISO DDKW27141-C sheet 5 pipe support T30-33H is out of square & loose clamp. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02402 | Verified | ISO DDKW27141-C sheet 5 pipe support T30-21H out of plumb. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02403 | Verified | ISO DDKW27141-C sheet 5 pipe support T30-01H support not anchored. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02404 | Verified | ISO DDKW27141-C sheet 7 pipe support T30-01H is not anchored. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02405 | Verified | ISO DDKW27141-C sheet 7 pipe support T30-18H is not installed. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02406 | Verified | ISO DDKW27141-C sheet 8 pipe support T30-06H is out of square 5/8". | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02407 | Verified | ISO DDKW27141-C sheet 8 pipe support T30-11H is not installed. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02408 | Verified | ISO DDKW27141-C sheet 9 pipe support T30-33H loose clamp. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02409 | Verified | ISO DDKW27141-C sheet 9 pipe support T30-21H out of plumb. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02410 | Verified | ISO DDKW27141-C sheet 9 pipe support T30-22H not connected to steel beam. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02411 | Verified | ISO DDKW27141-C sheet 9 pipe support T30-01H support not anchored & loose clamp. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02412 | Verified | ISO DDKW27141-C sheet 10 pipe support T30-23H is not installed. | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-20 | Kelvin Cook
STH-01 | STH-01 | PI02416 | Verified | ISO DDKW27141-C sheet 3 complete installation of spool FAS-10 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02417 | Verified | ISO DDKW27141-C sheet 3 complete installation of spool FAS-08 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02418 | Verified | ISO DDKW27141-C sheet 3 support T#)-04H needs second set of nuts | B | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-01 | Kelvin Cook
STH-01 | STH-01 | PI02419 | Verified | ISO DDKW27141-C sheet 4 complete installation of spool FAS-14 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-08-02 | Kelvin Cook
STH-01 | STH-01 | PI02420 | Verified | ISO DDKW27141-C sheet 4 complete installation of spool FAS-16 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-08-02 | Kelvin Cook
STH-01 | STH-01 | PI02421 | Verified | ISO DDKW27141-C sheet 5 FAS-17 slope is incorrect, set the slope per the detail | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-08-02 | Kelvin Cook
STH-01 | STH-01 | PI02422 | Verified | ISO DDKW27141-C sheet 5 support T30-33H needs a second set of nuts | B | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-01 | Kelvin Cook
STH-01 | STH-01 | PI02423 | Verified | ISO DDKW27141-C sheet 5 support T30-32H needs a second set of nuts | B | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-01 | Kelvin Cook
STH-01 | STH-01 | PI02424 | Verified | ISO DDKW27141-C sheet 5 support T30-21H needs a second set of nuts | B | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-01 | Kelvin Cook
STH-01 | STH-01 | PI02425 | Verified | ISO DDKW27141-C sheet 5 complete installation of spool FAS-24 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02426 | Verified | ISO DDKW27141-C sheet 5 complete installation of spool FAS-25 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02427 | Verified | ISO DDKW27141-C sheet 5 spool FAS-22 has a sloping issue from 90 EL to the tee | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02428 | Verified | ISO DDKW27141-C sheet 6 complete installation of spool FAS-35 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02429 | Verified | ISO DDKW27141-C sheet 6 complete installation of spool FAS-36 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02430 | Verified | ISO DDKW27141-C sheet 6 complete installation of spool FAS-31 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02431 | Verified | ISO DDKW27141-C sheet 6 complete installation of spool FAS-32 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02432 | Verified | ISO DDKW27141-C sheet 6 spool FAS-35 E/W run has a slope issue set the slope per the detail | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02433 | Verified | ISO DDKW27141-C sheet 7 complete installation of spool FAS-35 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02434 | Verified | ISO DDKW27141-C sheet 7 FCD-01 slope is incorrect set the slope per the detail | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-29 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02435 | Verified | ISO DDKW27141-C sheet 7 complete installation of spool FCD-10 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-29 | Luis Cantu
STH-01 | STH-01 | PI02436 | Verified | ISO DDKW27141-C sheet 7 complete installation of spool FCD-08 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02437 | Verified | ISO DDKW27141-C sheet 7 spool FCD-08 looks like it was struck by scissor lift pipe needs to per fixed for proper slope | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-02 | Kelvin Cook
STH-01 | STH-01 | PI02438 | Verified | ISO DDKW27141-C sheet 8 complete installation of spool FCD-14 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02439 | Verified | ISO DDKW27141-C sheet 8 complete installation of spool FCD-16 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02440 | Verified | ISO DDKW27141-C sheet 9 complete installation of spool FCD-25 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02441 | Verified | ISO DDKW27141-C sheet 9 complete installation of spool FCD-24 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02442 | Verified | ISO DDKW27141-C sheet 10 complete installation of spool FCD-36 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02443 | Verified | ISO DDKW27141-C sheet 10 complete installation of spool FCD-35 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02444 | Verified | ISO DDKW27141-C sheet 10 complete installation of spool FCD-32 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02445 | Verified | ISO DDKW27141-C sheet 10 complete installation of spool FCD-31 to the block | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI02446 | Verified | ISO DDKW27141-C sheet 10 spool FCD-29 N/S run from 90 EL to tee has reverse slope set slope per the detail | A | P | Damon Turner | McD | 2019-07-20 | Damon Turner | Const |  |  | 2019-07-29 | Kelvin Cook
STH-01 | STH-01 | PI16899 | Verified | Clean and paint outside of EHC enclosure, STG Bldg. ground floor | C | X | Johnny Campbell | McD | 2020-02-18 | Johnny Campbell | Comm | 2020-04-24 | Johnny Campbell | 2020-04-24 | Mark Williamson
STH-01 | STH-01 | PI16900 | Verified | Remove tape from EHC enclosure, STG Bldg. ground floor | C | C | Johnny Campbell | McD | 2020-02-18 | Johnny Campbell | Comm | 2020-04-14 | Johnny Campbell | 2020-04-24 | Mark Williamson
STH-01 | STH-01 | PI16901 | Verified | Clean up inside of EHC enclosure, STG Bldg. ground floor | C | C | Johnny Campbell | McD | 2020-02-18 | Johnny Campbell | Comm | 2020-04-14 | Johnny Campbell | 2020-04-24 | Mark Williamson
STH-01 | STH-01 | PI16902 | Verified | Adjust Southwest EHC enclosure door handle, STG Bldg. ground floor | C | C | Tim Gallegos | McD | 2020-02-18 | Tim Gallegos | Comm | 2020-05-07 | Tim Gallegos | 2021-04-26 | Keith Pollock
STH-01 | STH-01 | PI16903 | Verified | EHC enclosure ground cable at Southeast corner needs to be reworked and protected | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2021-04-26 | Keith Pollock
STH-01 | STH-01 | PI16906 | Verified | Need extra support for EHC supply and return tubing at 1C-STS-CRV-900A; Combined Reheat Valve, STG Bldg. Steam Turbine East end | D | P | Kelvin Cook | McD | 2020-02-18 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-07 | Bernard Stasse
STH-01 | STH-01 | PI16907 | Verified | Need extra support for EHC supply and return tubing at 1C-STS-CRV-900B; Combined Reheat Valve, STG Bldg. Steam Turbine East end | D | P | Kelvin Cook | McD | 2020-02-18 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-07 | Bernard Stasse
STH-01 | STH-01 | PI16908 | Verified | Need extra support for EHC supply and return tubine at 1C-LPS-PV-9000; LP Induction Control Valve, STG Bldg. Steam Turbine East end | D | P | Kelvin Cook | McD | 2020-02-18 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-07 | Bernard Stasse
STH-01 | STH-01 | PI16909 | Verified | Need extra support for EHC supply and return tubine at 1C-HYV-PV-9000; LP Induction Stop Valve, STG Bldg. Steam Turbine East end | D | P | Kelvin Cook | McD | 2020-02-18 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-07 | Bernard Stasse
STH-01 | STH-01 | PI17362 | Verified | Test record for EHC oil to submit | C | M | Alan Joiner | McD | 2020-02-28 | Alan Joiner | Comm | 2020-05-28 | Alan Joiner | 2021-06-17 | John Watts
STH-01 | STH-01 | PI18122 | Verified | 1C-STH-FLT-9250 - EHC Air Breather (1C-STH-FLT-9250) is exhausted and needs to be replaced. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-20 | William Mitchell | 2020-07-28 | Keith Pollock
STL-01 | STL-01 | PI01751 | Verified | 1CSTLC0006, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-22 | Luis Cantu | 2019-07-22 | Mike Tabbert
STL-01 | STL-01 | PI01752 | Verified | 1CSTLC0007, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01753 | Verified | 1CSTLC0008, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01754 | Verified | 1CSTLC0014, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01755 | Verified | 1CSTLC0015, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01757 | Verified | 1CSTLC0021, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-26 | Dustin Futrell | 2019-07-31 | Mike Tabbert
STL-01 | STL-01 | PI01758 | Verified | 1CSTLC0022, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-26 | Dustin Futrell | 2019-07-31 | Mike Tabbert
STL-01 | STL-01 | PI01759 | Verified | 1CSTLC0023, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-26 | Dustin Futrell | 2019-07-31 | Mike Tabbert
STL-01 | STL-01 | PI01760 | Verified | 1CSTLC0025, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01761 | Verified | 1CSTLC0028, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01762 | Verified | 1CSTLC0031, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01763 | Verified | 1CSTLC0032, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01764 | Verified | 1CSTLC0033, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01765 | Verified | 1CSTLC0034, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const |  |  | 2019-07-08 | Luis Cantu
STL-01 | STL-01 | PI01766 | Verified | 1CSTLK0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const |  |  | 2019-07-08 | Luis Cantu
STL-01 | STL-01 | PI01767 | Verified | 1CSTLK0002, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01768 | Verified | 1CSTLK0003, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01769 | Verified | 1CSTLK0004, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01770 | Verified | 1CSTLK0005, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01771 | Verified | 1CSTLK0006, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01772 | Verified | 1CSTLK0007, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-17 | Michael Law | 2019-07-22 | Mike Tabbert
STL-01 | STL-01 | PI01773 | Verified | 1CSTLK0008, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-22 | Luis Cantu | 2019-07-22 | Mike Tabbert
STL-01 | STL-01 | PI01774 | Verified | 1CSTLK0009, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-17 | Michael Law | 2019-07-22 | Mike Tabbert
STL-01 | STL-01 | PI01775 | Verified | 1CSTLK0010, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-17 | Michael Law | 2019-07-22 | Mike Tabbert
STL-01 | STL-01 | PI01776 | Verified | 1CSTLK0012, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-26 | Dustin Futrell | 2019-07-31 | Mike Tabbert
STL-01 | STL-01 | PI01777 | Verified | 1CSTLL0001N1, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-19 | Mike Tabbert | 2019-07-19 | Mike Tabbert
STL-01 | STL-01 | PI01781 | Verified | 1CSTLL0001P1, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-19 | Mike Tabbert | 2019-07-19 | Mike Tabbert
STL-01 | STL-01 | PI01785 | Verified | 1CSTLL0005A, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01786 | Verified | 1CSTLL0005B, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01787 | Verified | 1CSTLL0005C, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01788 | Verified | 1CSTLL0005G, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01789 | Verified | 1CSTLL0006A, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01790 | Verified | 1CSTLL0006B, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01791 | Verified | 1CSTLL0006C, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01792 | Verified | 1CSTLL0006G, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01793 | Verified | 1CSTLX0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01794 | Verified | 1CSTLX0002, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01795 | Verified | 1CSTLX0003, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01796 | Verified | 1CSTLX0004, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01797 | Verified | 1CSTLX0005, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01798 | Verified | 1CSTLX0006, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01799 | Verified | 1CSTLX0007, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STL-01 | STL-01 | PI01800 | Verified | 1CSTSX0126, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-26 | Dustin Futrell | 2019-07-31 | Mike Tabbert
STL-01 | STL-01 | PI01801 | Verified | Complete all Raceway | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-22 | Mike Tabbert
STL-01 | STL-01 | PI01802 | Verified | Complete all equipment ground connections to grid | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-23 | Mike Tabbert
STL-01 | STL-01 | PI01803 | Verified | Complete all raceway grounding | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-22 | Mike Tabbert
STL-01 | STL-01 | PI01804 | Verified | Complete all completion paperwork | A | E | Dustin Futrell | McD | 2019-07-01 | Dustin Futrell | Const | 2019-07-30 | Luis Cantu | 2019-08-06 | Mike Tabbert
STL-01 | STL-01 | PI01805 | Verified | Confirm all cables are pulled in correct trays as per cable pull routing. | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-23 | Mike Tabbert
STL-01 | STL-01 | PI01807 | Verified | Clean and close all Motor Control Buckets, and all equipment control panels. | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-22 | Mike Tabbert
STL-01 | STL-01 | PI01808 | Verified | Install conduit for DC Lube Oil Motor | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-19 | Mike Tabbert
STL-01 | STL-01 | PI01809 | Verified | Install 1C-STL-PSL-9189A, 1C-STL-PSL-9189B and 1C-STL-PSL-9189C. | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-19 | Gonzalo Pena | 2019-07-22 | Mike Tabbert
STL-01 | STL-01 | PI01810 | Verified | Install Terminal Box 1C-GMS-TB-9040D at STG collector. | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-19 | Gonzalo Pena | 2019-07-29 | Mike Tabbert
STL-01 | STL-01 | PI01811 | Verified | Install Lube Oil Heaters in Lube Oil Storage Tank, 1C-STL-H-9100D, 9100C, 9100B and 9100A. | A | M | Shane Crowe | McD | 2019-07-01 | Shane Crowe | Const | 2019-07-10 | Michael Law | 2019-07-19 | Mike Tabbert
STL-01 | STL-01 | PI01812 | Verified | On Drawing DDKW27132-d sheet 4 on the 3 way valve connections missng bolts & gasket | B | P | James Beech | McD | 2019-07-01 | James Beech | Const |  |  | 2019-12-01 | Stuart Herring
STL-01 | STL-01 | PI01813 | Verified | On Drawing DDKW27132-d sheet 4 pipe support T00-01H has a loose ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01814 | Verified | On Drawing DDKW27132-d sheet 5 pipe support T00-02H needs grout | B | C | Johnny Campbell | McD | 2019-07-01 | Johnny Campbell | Const | 2019-07-25 | Johnny Campbell | 2019-08-08 | Kelvin Cook
STL-01 | STL-01 | PI01815 | Verified | On Drawing DDKW27132-d sheet 5 to duplex oil filter 1C-STL-FLT-9130A,B has loose bolts | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01816 | Verified | On Drawing DDKW27132-d sheet 5 on Nozzle table item H is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01817 | Verified | On Drawing DDKW27132-d sheet 5 on Nozzle table item G is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01818 | Verified | On Drawing DDKW27132-d sheet 5 on Nozzle table item F is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01819 | Verified | On Drawing DDKW27132-d sheet 5 on Nozzle table item E is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01820 | Verified | On Drawing DDKW27132-d sheet 6 Spool OFB-1-3 missing second set of nuts & cold galve the support | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01821 | Verified | On Drawing DDKW27132-d sheet 6 Spool OFHB-1 needs to be rolled up to make Field Weld | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01822 | Verified | On Drawing DDKW27132-d sheet 6 Spool OFB-1-1 grind excess weld from pipe | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01823 | Verified | On Drawing DDKW27132-d sheet 6 Spool OFB-1-1 loose nuts at ubolt & cold galve the support | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01824 | Verified | On Drawing DDKW27132-d sheet 6 Spool OFHB-1 flange connection from Duplex oil filter 1C-STL-FLT-9130A,B needs to bolt up & install gasket. | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01825 | Verified | On Drawing DDKW27132-d sheet 7 on spool OFHSB-1 remove trash bag from support & cold galve support | C | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01826 | Verified | On Drawing DDKW27132-d sheet 7 on spool OFHB-5 cont on drg 5 point b remove fire blanket | B | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01827 | Verified | On Drawing DDKW27132-d sheet 7 on spool OFHB-5 just off cont on drg 5 point b cold galve support & straighthen up ubolt. | B | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01828 | Verified | On Drawing DDKW27132-d sheet 8 at orifice 1C-STL-FO-9181 commissioining to install after flush is complete | B | P | Stuart Herring | McD | 2019-07-01 | Stuart Herring | Comm |  |  | 2019-12-01 | Stuart Herring
STL-01 | STL-01 | PI01829 | Verified | On Drawing DDKW27132-d sheet 8 flanges connecting the orifice plate has no gasket & no bolts | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01854 | Verified | On Drawing DDKW27132-d sheet 6 pipe support on spool OFB-1-1 has loose ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01855 | Verified | On Drawing DDKW27132-d sheet 6 field weld not made yet on 4SN 10A | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01856 | Verified | On Drawing DDKW27132-d sheet 6 pipe support on Spool OFB-1-2 has loose nut | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01857 | Verified | On Drawing DDKW27132-d 4 through 20 remove all tie wire tape | B | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01858 | Verified | On Drawing DDKW27139-f sheet 4 is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01859 | Verified | On Drawing DDKW27139-f sheet 4 has no supports | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-08-05 | Kelvin Cook
STL-01 | STL-01 | PI01860 | Verified | On Drawing DDKW27139-f sheet 4 spool OFB-7-1 is making contact with generator | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01861 | Verified | On Drawing DDKW27139-f sheet 5 orifice 1C-STL-FO-9173 to be installed after commissioning flush is complete | C | P | Stuart Herring | McD | 2019-07-01 | Stuart Herring | Const |  |  | 2019-12-01 | Stuart Herring
STL-01 | STL-01 | PI01862 | Verified | On Drawing DDKW27139-f sheet 5 orifice 1C-STL-FO-9172 to be installed after commissioning flush is complete | C | P | Stuart Herring | McD | 2019-07-01 | Stuart Herring | Const |  |  | 2019-12-01 | Stuart Herring
STL-01 | STL-01 | PI01863 | Verified | On Drawing DDKW27139-f sheet 5 orifice 1C-STL-FO-9174 to be installed after commissioning flush is complete | C | P | Stuart Herring | McD | 2019-07-01 | Stuart Herring | Const |  |  | 2019-12-01 | Stuart Herring
STL-01 | STL-01 | PI01864 | Verified | On Drawing DDKW27139-f sheet 5 orifice 1C-STL-FO-9175 to be installed after commissioning flush is complete | C | P | Stuart Herring | McD | 2019-07-01 | Stuart Herring | Const |  |  | 2019-12-01 | Stuart Herring
STL-01 | STL-01 | PI01865 | Verified | On Drawing DDKW27139-f sheet 6 line from NO 4 BGR to the NO 4 oil sight is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01866 | Verified | On Drawing DDKW27139-f sheet 6 spool ODSD-4-1 from NO 4 oil sight is not welded | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01867 | Verified | On Drawing DDKW27139-f sheet 7 orifice 1C-STL-FO-9184 to be installed after commissioning flush is complete | C | P | Stuart Herring | McD | 2019-07-01 | Stuart Herring | Const |  |  | 2019-12-01 | Albert Burge
STL-01 | STL-01 | PI01868 | Verified | On Drawing DDKW27139-f sheet 7 flange for orifice place is tighten unevenly showing gap at racer flange | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01869 | Verified | On Drawing DDKW27139-f sheet 8 orifice 1C-STL-FO-9186 to be installed after commissioning flush is complete | C | P | Stuart Herring | McD | 2019-07-01 | Stuart Herring | Const |  |  | 2019-12-01 | Stuart Herring
STL-01 | STL-01 | PI01870 | Verified | On Drawing DDKW27139-f sheet 9 on spool OSV-A-2 from Duplex oil filter A remove wood, additional support is required. | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01871 | Verified | On Drawing DDKW27139-f sheet 9 on spool OSV-A-2 from Duplex oil filter A missing ubolts | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01872 | Verified | On Drawing DDKW27139-f sheet 9 on spool OSV-B-2 from duplex oil filter B to main oil tank remove wood | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01873 | Verified | On Drawing DDKW27139-f sheet 9 on spool OSV-B-2 from duplex oil filter B to main oil tank missing ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01874 | Verified | On Drawing DDKW27139-f sheet 10 on spool OCVS-B-1 there is a loose ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01875 | Verified | On Drawing DDKW27139-f sheet 10 on spool OCVS-B-2 there is a loose ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01876 | Verified | On Drawing DDKW27139-f sheet 10 on spool OCVS-B-2 before the elbow pipe needs a support | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01877 | Verified | On Drawing DDKW27139-f sheet 10 on spool OCVS-A-1 after the elbow pipe needs a support | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01878 | Verified | On Drawing DDKW27139-f sheet 10 on spool OCVS-A-2 there is a loose ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01879 | Verified | On Drawing DDKW27139-f sheet 4 no flange at to steady support BRG | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01971 | Verified | Reilief valve coming off the conditioner skid need ti be piped down. | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-08-08 | Stuart Herring
STL-01 | STL-01 | PI01972 | Verified | Install two blind flanges coming off conditioner skid | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-08-08 | Stuart Herring
STL-01 | STL-01 | PI01973 | Verified | Finish tubing Duplex Differential Gauge | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-22 | Gonzalo Pena | 2019-08-08 | Stuart Herring
STL-01 | STL-01 | PI01974 | Verified | Bottom flange missing hardware near conditioner skid | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-08-08 | Stuart Herring
STL-01 | STL-01 | PI01975 | Verified | Pipe support still has rigging on it | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-08-08 | Stuart Herring
STL-01 | STL-01 | PI01976 | Verified | Missing hardware on the three way valve near conditoner skid | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-25 | Kelvin Cook | 2019-07-25 | Kelvin Cook
STL-01 | STL-01 | PI01977 | Verified | Grout Duplex Oil Filter | A | C | Johnny Campbell | McD | 2019-07-01 | Johnny Campbell | Const | 2019-07-19 | Johnny Campbell | 2019-07-22 | Stuart Herring
STL-01 | STL-01 | PI01853 | Verified | On Drawing DDKW27132-d sheet 19 not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01852 | Verified | On Drawing DDKW27132-d sheet 18 flange just off item S on the nozzle table is missing gasket & bolts | B | P | James Beech | McD | 2019-07-01 | James Beech | Const |  |  | 2019-11-23 | Kelvin Cook
STL-01 | STL-01 | PI01851 | Verified | On Drawing DDKW27132-d sheet 18 flange from NO 6 BRG on spool ODB-6-1 is missing gasket & bolts | B | P | James Beech | McD | 2019-07-01 | James Beech | Const |  |  | 2019-11-23 | Kelvin Cook
STL-01 | STL-01 | PI01850 | Verified | On Drawing DDKW27132-d sheet 14 spool ODB-3-1 is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01849 | Verified | On Drawing DDKW27132-d sheet 12 on spool G-OFB-3-2 flange is missing bolts and gasket | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01848 | Verified | On Drawing DDKW27132-d sheet 12 on split pipe G-OFB-3-1 flange is not sealed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01847 | Verified | On Drawing DDKW27132-d sheet 11 spool OFB-6-3 ss wrap required & worm gear clamp | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01846 | Verified | On Drawing DDKW27132-d sheet 11 just off the reducer on spool OFB-6-5 ss wrap required & worm gear clamp | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01845 | Verified | On Drawing DDKW27132-d sheet 11 second flange connection on spool OFB-6-5 it has no gasket & no bolts | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-29 | Kelvin Cook | 2019-08-02 | Kelvin Cook
STL-01 | STL-01 | PI01844 | Verified | On Drawing DDKW27132-d sheet 11 flange for orifice 1C-STL-FO-9187 is missing bolts & gaskets | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-08-02 | Kelvin Cook
STL-01 | STL-01 | PI01843 | Verified | On Drawing DDKW27132-d sheet 11 orifice 1C-STL-FO-9187 to be installed after commissioning flush is complete | C | P | Stuart Herring | McD | 2019-07-01 | Stuart Herring | Comm |  |  | 2019-12-01 | Stuart Herring
STL-01 | STL-01 | PI01842 | Verified | On Drawing DDKW27132-d sheet 10 flange connection just of orifice 1C-STL-FO-9182 is missing bolts & gaskets | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01841 | Verified | On Drawing DDKW27132-d sheet 10 flange for orifice 1C-STL-FO-9182 is missing bolts & gaskets | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01840 | Verified | On Drawing DDKW27132-d sheet 10 orifice 1C-STL-FO-9182 to be installed after commissioning flush is complete | B | P | Stuart Herring | McD | 2019-07-01 | Stuart Herring | Comm |  |  | 2019-12-01 | Stuart Herring
STL-01 | STL-01 | PI01839 | Verified | On Drawing DDKW27132-d sheet 10 spool OFB-4-1 just of pipe support T00-15H missing ubolt & cold galve support | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01838 | Verified | On Drawing DDKW27132-d sheet 10 spool OFB-5-3 just off drain valve remove rope & tie wire | B | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01837 | Verified | On Drawing DDKW27132-d sheet 10 the blind flange on spool OFB-5-2 is not installed | B | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-08-26 | Damon Turner | 2019-09-18 | Kelvin Cook
STL-01 | STL-01 | PI01836 | Verified | On Drawing DDKW27132-d sheet 10 pipe supoort T00-15H is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01835 | Verified | On Drawing DDKW27132-d sheet 10 flange connecting spools OFB-5-1 & OFB-5-2 orifice installed wrong bolts too short. | B | P | Danny Pase | McD | 2019-07-01 | Danny Pase | Const |  |  | 2019-07-29 | Kelvin Cook
STL-01 | STL-01 | PI01834 | Verified | On Drawing DDKW27132-d sheet 10 orifice 1C-STL-FO-9185 to be installed after commissioning flush is complete | C | P | Stuart Herring | McD | 2019-07-01 | Stuart Herring | Comm |  |  | 2019-12-01 | Stuart Herring
STL-01 | STL-01 | PI01833 | Verified | On Drawing DDKW27132-d sheet 9 on Nozzle table item K is not complete | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-08-02 | Kelvin Cook
STL-01 | STL-01 | PI01832 | Verified | On Drawing DDKW27132-d sheet 9 Spool OTGB-7 connecting OTGB-1 Field weld is not made | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01831 | Verified | On Drawing DDKW27132-d sheet 8 on Spool OFB-3-4 support missing second set of nuts at ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01830 | Verified | On Drawing DDKW27132-d sheet 8 on Spool OFB-3-3 going to NO 3 BRG weld is imcomplete | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STL-01 | STL-01 | PI01978 | Verified | Missing drain, nipple and cap on valve 1C-STL-V-9123A and !C-STL-V-6123B | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-08-08 | Stuart Herring
STL-01 | STL-01 | PI01979 | Verified | Clean and close on Main Lube Oil Tank after touch up paint | A | M | Shane Crowe | McD | 2019-07-01 | Shane Crowe | Const | 2019-08-05 | Joshua Sturgeon | 2019-08-05 | Joshua Sturgeon
STL-01 | STL-01 | PI02000 | Verified | Oil drain from No. 3 bearing Gauge is missing | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-22 | Stuart Herring
STL-01 | STL-01 | PI02001 | Verified | Line going to the No. 5 bearing missing a flange | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-08-08 | Stuart Herring
STL-01 | STL-01 | PI02002 | Verified | No. 4 bearing Oil side pipe missing support | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-08-08 | Stuart Herring
STL-01 | STL-01 | PI02003 | Verified | Hardware missing on No.6 bearing piping | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-08-08 | Stuart Herring
STL-01 | STL-01 | PI02018 | Verified | STL-RAK-9055 grout instrument stand | C | C | Johnny Campbell | McD | 2019-07-01 | Johnny Campbell | Const | 2019-07-30 | Johnny Campbell | 2019-08-08 | Shannon Scott
STL-01 | STL-01 | PI02019 | Verified | RAK-9055 to strap the conduit | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-19 | Ken Mundy | 2019-07-23 | Shannon Scott
STL-01 | STL-01 | PI02020 | Verified | PT-9191 pull and term the cables | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const |  |  | 2019-07-31 | Mike Tabbert
STL-01 | STL-01 | PI02021 | Verified | PT-9191 grout instrument stand | C | C | Johnny Campbell | McD | 2019-07-01 | Johnny Campbell | Const | 2019-07-31 | Jack Fields | 2019-08-08 | Shannon Scott
STL-01 | STL-01 | PI02024 | Verified | RAK-9050 conduit and cable not installed | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const |  |  | 2019-07-31 | Mike Tabbert
STL-01 | STL-01 | PI02025 | Verified | RAK-9050 tubing not installed | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-19 | Gonzalo Pena | 2019-07-26 | Gonzalo Pena
STL-01 | STL-01 | PI02027 | Verified | TEW-9172 to 9175 tubing not installed | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-02 | Gonzalo Pena | 2019-08-12 | Albert Burge
STL-01 | STL-01 | PI02028 | Verified | CP-9100 to remove tie wraps and support all flex conduits | B | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-26 | Ken Mundy | 2019-07-31 | Shannon Scott
STL-01 | STL-01 | PI02029 | Verified | TI-9121 to rate dial indicator | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-03 | Gonzalo Pena | 2019-08-26 | Albert Burge
STL-01 | STL-01 | PI02030 | Verified | CP-9100 need tag | C | E | Dustin Futrell | McD | 2019-07-01 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
STL-01 | STL-01 | PI02031 | Verified | Need general houskeeping on LO tank area | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-23 | Mike Tabbert
STL-01 | STL-01 | PI02032 | Verified | Put tags on LO tank heaters | C | M | Joshua Sturgeon | McD | 2019-07-01 | Joshua Sturgeon | Const | 2019-07-31 | Joshua Sturgeon | 2019-08-19 | Shannon Scott
STL-01 | STL-01 | PI02033 | Verified | 9100B Loose seal on ground cable to fix on motor terminal box | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-26 | Ken Mundy | 2019-07-31 | Shannon Scott
STL-01 | STL-01 | PI02034 | Verified | 9100A missing rubber cover for greasing motor A | C | E | Dustin Futrell | McD | 2019-07-01 | Dustin Futrell | Const | 2019-09-06 | Mike Tabbert | 2019-09-11 | Shannon Scott
STL-01 | STL-01 | PI02035 | Verified | System wide all thermocouple check for ring lugs. To remove | B | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-19 | Fred Michael | 2019-07-19 | Fred Michael
STL-01 | STL-01 | PI02036 | Verified | System wide all motor terminal boxes to check for holes to seal with silicon | B | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-19 | Fred Michael | 2019-07-19 | Fred Michael
STL-01 | STL-01 | PI02037 | Verified | M-9140A/B need to motor terminal kits | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-23 | Mike Tabbert
STL-01 | STL-01 | PI02038 | Verified | CP-9100 need additional tag on the panel itself | C | E | Dustin Futrell | McD | 2019-07-01 | Dustin Futrell | Const | 2019-09-11 | Shannon Scott | 2019-09-11 | Shannon Scott
STL-01 | STL-01 | PI02039 | Verified | Tidy up LO tank skid grounding . Torque the grounding | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-08-02 | Fred Michael
STL-01 | STL-01 | PI02040 | Verified | Tidy up LO conditioner skid grounding . Torque the grounding | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-08-02 | Fred Michael
STL-01 | STL-01 | PI02041 | Verified | 1CSTLC0025-4 termination is loose (at LO conditioner skid panel) | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-11 | Shannon Scott
STL-01 | STL-01 | PI02042 | Verified | Finish the grounding on heat exchangers | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-22 | Luis Cantu | 2019-08-05 | Mike Tabbert
STL-01 | STL-01 | PI02043 | Verified | 1C-STL-PDIT-9131 set screw to tightened | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-03 | Gonzalo Pena | 2019-08-02 | Fred Michael
STL-01 | STL-01 | PI02044 | Verified | 1C-STL-PDIT-9131 tubing to complete | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-22 | Gonzalo Pena | 2019-08-02 | Fred Michael
STL-01 | STL-01 | PI02045 | Verified | Seal up conduits, housekeeping on the panel at STL main PDC panel | B | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-19 | Ken Mundy | 2019-07-23 | Shannon Scott
STL-01 | STL-01 | PI02046 | Verified | Protective covers to install at STL panel at PDC | B | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-19 | Ken Mundy | 2019-07-23 | Shannon Scott
STL-01 | STL-01 | PI02081 | Verified | Handrail bent on stairway leading up to Lube Oil tank top. | C | C | Robert Risher | McD | 2019-07-02 | Robert Risher | Const | 2019-07-26 | Tim Gallegos | 2019-08-08 | Dave Goldak
STL-01 | STL-01 | PI02082 | Verified | Line# 1C-STL-0041-15D1-PP-1.0 not installed | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-31 | Shannon Scott
STL-01 | STL-01 | PI02083 | Verified | Line# 1C-STL-0042-15D1-PP-1.0 not installed | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-31 | Shannon Scott
STL-01 | STL-01 | PI02085 | Verified | Line# 1C-STL-0010-15D1-FP-2-ET cap not installed at fill location | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-31 | Shannon Scott
STL-01 | STL-01 | PI02086 | Verified | Cold galv. all supports. | C | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-08-29 | Shannon Scott
STL-01 | STL-01 | PI02087 | Verified | Line# 1C-STL-0015-15D1-PP-1.0 Screen not installed | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-31 | Shannon Scott
STL-01 | STL-01 | PI02088 | Verified | Line# 1C-STL-0021-15D1-PP-1.0 Valve 9115 not ON McDermott P&ID | C | P | Charles Worthington | McD | 2019-07-02 | Charles Worthington | Const | 2020-06-10 | Charles Worthington | 2020-07-24 | Nelson Eichelberger
STL-01 | STL-01 | PI02089 | Verified | Oil inlet has no blind flange installed (LO-01) | B | P | James Beech | McD | 2019-07-02 | James Beech | Const |  |  | 2019-12-01 | Stuart Herring
STL-01 | STL-01 | PI02090 | Verified | Oil disharge has no blind flange installed (LO-02) | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-29 | Damon Turner | 2019-07-31 | Shannon Scott
STL-01 | STL-01 | PI02091 | Verified | Tag all valves and equipment | C | P | James Beech | McD | 2019-07-02 | James Beech | Const | 2020-05-07 | James Beech | 2021-01-22 | Eric Policarpio
STL-01 | STL-01 | PI02092 | Verified | Verify orientation of sight glasses | A | P | Kelvin Cook | McD | 2019-07-02 | Kelvin Cook | Const | 2019-07-30 | Kelvin Cook | 2019-08-02 | Dave Goldak
STL-01 | STL-01 | PI02093 | Verified | Remove scaffolding, plumb piping and install u-bolts | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-31 | Shannon Scott
STL-01 | STL-01 | PI02094 | Verified | Drain valves on filter skid not lockable | D | P | Michael Law | McD | 2019-07-02 | Michael Law | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
STL-01 | STL-01 | PI02095 | Verified | TP-OD-10 Teflon tape on threads and union installed backwards | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-08-01 | Damon Turner | 2019-08-16 | Dave Goldak
STL-01 | STL-01 | PI02096 | Verified | All areas and skids pertaining to this system need to be cleaned | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-08 | Michael Law | 2019-08-15 | Dave Goldak
STL-01 | STL-01 | PI02097 | Verified | SRV-9164 missing discharge piping | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-31 | Shannon Scott
STL-01 | STL-01 | PI02098 | Verified | SKD-9160 needs grout form removed | C | C | Johnny Campbell | McD | 2019-07-02 | Johnny Campbell | Const | 2019-07-31 | Jack Fields | 2019-08-08 | Dave Goldak
STL-01 | STL-01 | PI02099 | Verified | TP-OD-09 not connected | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-31 | Shannon Scott
STL-01 | STL-01 | PI02100 | Verified | OD-11 drain line not installed | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-08-05 | Damon Turner | 2019-08-16 | Dave Goldak
STL-01 | STL-01 | PI02101 | Verified | Fix hillside washers on u-bolts in containment area around lube oil tank | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-31 | Shannon Scott
STL-01 | STL-01 | PI02102 | Verified | Line# 1C-STL-0010-15D1-PP-1.0 needs support | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-08-20 | Damon Turner | 2019-08-29 | Nelson Eichelberger
STL-01 | STL-01 | PI02103 | Verified | Sample point at V-9104 lands outside lube oil containment area | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-31 | Shannon Scott
STL-01 | STL-01 | PI02382 | Verified | LK-1C-STL-PD-P41-0010-04 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-19 | Damon Turner | 2019-07-19 | Tom Noble
STL-01 | STL-01 | PI02383 | Verified | LK-1C-STL-PD-P41-0041-04 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-19 | Damon Turner | 2019-07-19 | Tom Noble
STL-01 | STL-01 | PI02384 | Verified | LK-1C-STL-PD-P41-0042-01 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-19 | Damon Turner | 2019-07-19 | Tom Noble
STL-01 | STL-01 | PI02385 | Verified | LK-1C-STL-PD-P41-0021-01 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STL-01 | STL-01 | PI02386 | Verified | DDKW27132 (155126-110101-01-SD-00108) Page 12/20 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STL-01 | STL-01 | PI02387 | Verified | DDKW27132 (155126-110101-01-SD-00108) Page 19/20 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STL-01 | STL-01 | PI02388 | Verified | DDKW27139 (155126-110101-01-SD-00115) Page 11/13 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STL-01 | STL-01 | PI04243 | Verified | Install low point drains in conduit at rack 1C-STL-RAK-9050. | C | E | Dustin Futrell | McD | 2019-08-14 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-06 | Fred Michael
STL-01 | STL-01 | PI14593 | Verified | Rework 1C Lube Oil Conditioning Skid ground cable at NW side of skid, currently a trip hazard | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-04-14 | Chris Colvin | 2020-05-28 | Dave Goldak
STL-01 | STL-01 | PI14594 | Verified | Clean up 1C Lube Oil Conditioning Skid | C | C | Brooks Baker | McD | 2019-12-07 | Brooks Baker | Comm | 2020-04-09 | Brooks Baker | 2020-04-24 | Mark Williamson
STL-01 | STL-01 | PI14595 | Verified | Rework ground cable at NE corner of 1C STG Main Oil Tank, currently a trip hazard | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14596 | Verified | Remove tape signs and old tags from sides of 1C STG Main Oil Tank | C | C | Johnny Campbell | McD | 2019-12-07 | Johnny Campbell | Comm | 2020-04-30 | Johnny Campbell | 2020-05-28 | Dave Goldak
STL-01 | STL-01 | PI14597 | Verified | Paint piping throughout system as necessary | C | X | Jerry Smith | McD | 2019-12-07 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14598 | Verified | Install insulation on 1C STG Oil Mist Eliminator drain piping, Line No.'s 1-1C-STL-0016 and 1-1C-STL-0017 | C | Q | Richard McSpadden | PCI | 2019-12-07 | Richard McSpadden | Comm | 2020-08-07 | Richard McSpadden | 2021-02-24 | John Watts
STL-01 | STL-01 | PI14599 | Verified | Install insulation on 1C STG Oil Mist Eliminator drain piping, Line No. 1-1C-STL-0010 | C | Q | Richard McSpadden | PCI | 2019-12-07 | Richard McSpadden | Comm | 2020-08-07 | Richard McSpadden | 2020-08-20 | Nelson Eichelberger
STL-01 | STL-01 | PI14600 | Verified | Clean up top deck of 1C STG Main Oil Tank | C | C | Johnny Campbell | McD | 2019-12-07 | Johnny Campbell | Comm | 2020-02-20 | Alan Huntsman | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14601 | Verified | Ensure Main Oil Pump A motor cable termination box has a gasket | C | E | Jonathan Donham | McD | 2019-12-07 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14602 | Verified | Missing washers on Main Oil Pump B motor cable termination box | C | E | Jonathan Donham | McD | 2019-12-07 | Jonathan Donham | Comm | 2020-03-02 | Jonathan Donham | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14603 | Verified | Missing washers on Main Oil Pump A motor cable termination box | C | E | Jonathan Donham | McD | 2019-12-07 | Jonathan Donham | Comm | 2020-03-02 | Jonathan Donham | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14604 | Verified | Per Toshiba Drawing 2KW010183, 1C-STL-V-9115;1C STG Main Oil Tank Drain Valve should be locked closed | C | P | Alan Joiner | McD | 2019-12-07 | Alan Joiner | Comm | 2020-05-07 | Alan Joiner | 2020-05-28 | Dave Goldak
STL-01 | STL-01 | PI14605 | Verified | Per Toshiba Drawing 2KW010183, 1C-STL-V-9103; STG Lube Oil Conditioner New Oil Inlet Valve should be locked closed | C | P | Alan Joiner | McD | 2019-12-07 | Alan Joiner | Comm | 2020-05-07 | Alan Joiner | 2020-05-28 | Dave Goldak
STL-01 | STL-01 | PI14606 | Verified | Per Toshiba Drawing 2KW010183, 1C-STL-V-9106; STG Lube Oil Conditioner Sample Line Oil Discharge Valve should be locked closed | C | P | Alan Joiner | McD | 2019-12-07 | Alan Joiner | Comm | 2020-05-07 | Alan Joiner | 2020-05-28 | Dave Goldak
STL-01 | STL-01 | PI14607 | Verified | 1C-STL-TT-9161; Lube Oil Conditioner Heater Temperature Transmitter tag is incorrect, stamped as 1C-STL-TS-9161 | C | P | Gonzalo Pena | McD | 2019-12-07 | Gonzalo Pena | Comm | 2020-01-31 | Gonzalo Pena | 2020-02-06 | Dave Goldak
STL-01 | STL-01 | PI14608 | Verified | 1C-STL-V-9170; Lube Oil Conditioner Oil Pan Drain Valve needs plug | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-03-26 | John Watts
STL-01 | STL-01 | PI14609 | Verified | 1C-STL-V-9164; Lube Oil Conditioner PT Isolation Valve missing tag | C | P | Tim Green | McD | 2019-12-07 | Tim Green | Comm | 2020-06-04 | Tim Green | 2020-07-31 | Nelson Eichelberger
STL-01 | STL-01 | PI14610 | Verified | Lube Oil Conditioner Coalescing Filter lid swing arm bolt needs to be cleaned and protective coating applied | C | P | Tim Green | McD | 2019-12-07 | Tim Green | Comm | 2020-06-02 | Tim Green | 2020-07-31 | Nelson Eichelberger
STL-01 | STL-01 | PI14611 | Verified | Remove carbon contamination from 10" SS Lube Oil discharge from 1C Duplex Oil Filter A&B to 22" supply and return header | C | X | Johnny Campbell | McD | 2019-12-07 | Johnny Campbell | Comm | 2020-04-09 | Johnny Campbell | 2020-04-24 | Mark Williamson
STL-01 | STL-01 | PI14612 | Verified | U-Bolts cocked need to be straightened up at 8" Supply/Return to #1 Bearing, STG Bldg mezzanine, E side | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14613 | Verified | Flange bolts too long at 1C-STL-FO-9174; Flow Orifice, STG Operating Deck, between #1 and #2 Bearing | C | P | Kelvin Cook | McD | 2019-12-07 | Kelvin Cook | Comm | 2020-02-10 | Kelvin Cook | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14614 | Verified | Flange bolts too long at 1C-STL-FO-9173; Flow Orifice, STG Operating Deck, between #1 and #2 Bearing | C | P | Kelvin Cook | McD | 2019-12-07 | Kelvin Cook | Comm | 2020-02-10 | Kelvin Cook | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14615 | Verified | Flange bolts too long at 1C-STL-FO-9172; Flow Orifice, STG Operating Deck, between #1 and #2 Bearing | C | P | Kelvin Cook | McD | 2019-12-07 | Kelvin Cook | Comm | 2020-02-10 | Kelvin Cook | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14616 | Verified | Wrong size U-Bolt nuts at 20" Supply/Discharge header, STG Bldg. Mezzanine, N side | C | P | Tim Green | McD | 2019-12-07 | Tim Green | Comm | 2020-06-03 | Nelson Eichelberger | 2020-06-03 | Nelson Eichelberger
STL-01 | STL-01 | PI14617 | Verified | Flange Bolts too long at Main Oil Cooler A&B drain lines | C | P | Kelvin Cook | McD | 2019-12-07 | Kelvin Cook | Comm | 2020-02-10 | Kelvin Cook | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14618 | Verified | Lube oil temperature instrumentation downstream of Main Oil Cooler Transfer Valve is not installed per Toshiba drawing #1KT004145, 1C-STL-TI-0129 and 1C-STL-TE-0129B are swapped out | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-05-21 | James Beech | 2020-05-28 | Dave Goldak
STL-01 | STL-01 | PI14619 | Verified | Tighten U-Bolts at 1" line to 1C-STL-FG-912A; Sighgt Glass, above Main Oil Cooler A&B | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14620 | Verified | Main Oil Cooler Transfer Valve handle is broken | B | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-03-12 | Tim Green | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14621 | Verified | No clearance between top of STG Lube Oil Containment wall and Duplex Oil Filter switching handle, lack of clearance creates pinch point | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-05-27 | James Beech | 2020-07-31 | Nelson Eichelberger
STL-01 | STL-01 | PI14622 | Verified | Duplex Oil Filter skid ground cable is disconnected | B | E | Jonathan Donham | McD | 2019-12-07 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14623 | Verified | 1C-STL-V-9132A and 1C-STL-V-9132B; Duplex Oil Filter vent valves are not lockable, all valves are required to be lockable per contract EPC A-3 4.3.1 | D | P | Kevin Leppert | McD | 2019-12-07 | Kevin Leppert | Comm | 2020-02-25 | Kevin Leppert | 2020-02-25 | John Watts
STL-01 | STL-01 | PI14624 | Verified | Turn 1C-STL-FG-9132A and 1C-STL-FG-9132B; Duplex Oil Filter vent site glasses to the East for operator observation, currently facing down | D | P | Tim Green | McD | 2019-12-07 | Tim Green | Comm | 2020-07-24 | Tim Gallegos | 2020-11-25 | Dave Goldak
STL-01 | STL-01 | PI14625 | Verified | Turn 1C-STL-FG-9122A and 1C-STL-FG-9122B; Main Oil Cooler vent site glasses to the North for operator observation, currently facing down | D | P | Tim Green | McD | 2019-12-07 | Tim Green | Comm | 2020-07-24 | Tim Gallegos | 2020-11-25 | Dave Goldak
STL-01 | STL-01 | PI14626 | Verified | 1C-STL-BLW-9140A; Main Oil Tank Vapor Extractor A needs tag | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-05-27 | James Beech | 2020-05-28 | Dave Goldak
STL-01 | STL-01 | PI14627 | Verified | 1C-STL-BLW-9140B; Main Oil Tank Vapor Extractor B needs tag | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-05-27 | James Beech | 2020-05-28 | Dave Goldak
STL-01 | STL-01 | PI14628 | Verified | 1C-STL-V-9140A; Main Oil Tank Vapor Extractor A discharge valve needs tag | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-05-27 | James Beech | 2020-05-28 | Dave Goldak
STL-01 | STL-01 | PI14629 | Verified | 1C-STL-V-9140B; Main Oil Tank Vapor Extractor B discharge valve needs tag | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-05-27 | James Beech | 2020-05-28 | Dave Goldak
STL-01 | STL-01 | PI14630 | Verified | 1C-STL-EJ-9140A; Main Oil Tank Vapor Extractor A Expansion Joint needs tag | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-05-27 | James Beech | 2020-05-28 | Dave Goldak
STL-01 | STL-01 | PI14631 | Verified | 1C-STL-EJ-9140B; Main Oil Tank Vapor Extractor B Expansion Joint needs tag | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-05-27 | James Beech | 2020-05-28 | Dave Goldak
STL-01 | STL-01 | PI14632 | Verified | 1C-STL-EJ-9140A; Main Oil Tank Vapor Extractor A Expansion Joint guide pins not set | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14633 | Verified | 1C-STL-EJ-9140B; Main Oil Tank Vapor Extractor B Expansion Joint guide pins not set | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14634 | Verified | 1C-STL-P-9100A; Main Oil Pump Motor not grounded, motor has cable connection but no ground cable | B | E | Jonathan Donham | McD | 2019-12-07 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14635 | Verified | 1C-STL-P-9100B; Main Oil Pump Motor not grounded, motor has cable connection but no ground cable | B | E | Jonathan Donham | McD | 2019-12-07 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14636 | Verified | 1C-STL-P-9110; Emergency Oil Pump not grounded, motor has cable connection but no ground cable | B | E | Jonathan Donham | McD | 2019-12-07 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-08 | Bernard Stasse
STL-01 | STL-01 | PI14637 | Verified | Duplex Oil Filter skid hold down anchors are too long | C | M | Shane Crowe | McD | 2019-12-07 | Shane Crowe | Comm |  |  | 2019-12-17 | Shane Crowe
STO-01 | STO-01 | PI01880 | Verified | 1CSTOC0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
STO-01 | STO-01 | PI01881 | Verified | 1CSTOC0002, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-29 | Ken Mundy | 2019-07-29 | Mike Tabbert
STO-01 | STO-01 | PI01882 | Verified | 1CSTOC0003, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-29 | Ken Mundy | 2019-07-29 | Mike Tabbert
STO-01 | STO-01 | PI01883 | Verified | 1CSTOC0004, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STO-01 | STO-01 | PI01884 | Verified | 1CSTOC0005, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STO-01 | STO-01 | PI01885 | Verified | 1CSTOC0006, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STO-01 | STO-01 | PI01886 | Verified | 1CSTOC0007, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
STO-01 | STO-01 | PI01887 | Verified | 1CSTOC0009, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STO-01 | STO-01 | PI01888 | Verified | 1CSTOK0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STO-01 | STO-01 | PI01889 | Verified | 1CSTOK0002, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STO-01 | STO-01 | PI01890 | Verified | 1CSTOL0001N, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STO-01 | STO-01 | PI01891 | Verified | 1CSTOL0001P, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STO-01 | STO-01 | PI01892 | Verified | 1CSTOX0001, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STO-01 | STO-01 | PI01893 | Verified | 1CSTOX0002, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-08 | Luis Cantu | 2019-07-08 | Mike Tabbert
STO-01 | STO-01 | PI01894 | Verified | 1CSTOX0003, Pull and Terminate Cable | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-11 | Luis Cantu | 2019-07-11 | Mike Tabbert
STO-01 | STO-01 | PI01896 | Verified | Complete all Raceway | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-22 | Mike Tabbert
STO-01 | STO-01 | PI01897 | Verified | Complete all equipment ground connections to grid | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-22 | Mike Tabbert
STO-01 | STO-01 | PI01898 | Verified | Complete all raceway grounding | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-22 | Mike Tabbert
STO-01 | STO-01 | PI01899 | Verified | Complete all completion paperwork | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-31 | Ed Gober | 2019-07-31 | Mike Tabbert
STO-01 | STO-01 | PI01900 | Verified | Confirm all cables are pulled in correct trays as per cable pull routing. | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-22 | Luis Cantu | 2019-07-29 | Mike Tabbert
STO-01 | STO-01 | PI01901 | Verified | Confirm cables are neat and orderly in cable trays, and secured to cable tray rungs, ty-raps tails trimmed. | B | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-29 | Ken Mundy | 2019-07-29 | Mike Tabbert
STO-01 | STO-01 | PI01902 | Verified | Clean and close all Motor Control Buckets, and all equipment control panels. | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-22 | Mike Tabbert
STO-01 | STO-01 | PI01903 | Verified | 1C-STO-PDIT-9355, Installed tubing not complete need root valve. | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-26 | Gonzalo Pena | 2019-07-29 | Mike Tabbert
STO-01 | STO-01 | PI01904 | Verified | 1C-STO-PDIT-9335, Installed tubing not complete need root valve. | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-22 | Gonzalo Pena | 2019-07-29 | Mike Tabbert
STO-01 | STO-01 | PI01905 | Verified | 1C-STO-PDIT-9345, Installed tubing not complete need root valve | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-22 | Gonzalo Pena | 2019-07-29 | Mike Tabbert
STO-01 | STO-01 | PI01906 | Verified | 1C-STO-PSL-9308, Not installed, missing root valve | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-22 | Gonzalo Pena | 2019-07-29 | Mike Tabbert
STO-01 | STO-01 | PI01907 | Verified | 1C-STO-LSL-9380, Researching location | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-22 | Gonzalo Pena | 2019-07-30 | Mike Tabbert
STO-01 | STO-01 | PI01908 | Verified | 1C-STO-LSH-9362, Researching location | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-30 | Gonzalo Pena | 2019-07-30 | Mike Tabbert
STO-01 | STO-01 | PI01909 | Verified | On Drawing DDKW27134-C sheet 3 support T50-18H is missing a ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-29 | Kelvin Cook
STO-01 | STO-01 | PI01910 | Verified | On Drawing DDKW27134-C sheet 4 on nozzle table item B is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01911 | Verified | On Drawing DDKW27134-C sheet 4 on spool HMA-4 top flange has missing bolts & gasket | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-25 | Damon Turner | 2019-07-29 | Kelvin Cook
STO-01 | STO-01 | PI01912 | Verified | On Drawing DDKW27134-C sheet 5 Pipe support T50-26H has no ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01913 | Verified | On Drawing DDKW27134-C sheet 5 on nozzle table item F is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01914 | Verified | On Drawing DDKW27134-C sheet 5 on nozzle table item G is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01915 | Verified | On Drawing DDKW27134-C sheet 5 Pipe support T50-25H is installed at wrong location | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01916 | Verified | On Drawing DDKW27134-C sheet 5 on nozzle table item E valve handle is not operator friendly | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01917 | Verified | On Drawing DDKW27134-C sheet 6 line from deferntial press regulation valve 1C-STO-PV-9325 has no gasket | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01918 | Verified | On Drawing DDKW27134-C sheet 6 line from to deferential press regulation valve 1C-STO-PV-9325 has no gasket | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01919 | Verified | On Drawing DDKW27134-C sheet 6 pipe support T50-28H missing ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01920 | Verified | On Drawing DDKW27134-C sheet 6 on both side of flange connection ASME 150LB SW RF connecting to flow meter bolts are 1C- STO-FI-9328 too long | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01921 | Verified | On Drawing DDKW27134-C sheet 6 pipe support T50-27H has loose nuts at ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01922 | Verified | On Drawing DDKW27134-C sheet 7 Pipe support T50-32H is installed in the wrong location | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01923 | Verified | On Drawing DDKW27134-C sheet 7 Pipe support T50-34H double nut ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01924 | Verified | On Drawing DDKW27134-C sheet 7 Pipe support T50-36H is in the wrong location | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01925 | Verified | On Drawing DDKW27134-C sheet 8 Pipe support T50-12H missing ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01926 | Verified | On Drawing DDKW27134-C sheet 8 Pipe support T50-11H missing ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01927 | Verified | On Drawing DDKW27134-C sheet 8 Pipe support T50-13H double nut ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01928 | Verified | On Drawing DDKW27134-C sheet 8 at 1C-STD-D-9380 to air detrainning section remove lock washer from bolt head & to nut the flange properly | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01929 | Verified | On Drawing DDKW27134-C sheet 8 ASME 150LB SO RF flange connection has no gasket installed & use all the same size bolts | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01930 | Verified | On Drawing DDKW27134-C sheet 9 ASME 150LB SO FF with Groove connection needs complete bolting | B | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-29 | Damon Turner | 2019-08-02 | Kelvin Cook
STO-01 | STO-01 | PI01931 | Verified | On Drawing DDKW27134-C sheet 9 1C-STO-D-9350 to H2 Detraining section connection needs complete bolting | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01932 | Verified | On Drawing DDKW27134-C sheet 10 pipe support T50-05H has loose ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01933 | Verified | On Drawing DDKW27134-C sheet 10 pipe support T50-03H has a loose ubolt & nuts | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01934 | Verified | On Drawing DDKW27134-C sheet 10 pipe support T50-04H missing second set of nuts | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01935 | Verified | On Drawing DDKW27134-C sheet 11 on nozzle table item U is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01936 | Verified | On Drawing DDKW27134-C sheet 11 on nozzle table item V is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01937 | Verified | On Drawing DDKW27134-C sheet 11 on nozzle table item Q is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01938 | Verified | On Drawing DDKW27134-C sheet 11 on nozzle table item R is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-29 | Kelvin Cook
STO-01 | STO-01 | PI01939 | Verified | On Drawing DDKW27134-C sheet 11 on nozzle table item S is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-29 | Kelvin Cook
STO-01 | STO-01 | PI01940 | Verified | On Drawing DDKW27134-C sheet 11 on nozzle table item W is missing hand wheel | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STO-01 | STO-01 | PI01941 | Verified | On Drawing DDKW27140-e sheet 4 the spectacle flange is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01942 | Verified | On Drawing DDKW27140-e sheet 5 valve 1C-STO-V-9323 pinch point not operator friendly | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01943 | Verified | On Drawing DDKW27140-e sheet 6 on spool HRD-3 hanger rod all thread too short must have full angement plus 2 threads. | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01944 | Verified | On Drawing DDKW27140-e sheet 6 on spool HRD-3 pipe hanger locks nuts are required at eye bolt turn buckle to lock in place. | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01945 | Verified | On Drawing DDKW27140-e sheet 6 on spool HRD-3 just of the the elbow pipe hanger locks nuts required at eyebolt at turnbuckle to lock in place. | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01946 | Verified | On Drawing DDKW27140-e sheet 7 To No 5 BRG Duplex seal oil filter ASME 150LB SW RF is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const |  |  | 2019-07-29 | Kelvin Cook
STO-01 | STO-01 | PI01947 | Verified | On Drawing DDKW27140-e sheet 7 on nozzle table item A is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01948 | Verified | On Drawing DDKW27140-e sheet 7 on nozzle table item B is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-29 | Kelvin Cook
STO-01 | STO-01 | PI01949 | Verified | On Drawing DDKW27140-e sheet 7 To No 6 BRG Duplex seal oil filter ASME 150LB SW RF is not installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const |  |  | 2019-07-29 | Kelvin Cook
STO-01 | STO-01 | PI01950 | Verified | On Drawing DDKW27140-e sheet 6 spool HRD-4 support has no ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-29 | Kelvin Cook
STO-01 | STO-01 | PI01951 | Verified | On Drawing DDKW27140-e sheet 6 spool HRD-5 missing nut at turnbuckle snug nut to eye bolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01952 | Verified | On Drawing DDKW27140-e sheet 6 spool HRD-5 remove temporary support | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-29 | Kelvin Cook
STO-01 | STO-01 | PI01953 | Verified | On Drawing DDKW27134-c sheet 4 through 12 clean grout of pipe | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01954 | Verified | On Drawing DDKW27134-c sheet 7 spool HSF-13 is contact with stainless steel at insulation | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-29 | Kelvin Cook
STO-01 | STO-01 | PI01955 | Verified | On Drawing DDKW27134-c sheet 7 spool HSF-12 slope is not good, needs to be verified | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01956 | Verified | On Drawing DDKW27134-c sheet 7 spool HSF-12 slope is not good, needs to be verified | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01957 | Verified | On Drawing DDKW27134-c sheet 7 spool HSF-12 slope is not good, needs to be verified | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-18 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01958 | Verified | On Drawing DDKW27140-c sheet 8 on spool HAS-2 hanger has loose ubolt & missing second set of flat washers | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01959 | Verified | On Drawing DDKW27140-c sheet 8 on spool HAS-3 hanger missing second set of flat washers | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01960 | Verified | On Drawing DDKW27140-c sheet 8 on spool HAS-3 hanger needs tape removed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01961 | Verified | On Drawing DDKW27140-c sheet 8 on spool HAS-3 hanger missing second set of nuts and flat washers | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01962 | Verified | On Drawing DDKW27140-c sheet 8 on spool HAS-3 hanger just off field weld has loose nuts at ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01963 | Verified | On Drawing DDKW27140-c sheet 8 on spool HAS-4 hangers missing set flat washer & second set of nuts | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01964 | Verified | On Drawing DDKW27140-c sheet 8 on spool HAS-4 connecting to the float switch. | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01965 | Verified | On Drawing DDKW27140-c sheet 9 hanger on the slope elevation of the line is missing ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01966 | Verified | On Drawing DDKW27140-c sheet 10 hanger on SOFB-VEN-1 missing ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01967 | Verified | On Drawing DDKW27140-c sheet 10 hanger on SOFB-VEN-1 missing hardware at ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01968 | Verified | On Drawing DDKW27140-c sheet 10 hanger on SOFB-DRN-3 on hanger of the T is missing nuts at ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01969 | Verified | On Drawing DDKW27140-c sheet 10 hanger on SOFB-VEN-3 hanger has loose nuts at ubolt | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01970 | Verified | On Drawing DDKW27140-c sheet 10 hanger on SOFB-VEN-4 remove dunage | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-22 | Kelvin Cook
STO-01 | STO-01 | PI01980 | Verified | Flange 1C-STO-PV-9325 needs to be covered, finish piping up | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-08-08 | Stuart Herring
STO-01 | STO-01 | PI01981 | Verified | Grout each of the seal oil pumps | A | C | Johnny Campbell | McD | 2019-07-01 | Johnny Campbell | Const | 2019-07-16 | Johnny Campbell | 2019-08-08 | Stuart Herring
STO-01 | STO-01 | PI01982 | Verified | Gap between seal oil pump and pipe, fix alignment | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-22 | Stuart Herring
STO-01 | STO-01 | PI01983 | Verified | All instrumentation needs to be completed | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-30 | Gonzalo Pena | 2019-08-08 | Stuart Herring
STO-01 | STO-01 | PI01984 | Verified | Orifice plate missing from discharge side of seal oil pump | B | P | Stuart Herring | McD | 2019-07-01 | Stuart Herring | Const |  |  | 2019-12-01 | Stuart Herring
STO-01 | STO-01 | PI01985 | Verified | Grout pipe supports of the piping coming from seal oil pumps | C | C | Johnny Campbell | McD | 2019-07-01 | Johnny Campbell | Const | 2019-07-16 | Johnny Campbell | 2019-07-22 | Stuart Herring
STO-01 | STO-01 | PI01993 | Verified | Missing sight glass on Air Detaining Tank | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-22 | Stuart Herring
STO-01 | STO-01 | PI01995 | Verified | Slope down YGV-1 | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-22 | Stuart Herring
STO-01 | STO-01 | PI01996 | Verified | Finish piping | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-08-08 | Stuart Herring
STO-01 | STO-01 | PI01997 | Verified | Seal Oil supply gauge is too high | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-22 | Stuart Herring
STO-01 | STO-01 | PI01998 | Verified | Seal Oil return flange need to be completely installed | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-22 | Stuart Herring
STO-01 | STO-01 | PI01999 | Verified | Instrument tubing needs to be finished | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-30 | Gonzalo Pena | 2019-08-08 | Stuart Herring
STO-01 | STO-01 | PI02004 | Verified | Need grounding on flex conduit for both motors | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-19 | Logan Holland
STO-01 | STO-01 | PI02005 | Verified | Grout conduit supports near seal oil pumps | B | C | Johnny Campbell | McD | 2019-07-01 | Johnny Campbell | Const | 2019-07-25 | Johnny Campbell | 2019-07-31 | Shannon Scott
STO-01 | STO-01 | PI02006 | Verified | STO-PSL-9308 tubing to complete | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-22 | Gonzalo Pena | 2019-07-24 | Shannon Scott
STO-01 | STO-01 | PI02007 | Verified | System wide install all condulet covers and tightened | B | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-09 | Luis Cantu | 2019-07-11 | Shannon Scott
STO-01 | STO-01 | PI02008 | Verified | Seal holes on the motor termination box, inside and out | B | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-19 | Ken Mundy | 2019-07-26 | Logan Holland
STO-01 | STO-01 | PI02009 | Verified | CSTO-RAK -9090 need support on conduit, need grounding on flex, complete the install of the instrument | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-19 | Ken Mundy | 2019-07-23 | Shannon Scott
STO-01 | STO-01 | PI02010 | Verified | LSL-9380 to install instrument | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-22 | Gonzalo Pena | 2019-07-30 | Gonzalo Pena
STO-01 | STO-01 | PI02011 | Verified | LSL-9380 to run conduit and pull and terminate cabling | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-30 | Ken Mundy | 2019-07-30 | Gonzalo Pena
STO-01 | STO-01 | PI02012 | Verified | LSH-9362 to install instrument | A | I | Gonzalo Pena | McD | 2019-07-01 | Gonzalo Pena | Const | 2019-07-23 | Gonzalo Pena | 2019-07-23 | Ayda Chaves
STO-01 | STO-01 | PI02013 | Verified | LSL-9362 to run conduit and pull and terminate cabling | A | E | Luis Cantu | McD | 2019-07-01 | Luis Cantu | Const | 2019-07-30 | Ken Mundy | 2019-07-30 | Gonzalo Pena
STO-01 | STO-01 | PI02014 | Verified | PDIT-9345 to install and weld root valves | A | P | Damon Turner | McD | 2019-07-01 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-22 | Gonzalo Pena
STO-01 | STO-01 | PI02015 | Verified | RAK-9070A check if there is missing conduit support near the condulet | B | E | Mike Tabbert | McD | 2019-07-01 | Mike Tabbert | Const | 2019-07-29 | Mike Tabbert | 2019-07-29 | Shannon Scott
STO-01 | STO-01 | PI02016 | Verified | RAK-9070A and PDIT-9345 grout all instrument stands | B | C | Johnny Campbell | McD | 2019-07-01 | Johnny Campbell | Const | 2019-07-25 | Johnny Campbell | 2019-07-31 | Shannon Scott
STO-01 | STO-01 | PI02073 | Verified | Install tags on all valves and equipment | C | P | Tim Green | McD | 2019-07-02 | Tim Green | Const | 2021-01-22 | Eric Policarpio | 2021-01-22 | Eric Policarpio
STO-01 | STO-01 | PI02074 | Verified | Replace burnt tags | C | P | Tim Green | McD | 2019-07-02 | Tim Green | Const | 2021-01-22 | Eric Policarpio | 2021-01-22 | Eric Policarpio
STO-01 | STO-01 | PI02075 | Verified | FO-9300 fix flange hi-lo | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-31 | Shannon Scott
STO-01 | STO-01 | PI02076 | Verified | LSL-9380 and associated piping and valves not installed | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-31 | Shannon Scott
STO-01 | STO-01 | PI02077 | Verified | Piping connected to V-9383 and V-9384 needs support | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-22 | Damon Turner | 2019-07-31 | Shannon Scott
STO-01 | STO-01 | PI02078 | Verified | Seal Oil piping at turbine is incomplete and is in the process of being worked | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-20 | Damon Turner | 2019-07-31 | Shannon Scott
STO-01 | STO-01 | PI02079 | Verified | Install screen on vent line | A | P | Damon Turner | McD | 2019-07-02 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-31 | Shannon Scott
STO-01 | STO-01 | PI02080 | Verified | TRP-9370 tagged incorrectly | B | P | Justin Houdeshell | McD | 2019-07-02 | Justin Houdeshell | Const | 2019-07-27 | Justin Houdeshell | 2019-10-03 | Nelson Eichelberger
STO-01 | STO-01 | PI02389 | Verified | DDKW27134 (155126-110101-01-SD-00110) Page 7/12 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STO-01 | STO-01 | PI02390 | Verified | DDKW27140 (155126-110101-01-SD-00116) Page 4/11 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-19 | Damon Turner | 2019-07-19 | Tom Noble
STO-01 | STO-01 | PI02391 | Verified | DDKW27140 (155126-110101-01-SD-00116) Page 6/11 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STO-01 | STO-01 | PI02392 | Verified | DDKW27140 (155126-110101-01-SD-00116) Page 7/11 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-29 | Damon Turner | 2019-07-29 | Tom Noble
STO-01 | STO-01 | PI02393 | Verified | DDKW27140 (155126-110101-01-SD-00116) Page 8/11 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-29 | Damon Turner | 2019-07-29 | Tom Noble
STO-01 | STO-01 | PI02394 | Verified | DDKW27140 (155126-110101-01-SD-00116) Page 9/11 Weld is not cleared | A | P | Damon Turner | McD | 2019-07-19 | Damon Turner | Const | 2019-07-26 | Damon Turner | 2019-07-26 | Tom Noble
STO-01 | STO-01 | PI14584 | Verified | Install Personnel Protection insulation as required on Line No. 6-1C-STO-0010, STG Bldg. Float Trap Assembly, and Air Detraining Section Vent | C | C | Josh Koerner | PCI | 2019-12-07 | Josh Koerner | Comm | 2020-06-18 | Josh Koerner | 2021-06-17 | John Watts
STO-01 | STO-01 | PI14585 | Verified | Paint system piping as necessary | C | X | Jerry Smith | McD | 2019-12-07 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-04-08 | Bernard Stasse
STO-01 | STO-01 | PI14586 | Verified | Install uni-strut end caps at Seal Oil Skid | C | E | Chris Colvin | McD | 2019-12-07 | Chris Colvin | Comm | 2020-05-05 | Chris Colvin | 2020-08-17 | Dave Goldak
STO-01 | STO-01 | PI14587 | Verified | Incorrect installation of hillside washers on all U-bolts at Seal Oil Skid | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-08 | Bernard Stasse
STO-01 | STO-01 | PI14588 | Verified | Tighten rod-hanger clamps on SRV-9305 discharge piping under mezzanine grating | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-08 | Bernard Stasse
STO-01 | STO-01 | PI14589 | Verified | 1" SS line to PDIT-9355 is crooked, needs to be straightened | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-08 | Bernard Stasse
STO-01 | STO-01 | PI14590 | Verified | 1" Carbon Steel line to PDIT-9355 is crooked, needs to be straightened | C | P | James Beech | McD | 2019-12-07 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-08 | Bernard Stasse
STO-01 | STO-01 | PI14591 | Verified | 1" SS line to PDIT-9355 needs additional support at STG Bldg mezzanine level | C | P | Kelvin Cook | McD | 2019-12-07 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-08 | Bernard Stasse
STO-01 | STO-01 | PI14592 | Verified | Drawing needs to be changed to indicate SS piping for 1" SS line to PDIT-9355 | C | P | Charles Worthington | McD | 2019-12-07 | Charles Worthington | Comm | 2020-04-28 | Charles Worthington | 2020-07-31 | Nelson Eichelberger
STO-01 | STO-01 | PI17230 | Verified | Missing SRV certification. Toshiba to provide | C | I | Eric Policarpio | TOS | 2020-02-26 | Eric Policarpio | Comm | 2020-03-10 | Eric Policarpio | 2020-04-07 | Bernard Stasse
STO-01 | STO-01 | PI18159 | Verified | Water in seal oil on STG - Curtain sprays overspray because the temperature in the condenser is out of control. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-14 | William Mitchell | 2021-01-05 | Keith Pollock
STS-01 | STS-01 | PI02022 | Verified | TEW-9186 pull and terminate cables | A | E | Chris Colvin | McD | 2019-07-01 | Chris Colvin | Const | 2019-08-01 | Dustin Futrell | 2019-12-07 | Michael Law
STS-01 | STS-01 | PI02023 | Verified | TEW-9184 pull and terminate cables | A | E | Chris Colvin | McD | 2019-07-01 | Chris Colvin | Const | 2019-08-01 | Dustin Futrell | 2019-12-07 | Michael Law
STS-01 | STS-01 | PI02026 | Verified | TEW-9172 to 9175 no conduit, no wire | A | E | Chris Colvin | McD | 2019-07-01 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2020-01-22 | Albert Burge
STS-01 | STS-01 | PI10137 | Verified | 1CSTLC0017 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10138 | Verified | 1CSTSC0021 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10139 | Verified | 1CSTSX0017 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10140 | Verified | 1CSTSX0018 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10141 | Verified | 1CSTSX0019 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10142 | Verified | 1CSTSX0027 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10143 | Verified | 1CSTSX0028 From Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10230 | Verified | 1CSTSC0021 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10231 | Verified | 1CSTSC0046 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10232 | Verified | 1CSTSC0058 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10233 | Verified | 1CSTSC0060 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10234 | Verified | 1CSTSC0096 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10235 | Verified | 1CSTSX0017 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10236 | Verified | 1CSTSX0018 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10237 | Verified | 1CSTSX0019 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10238 | Verified | 1CSTSX0027 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10239 | Verified | 1CSTSX0028 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10240 | Verified | 1CSTSX0033 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10241 | Verified | 1CSTSX0034 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10242 | Verified | 1CSTSX0035 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10243 | Verified | 1CSTSX0036 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-24 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10244 | Verified | 1CSTSX0037 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const |  |  | 2019-10-25 | Mike Tabbert
STS-01 | STS-01 | PI10245 | Verified | 1CSTSX0038 To Term | A | E | Dustin Futrell | McD | 2019-10-22 | Dustin Futrell | Const | 2019-10-23 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10822 | Verified | 1CSTSX0026 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10824 | Verified | 1CSTSX0046 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10825 | Verified | 1CSTSX0048 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10826 | Verified | 1CSTSX0050 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10827 | Verified | 1CSTSX0052 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10828 | Verified | 1CSTSX0054 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10829 | Verified | 1CSTSX0056 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10830 | Verified | 1CSTSX0058 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10831 | Verified | 1CSTSX0060 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10832 | Verified | 1CSTSX0062 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10833 | Verified | 1CSTSX0063 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10834 | Verified | 1CSTSX0064 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10835 | Verified | 1CSTSX0065 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10836 | Verified | 1CSTSX0066 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10837 | Verified | 1CSTSX0102 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10838 | Verified | 1CSTSX0103 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10839 | Verified | 1CSTSX0105 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10840 | Verified | 1CSTSX0107 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10841 | Verified | 1CSTSX0108 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10842 | Verified | 1CSTSX0135 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10843 | Verified | 1CSTSX0136 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI10845 | Verified | 1CSTSX0169 Pulled | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11456 | Verified | 1CSTSX0026 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11457 | Verified | 1CSTSX0039 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11458 | Verified | 1CSTSX0046 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11459 | Verified | 1CSTSX0048 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11460 | Verified | 1CSTSX0050 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11461 | Verified | 1CSTSX0052 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11462 | Verified | 1CSTSX0054 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11463 | Verified | 1CSTSX0056 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11464 | Verified | 1CSTSX0058 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11465 | Verified | 1CSTSX0060 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11466 | Verified | 1CSTSX0062 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11467 | Verified | 1CSTSX0063 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11468 | Verified | 1CSTSX0064 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11469 | Verified | 1CSTSX0065 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11470 | Verified | 1CSTSX0066 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11471 | Verified | 1CSTSX0102 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11472 | Verified | 1CSTSX0103 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11473 | Verified | 1CSTSX0105 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11474 | Verified | 1CSTSX0107 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11475 | Verified | 1CSTSX0108 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11476 | Verified | 1CSTSX0135 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11477 | Verified | 1CSTSX0136 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI11478 | Verified | 1CSTSX0139 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12103 | Verified | 1CSTSX0026 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12104 | Verified | 1CSTSX0039 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-11-04 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12105 | Verified | 1CSTSX0046 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12106 | Verified | 1CSTSX0048 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12107 | Verified | 1CSTSX0050 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12108 | Verified | 1CSTSX0052 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12109 | Verified | 1CSTSX0054 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12110 | Verified | 1CSTSX0056 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12111 | Verified | 1CSTSX0058 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12112 | Verified | 1CSTSX0060 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12113 | Verified | 1CSTSX0062 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12114 | Verified | 1CSTSX0063 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12115 | Verified | 1CSTSX0064 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12116 | Verified | 1CSTSX0065 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12117 | Verified | 1CSTSX0066 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12118 | Verified | 1CSTSX0102 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12119 | Verified | 1CSTSX0103 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12120 | Verified | 1CSTSX0105 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12121 | Verified | 1CSTSX0107 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12122 | Verified | 1CSTSX0108 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12123 | Verified | 1CSTSX0135 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12124 | Verified | 1CSTSX0136 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12125 | Verified | 1CSTSX0139 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12240 | Verified | 1CSTSC0021 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-29 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12241 | Verified | 1CSTSX0017 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12242 | Verified | 1CSTSX0018 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12243 | Verified | 1CSTSX0019 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12244 | Verified | 1CSTSX0027 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12245 | Verified | 1CSTSX0028 From Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12466 | Verified | 1CSTSC0021 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12467 | Verified | 1CSTSC0046 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12468 | Verified | 1CSTSC0058 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12469 | Verified | 1CSTSC0060 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12470 | Verified | 1CSTSC0096 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12471 | Verified | 1CSTSX0017 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12472 | Verified | 1CSTSX0018 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12473 | Verified | 1CSTSX0019 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12474 | Verified | 1CSTSX0027 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12475 | Verified | 1CSTSX0028 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-31 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12476 | Verified | 1CSTSX0033 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12478 | Verified | 1CSTSX0035 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12479 | Verified | 1CSTSX0036 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12481 | Verified | 1CSTSX0038 To Term | A | E | Dustin Futrell | McD | 2019-10-25 | Dustin Futrell | Const | 2019-10-28 | Dustin Futrell | 2019-11-11 | Mike Tabbert
STS-01 | STS-01 | PI12847 | Verified | Close manways (after clean & close). | A | M | Shane Crowe | McD | 2019-11-08 | Shane Crowe | Const | 2020-02-10 | Shane Crowe | 2020-02-11 | Kelvin Cook
STS-01 | STS-01 | PI12848 | Verified | Install curtain spray nozzles. | A | M | Bobby Williams | McD | 2019-11-08 | Bobby Williams | Const | 2020-02-03 | Bobby Williams | 2020-03-03 | Michael Law
STS-01 | STS-01 | PI12849 | Verified | Install hood spray nozzles. | A | M | Shane Crowe | McD | 2019-11-08 | Shane Crowe | Const | 2020-02-10 | Shane Crowe | 2020-03-03 | Michael Law
STS-01 | STS-01 | PI12850 | Verified | Remove all tape, plastic, etc. from turbine. | A | M | Shane Crowe | McD | 2019-11-08 | Shane Crowe | Const | 2019-12-03 | Shane Crowe | 2019-12-03 | Joshua Sturgeon
STS-01 | STS-01 | PI12851 | Verified | Complete all insulation. | C | Q | Sheri Fritz | PCI | 2019-11-08 | Sheri Fritz | Const | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
STS-01 | STS-01 | PI12852 | Verified | Hot reheat line below south CRV - pipe support removed. | A | P | James Beech | McD | 2019-11-08 | James Beech | Const | 2019-12-04 | Joshua Sturgeon | 2019-12-10 | Joshua Sturgeon
STS-01 | STS-01 | PI13219 | Verified | 1C-STS-TB-9005A/B Terminal box for main steam stop valve to install and complete wiring after steam blows | A | E | Chris Colvin | McD | 2019-11-20 | Chris Colvin | Const | 2020-02-04 | Chris Colvin | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI13220 | Verified | 1C-STS-TB-9010A/B Terminal box for main steam control valve to install and complete wiring after steam blows | A | E | Chris Colvin | McD | 2019-11-20 | Chris Colvin | Const | 2020-02-04 | Chris Colvin | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI13221 | Verified | 1C-STS-TB-9015A/B Terminal box for reheat stop valve to install and complete wiring after steam blows | A | E | Chris Colvin | McD | 2019-11-20 | Chris Colvin | Const | 2020-02-04 | Chris Colvin | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI13222 | Verified | 1C-STS-TB-9020A/B Terminal box for intercept valve to install and complete wiring after steam blows | A | E | Chris Colvin | McD | 2019-11-20 | Chris Colvin | Const | 2020-02-04 | Chris Colvin | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI13223 | Verified | 1C-STS-TB-9030 LP induction box to install and wire after steam blows | A | E | Chris Colvin | McD | 2019-11-20 | Chris Colvin | Const | 2020-02-04 | Chris Colvin | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI13224 | Verified | 1C-STS-TB-9035A to complete wiring | A | E | Chris Colvin | McD | 2019-11-20 | Chris Colvin | Const | 2019-12-06 | Chris Caywood | 2019-12-10 | Mike Tabbert
STS-01 | STS-01 | PI13225 | Verified | 1C-STS-TB-9035A to clean out box and seal the conduit | A | E | Chris Colvin | McD | 2019-11-20 | Chris Colvin | Const | 2019-12-11 | Brad Stanford | 2019-12-11 | Fred Michael
STS-01 | STS-01 | PI13226 | Verified | 1C-STS-TB-9035B to clean out box and seal the conduit | A | E | Chris Colvin | McD | 2019-11-20 | Chris Colvin | Const | 2019-12-11 | Brad Stanford | 2019-12-11 | Fred Michael
STS-01 | STS-01 | PI13227 | Verified | 1C-STS-TB-9035B all internal and casing TE cables to be installed after insulation | B | E | Chris Colvin | McD | 2019-11-20 | Chris Colvin | Const | 2020-02-20 | Chris Colvin | 2020-02-20 | Mike Tabbert
STS-01 | STS-01 | PI13260 | Verified | Iso SPC-GIH-XULC1-00005 SH7/45 1st Stage Press(PT,PP) not installed | A | P | James Beech | McD | 2019-11-21 | James Beech | Const | 2019-12-13 | James Beech | 2019-12-14 | Ethan Byrd
STS-01 | STS-01 | PI13261 | Verified | Iso SPC-GIH-XULC1-00005 SH8/45 Turbine Reheat Bowl Press (PT,PP) not installed | A | P | James Beech | McD | 2019-11-21 | James Beech | Const | 2019-12-16 | James Beech | 2019-12-18 | Kelvin Cook
STS-01 | STS-01 | PI13262 | Verified | Iso SPC-GIH-XULC1-00005 SH13/45 IP Turbine EXH Steam Press (PT) not installed | A | P | James Beech | McD | 2019-11-21 | James Beech | Const | 2019-12-16 | James Beech | 2019-12-18 | Kelvin Cook
STS-01 | STS-01 | PI13263 | Verified | Iso SPC-GIH-XULC1-00005 SH 31/45 IP Turbine EXH Steam Press (PP) not installed | A | P | James Beech | McD | 2019-11-21 | James Beech | Const | 2019-12-16 | James Beech | 2019-12-18 | Kelvin Cook
STS-01 | STS-01 | PI13371 | Verified | 1CTL201101, 1CTL201001, 1CTL201101, 1CTC201001, Cable Tray North of Main PDC, Grounding not complete. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-09 | Frank Lopez | 2019-12-10 | Mike Tabbert
STS-01 | STS-01 | PI13372 | Verified | 1CTL201101, 1CTL201001, 1CTL201101, 1CTC201001, Cable Tray North of Main PDC, Hold down clamps missing | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-08 | Brad Stanford | 2019-12-10 | Mike Tabbert
STS-01 | STS-01 | PI13378 | Verified | 1CTK202021, 1CTK202022, 18 inch trays on west and north side of Mez Deck, Needs support horizontal 90 degree elbow northwest corner. | B | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-09 | Brad Stanford | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI13379 | Verified | 1CTK202021, 1CTK202022, 18 inch trays on west and north side of Mez Deck, north side middle offset needs supports. | B | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2019-12-09 | Brad Stanford | 2019-12-18 | Mike Tabbert
STS-01 | STS-01 | PI13382 | Verified | All conduit embeds on table top need grounding bushings grounded. | A | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const |  |  | 2019-12-12 | John Sullivan
STS-01 | STS-01 | PI13383 | Verified | Covers missing on conduit along STG Tray system | C | E | Chris Colvin | McD | 2019-11-22 | Chris Colvin | Const | 2020-05-11 | Matt Gilmore | 2020-05-19 | Mike Tabbert
STS-01 | STS-01 | PI14179 | Verified | 1CEXSC0001, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STS-01 | STS-01 | PI14180 | Verified | 1CNQSC0022, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14181 | Verified | 1CNQSK0012, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14182 | Verified | 1CSTSC0085, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STS-01 | STS-01 | PI14183 | Verified | 1CSTSK0014, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STS-01 | STS-01 | PI14184 | Verified | 1CSTSK0015, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STS-01 | STS-01 | PI14185 | Verified | 1CSTSK0025, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-07 | Mike Tabbert
STS-01 | STS-01 | PI14186 | Verified | 1CSTSK0026, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-07 | Mike Tabbert
STS-01 | STS-01 | PI14187 | Verified | 1CSTSX0020, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STS-01 | STS-01 | PI14188 | Verified | 1CSTSX0040, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STS-01 | STS-01 | PI14189 | Verified | 1CSTSX0146, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STS-01 | STS-01 | PI14190 | Verified | 1CSTSX0147, Pull Cable | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
STS-01 | STS-01 | PI14191 | Verified | 1CEXSC0001, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14216 | Verified | 1CSTSH0001G6, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14217 | Verified | 1CSTSH0002N1, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14218 | Verified | 1CSTSH0002N2, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14219 | Verified | 1CSTSH0002N3, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14220 | Verified | 1CSTSH0002N4, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14221 | Verified | 1CSTSH0002N5, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14222 | Verified | 1CSTSH0002P1, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14223 | Verified | 1CSTSH0002P2, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14224 | Verified | 1CSTSH0002P3, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14225 | Verified | 1CSTSH0002P4, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14226 | Verified | 1CSTSH0002P5, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14227 | Verified | 1CSTSK0012, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14228 | Verified | 1CSTSK0013, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14229 | Verified | 1CSTSK0014, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14230 | Verified | 1CSTSK0015, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14231 | Verified | 1CSTSK0016, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14232 | Verified | 1CSTSK0017, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14233 | Verified | 1CSTSK0019, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14234 | Verified | 1CSTSK0021, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-13 | Mike Tabbert
STS-01 | STS-01 | PI14235 | Verified | 1CSTSK0025, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2020-02-21 | Chris Colvin | 2020-02-21 | Mike Tabbert
STS-01 | STS-01 | PI14236 | Verified | 1CSTSK0026, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-18 | Chris Caywood
STS-01 | STS-01 | PI14237 | Verified | 1CSTSX0013, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14238 | Verified | 1CSTSX0020, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14239 | Verified | 1CSTSX0021, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14240 | Verified | 1CSTSX0040, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-07 | Mike Tabbert
STS-01 | STS-01 | PI14241 | Verified | 1CSTSX0081, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14242 | Verified | 1CSTSX0109, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-13 | Mike Tabbert
STS-01 | STS-01 | PI14243 | Verified | 1CSTSX0111, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14244 | Verified | 1CSTSX0112, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14245 | Verified | 1CSTSX0130, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14246 | Verified | 1CSTSX0146, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14247 | Verified | 1CSTSX0147, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14248 | Verified | 1CEXSC0001, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14215 | Verified | 1CSTSH0001G5, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14214 | Verified | 1CSTSH0001G4, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14213 | Verified | 1CSTSH0001G3, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14212 | Verified | 1CSTSH0001G2, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14211 | Verified | 1CSTSH0001G1, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14210 | Verified | 1CSTSC0090, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14209 | Verified | 1CSTSC0089, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14208 | Verified | 1CSTSC0085, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14207 | Verified | 1CSTSC0073, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14206 | Verified | 1CSTSC0072, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14205 | Verified | 1CSTSC0071, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14204 | Verified | 1CSTSC0070, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14203 | Verified | 1CSTSC0069, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14202 | Verified | 1CSTSC0068, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14201 | Verified | 1CSTSC0067, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14200 | Verified | 1CSTSC0066, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14199 | Verified | 1CSTSC0065, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-06 | Mike Tabbert
STS-01 | STS-01 | PI14198 | Verified | 1CSTSC0064, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-06 | Mike Tabbert
STS-01 | STS-01 | PI14197 | Verified | 1CSTSC0063, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-06 | Mike Tabbert
STS-01 | STS-01 | PI14196 | Verified | 1CSTSC0062, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14195 | Verified | 1CSTSC0018, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14194 | Verified | 1CSTSC0016, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14193 | Verified | 1CNQSK0012, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-01-06 | Mike Tabbert
STS-01 | STS-01 | PI14192 | Verified | 1CNQSC0022, From Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14249 | Verified | 1CNQSC0022, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14250 | Verified | 1CNQSK0012, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14251 | Verified | 1CSTSC0001, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14252 | Verified | 1CSTSC0002, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
STS-01 | STS-01 | PI14253 | Verified | 1CSTSC0003, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14254 | Verified | 1CSTSC0004, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14255 | Verified | 1CSTSC0005, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14256 | Verified | 1CSTSC0006, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14257 | Verified | 1CSTSC0007, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
STS-01 | STS-01 | PI14258 | Verified | 1CSTSC0008, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14259 | Verified | 1CSTSC0009, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14260 | Verified | 1CSTSC0016, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14261 | Verified | 1CSTSC0018, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14262 | Verified | 1CSTSC0061, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
STS-01 | STS-01 | PI14263 | Verified | 1CSTSC0085, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14264 | Verified | 1CSTSC0089, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14265 | Verified | 1CSTSC0090, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14266 | Verified | 1CSTSC0091, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14267 | Verified | 1CSTSC0092, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14268 | Verified | 1CSTSH0001G1, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14269 | Verified | 1CSTSH0001G2, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14270 | Verified | 1CSTSH0001G3, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14271 | Verified | 1CSTSH0001G4, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14272 | Verified | 1CSTSH0001G5, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14273 | Verified | 1CSTSH0001G6, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14274 | Verified | 1CSTSH0002N1, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14275 | Verified | 1CSTSH0002N2, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14276 | Verified | 1CSTSH0002N3, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14277 | Verified | 1CSTSH0002N4, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14278 | Verified | 1CSTSH0002N5, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14279 | Verified | 1CSTSH0002P1, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14280 | Verified | 1CSTSH0002P2, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14281 | Verified | 1CSTSH0002P3, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14282 | Verified | 1CSTSH0002P4, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14283 | Verified | 1CSTSH0002P5, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-02 | Mike Tabbert
STS-01 | STS-01 | PI14284 | Verified | 1CSTSK0005, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14285 | Verified | 1CSTSK0008, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14286 | Verified | 1CSTSK0009, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14287 | Verified | 1CSTSK0014, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
STS-01 | STS-01 | PI14288 | Verified | 1CSTSK0015, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-12 | Jared Stimpson | 2019-12-12 | Mike Tabbert
STS-01 | STS-01 | PI14289 | Verified | 1CSTSK0018, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14290 | Verified | 1CSTSK0019, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14291 | Verified | 1CSTSK0020, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14292 | Verified | 1CSTSK0021, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
STS-01 | STS-01 | PI14293 | Verified | 1CSTSK0025, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-18 | Chris Caywood
STS-01 | STS-01 | PI14294 | Verified | 1CSTSK0026, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-18 | Chris Caywood
STS-01 | STS-01 | PI14295 | Verified | 1CSTSX0001, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14296 | Verified | 1CSTSX0002, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14297 | Verified | 1CSTSX0003, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
STS-01 | STS-01 | PI14298 | Verified | 1CSTSX0004, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
STS-01 | STS-01 | PI14299 | Verified | 1CSTSX0005, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-07 | Mike Tabbert
STS-01 | STS-01 | PI14300 | Verified | 1CSTSX0006, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14301 | Verified | 1CSTSX0007, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14302 | Verified | 1CSTSX0008, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14303 | Verified | 1CSTSX0009, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14304 | Verified | 1CSTSX0010, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14305 | Verified | 1CSTSX0011, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14306 | Verified | 1CSTSX0012, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14307 | Verified | 1CSTSX0013, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
STS-01 | STS-01 | PI14308 | Verified | 1CSTSX0014, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
STS-01 | STS-01 | PI14309 | Verified | 1CSTSX0015, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
STS-01 | STS-01 | PI14310 | Verified | 1CSTSX0020, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14311 | Verified | 1CSTSX0021, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2019-12-21 | Mike Tabbert
STS-01 | STS-01 | PI14312 | Verified | 1CSTSX0040, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14313 | Verified | 1CSTSX0041, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14314 | Verified | 1CSTSX0045, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14315 | Verified | 1CSTSX0047, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14316 | Verified | 1CSTSX0049, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14317 | Verified | 1CSTSX0051, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14318 | Verified | 1CSTSX0053, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
STS-01 | STS-01 | PI14319 | Verified | 1CSTSX0055, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
STS-01 | STS-01 | PI14320 | Verified | 1CSTSX0057, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
STS-01 | STS-01 | PI14321 | Verified | 1CSTSX0059, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
STS-01 | STS-01 | PI14322 | Verified | 1CSTSX0068, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14323 | Verified | 1CSTSX0069, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14324 | Verified | 1CSTSX0070, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
STS-01 | STS-01 | PI14325 | Verified | 1CSTSX0071, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
STS-01 | STS-01 | PI14326 | Verified | 1CSTSX0072, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14327 | Verified | 1CSTSX0073, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14328 | Verified | 1CSTSX0075, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-13 | Mike Tabbert
STS-01 | STS-01 | PI14329 | Verified | 1CSTSX0077, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14330 | Verified | 1CSTSX0079, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
STS-01 | STS-01 | PI14331 | Verified | 1CSTSX0081, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
STS-01 | STS-01 | PI14332 | Verified | 1CSTSX0083, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
STS-01 | STS-01 | PI14333 | Verified | 1CSTSX0085, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-03 | Mike Tabbert
STS-01 | STS-01 | PI14334 | Verified | 1CSTSX0086, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14335 | Verified | 1CSTSX0088, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14336 | Verified | 1CSTSX0090, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14337 | Verified | 1CSTSX0092, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14338 | Verified | 1CSTSX0094, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14339 | Verified | 1CSTSX0096, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14340 | Verified | 1CSTSX0098, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14341 | Verified | 1CSTSX0099, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14342 | Verified | 1CSTSX0100, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
STS-01 | STS-01 | PI14343 | Verified | 1CSTSX0101, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
STS-01 | STS-01 | PI14344 | Verified | 1CSTSX0109, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-13 | Mike Tabbert
STS-01 | STS-01 | PI14345 | Verified | 1CSTSX0110, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14346 | Verified | 1CSTSX0111, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14347 | Verified | 1CSTSX0112, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14348 | Verified | 1CSTSX0113, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14349 | Verified | 1CSTSX0114, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-06 | Mike Tabbert
STS-01 | STS-01 | PI14350 | Verified | 1CSTSX0115, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14351 | Verified | 1CSTSX0146, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14352 | Verified | 1CSTSX0147, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2019-12-16 | Jared Stimpson | 2019-12-16 | Mike Tabbert
STS-01 | STS-01 | PI14353 | Verified | 1CSTSX0154, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14354 | Verified | 1CSTSX0155, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const |  |  | 2020-02-05 | Mike Tabbert
STS-01 | STS-01 | PI14355 | Verified | 1CSTSX0156, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
STS-01 | STS-01 | PI14356 | Verified | 1CSTSX0157, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
STS-01 | STS-01 | PI14357 | Verified | 1CSTSX0158, To Termination | A | E | Chris Colvin | McD | 2019-12-05 | Chris Colvin | Const | 2020-02-10 | Chris Colvin | 2020-02-10 | Mike Tabbert
STS-01 | STS-01 | PI14363 | Verified | Replace damaged TE (1C-STS-TE-9041A). | B | I | Gonzalo Pena | McD | 2019-12-05 | Gonzalo Pena | Const |  |  | 2019-12-06 | James Tanner
STS-01 | STS-01 | PI14364 | Verified | Replace damaged TE (1C-STS-TE-9041B). | B | I | Gonzalo Pena | McD | 2019-12-05 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-23 | Michael Law
STS-01 | STS-01 | PI14365 | Verified | Replace damaged TE (1C-STS-TE-9042A). | B | I | Gonzalo Pena | McD | 2019-12-05 | Gonzalo Pena | Const | 2019-12-31 | Gonzalo Pena | 2020-01-15 | Michael Law
STS-01 | STS-01 | PI14366 | Verified | Replace damaged TE (1C-STS-TE-9042B). | B | I | Gonzalo Pena | McD | 2019-12-05 | Gonzalo Pena | Const | 2019-12-17 | Gonzalo Pena | 2019-12-23 | Michael Law
STS-01 | STS-01 | PI14673 | Verified | Complete tubing connection PIT-9407A/B | A | I | James Tanner | McD | 2019-12-10 | James Tanner | Const | 2019-12-16 | James Tanner | 2019-12-16 | Michael Law
STS-01 | STS-01 | PI14809 | Verified | NEED TO INSTALL TUBE BUNDLE FOR 1C-STS-PIT-9047A & 1C-STS-PIT-9047B - DUPLICATE PUNCH ITEM - JOHN S. | A | I | James Tanner | McD | 2019-12-15 | James Tanner | Const |  |  | 2019-12-15 | Eric Policarpio
STS-01 | STS-01 | PI14810 | Verified | 1C-HTS-CAB-0302-- NEED TO CLEAN BOX INSIDE AND OUT. WATER INSIDE. | B | I | James Tanner | McD | 2019-12-15 | James Tanner | Const |  |  | 2019-12-21 | John Sullivan
STS-01 | STS-01 | PI14811 | Verified | 1C-STS-PIT-9064-NEED TO SHRINK BOOT ON TUBE BUNDLE(1C-HTS-CAB-0303) | B | I | Gonzalo Pena | McD | 2019-12-15 | Gonzalo Pena | Const | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Shannon Scott
STS-01 | STS-01 | PI14812 | Verified | 1C-STS-PIT-9064-NEED TO TIGHTEN LOCK NUT ON BOOT.(1C-HTS-CAB-0303) | B | I | James Tanner | McD | 2019-12-15 | James Tanner | Const | 2019-12-17 | Gonzalo Pena | 2019-12-21 | John Sullivan
STS-01 | STS-01 | PI14813 | Verified | NEED TO INSTALL TUBE BUNDLE FOR 1C-STS-PIT-9056A & 1C-STS-PIT-9056B(1C-HTS-CAB-0303) | A | I | James Tanner | McD | 2019-12-15 | James Tanner | Const | 2019-12-16 | James Tanner | 2019-12-16 | John Sullivan
STS-01 | STS-01 | PI14814 | Verified | 1C-HTS-CAB-0303- NEED TO CLEAN BOX INSIDE AND OUT. | B | I | James Tanner | McD | 2019-12-15 | James Tanner | Const | 2019-12-17 | John Sullivan | 2019-12-18 | John Sullivan
STS-01 | STS-01 | PI15054 | Verified | Clean up inside 1C-NQS-PNL-1000, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
STS-01 | STS-01 | PI15055 | Verified | Wire with bare ring lug not terminated 1C-NQS-PNL-1000, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-31 | Jared Stimpson | 2020-02-15 | Shannon Scott
STS-01 | STS-01 | PI15056 | Verified | Replace wiring duct covers inside 1C-NQS-PNL-1000, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
STS-01 | STS-01 | PI15057 | Verified | Heat shrink cable tags inside 1C-NQS-PNL-1000, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
STS-01 | STS-01 | PI15058 | Verified | Replace cable/wire tags that are too big to heat shrink inside 1C-NQS-PNL-1000, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
STS-01 | STS-01 | PI15059 | Verified | Replace door panel at 1C-NQS-PNL-1000, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
STS-01 | STS-01 | PI15060 | Verified | Cable from SEL-2407 to outdoor antena needs cable tray or conduit, currently stretched tight at an angle from cable tray to building penetration, 1C-NQS-PNL-1000, North end of Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-04-01 | Chris Colvin | 2020-04-07 | Bernard Stasse
STS-01 | STS-01 | PI16682 | Verified | 1C-STS-GEN-9000 - Near the brush rigging assembly, none of the pant leg washers are turned over. One of the pant leg tabs is supposed to be bent over the hex bolt, and the other is bent over the flats on the nut. | B | M | Shane Crowe | McD | 2020-02-07 | Shane Crowe | Comm | 2020-02-24 | Shane Crowe | 2020-03-05 | Nelson Eichelberger
STS-01 | STS-01 | PI16683 | Verified | 1C-STS-GEN-9000 - The STG, there is condensate around the collector rings, but the brushes are not installed yet. | B | M | William Mitchell | McD | 2020-02-07 | William Mitchell | Comm | 2020-03-09 | Michael Law | 2020-04-07 | Bernard Stasse
STS-01 | STS-01 | PI17445 | Verified | 1C-STS-PT-9056A is leaking and needs to be repaired. It is welded, needs to be cut and swaged. | B | I | James Beech | McD | 2020-03-02 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-03-07 | Albert Burge
STS-01 | STS-01 | PI17446 | Verified | 1C-STS-PT-9056B is leaking and needs to be repaired. It is welded, needs to be cut and swaged. | B | I | James Beech | McD | 2020-03-02 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-03-07 | Albert Burge
STS-01 | STS-01 | PI17447 | Verified | 1C-STS-PIT-9047A is leaking and needs to be repaired. It is welded, needs to be cut and swaged. | B | I | James Beech | McD | 2020-03-02 | James Beech | Comm | 2020-03-05 | Tim Green | 2020-03-07 | Albert Burge
STS-01 | STS-01 | PI18177 | Verified | Generator shaft voltage out of range, Grounding strap issue | C | E | Jonathan Donham | TOS | 2020-03-23 | Jonathan Donham | Comm | 2020-04-30 | Jonathan Donham | 2020-04-30 | Jonathan Donham
SWS-01 | SWS-01 | PI04330 | Verified | Tag motors 10-SWS-M-0100A and 10-SWS-M-0100B. | C | E | Dustin Futrell | McD | 2019-08-20 | Dustin Futrell | Const | 2019-08-27 | Dustin Futrell | 2019-08-27 | Albert Burge
SWS-01 | SWS-01 | PI04331 | Verified | Install 10-SWS-PI-0104A at service water pump A. | A | I | Gonzalo Pena | McD | 2019-08-20 | Gonzalo Pena | Const | 2019-08-27 | Gonzalo Pena | 2019-08-27 | Albert Burge
SWS-01 | SWS-01 | PI04332 | Verified | Replace plastic plug with SS plug on 10-SWS-PI-0106A & B and 10-SWS-PI-0104B (and A when installed). | B | I | Gonzalo Pena | McD | 2019-08-20 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-20 | Martin Perry
SWS-01 | SWS-01 | PI04333 | Verified | Replace service water pump tag 10-SWS-P-0100A. Currently both pumps are tagged B. The pump A tag is on the attached to the motor lifting eye. | C | M | Shane Crowe | McD | 2019-08-20 | Shane Crowe | Const | 2019-09-17 | Shane Crowe | 2019-10-05 | Mike Tabbert
SWS-01 | SWS-01 | PI04334 | Verified | Grout pipe support between service water pumps. | C | C | Johnny Campbell | McD | 2019-08-20 | Johnny Campbell | Const | 2019-09-12 | Jack Fields | 2019-09-24 | Kelvin Cook
SWS-01 | SWS-01 | PI04335 | Verified | Clean bucket for 10-SWS-M-0100B in MCC-0006B in the cooling tower PDC. | A | E | Dustin Futrell | McD | 2019-08-20 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
SWS-01 | SWS-01 | PI04336 | Verified | Clean bucket for 10-SWS-M-0100A in MCC-0006A in the cooling tower PDC. | A | E | Dustin Futrell | McD | 2019-08-20 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
SWS-01 | SWS-01 | PI04337 | Verified | Dress cables for the motor insight in bucket 10-SWS-M-0100B in MCC-0006B in the cooling tower PDC. | A | E | Dustin Futrell | McD | 2019-08-20 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
SWS-01 | SWS-01 | PI04338 | Verified | Check service water motor buckets for missing hardware, spacers, etc. in MCC-006A/B in the cooling tower PDC. | A | E | Dustin Futrell | McD | 2019-08-20 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
SWS-01 | SWS-01 | PI04339 | Verified | Seal conduits in 10-SWS-M-0100A & B in MCC-0006A & B in the cooling tower PDC. | A | E | Dustin Futrell | McD | 2019-08-20 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-10-05 | Mike Tabbert
SWS-01 | SWS-01 | PI04340 | Verified | Install 10-SWS-PI-0728A & B in the demin. Building. | A | I | Gonzalo Pena | McD | 2019-08-20 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-10 | Martin Perry
SWS-01 | SWS-01 | PI04341 | Verified | 10-SWS-PV-0110, Tighten sealtight connectors | A | E | Dustin Futrell | McD | 2019-08-20 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-28 | Mike Tabbert
SWS-01 | SWS-01 | PI04342 | Verified | 10-SWS-PIT-0110, Ground sealtight. | A | E | Dustin Futrell | McD | 2019-08-20 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-28 | Mike Tabbert
SWS-01 | SWS-01 | PI04343 | Verified | 10-SWS-M-0100A, Ground stub-ups at motor, tie into grid ground. | A | E | Dustin Futrell | McD | 2019-08-20 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-28 | Mike Tabbert
SWS-01 | SWS-01 | PI04344 | Verified | 10SWSK0001, Terminate motor space heater when temporary power is removed. | A | E | Dustin Futrell | McD | 2019-08-20 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-28 | Mike Tabbert
SWS-01 | SWS-01 | PI04345 | Verified | 10SWSK0002, Terminate motor space heater when temporary power is removed. | A | E | Dustin Futrell | McD | 2019-08-20 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-28 | Mike Tabbert
SWS-01 | SWS-01 | PI04346 | Verified | General cleanup at service water pumps. | B | E | Dustin Futrell | McD | 2019-08-20 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-28 | Mike Tabbert
SWS-01 | SWS-01 | PI04821 | Verified | ISO 1A-SWS-PD-P41-0308-01 item 9 1A-SWS-QC-0308 is not installed | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-17 | Damon Turner | 2019-10-07 | Kelvin Cook
SWS-01 | SWS-01 | PI04822 | Verified | ISO 1A-SWS-PD-P41-0317-01 pipe support 1A-SWS-PD-HGR-0117 loose 2 bolt clamp | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-24 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04823 | Verified | ISO 1A-SWS-PD-P41-0317-01 pipe support 1A-SWS-PD-HGR-0119 install nut to top of turnbuckle and lock down. 2 thread min at bottom of eyebolt is required | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-24 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04824 | Verified | ISO 1A-SWS-PD-P41-0317-02 item 6 1A-SWS-QC-0317 is not installed | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04825 | Verified | ISO 1A-SWS-PD-P41-0318-01 item 9 1A-SWS-QC-0318 is not installed | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04826 | Verified | ISO 1A-SWS-PD-P41-0319-01 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-17 | Damon Turner | 2019-10-07 | Kelvin Cook
SWS-01 | SWS-01 | PI04827 | Verified | ISO 1B-SWS-PD-P41-0308-01 item 9 1B-SWS-QC-0308 is not installed | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-17 | Damon Turner | 2019-10-07 | Kelvin Cook
SWS-01 | SWS-01 | PI04828 | Verified | ISO 1B-SWS-PD-P41-0310-01 missing valve handle cover on 1B-SWS-V-0310 | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04829 | Verified | ISO 1B-SWS-PD-P41-0318-01 item 9 1B-SWS-QC-0318 is not installed | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04830 | Verified | ISO 1B-SWS-PD-P41-0318-01 bolts are too short at the UG flange connection | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-18 | Damon Turner | 2019-10-03 | Kelvin Cook
SWS-01 | SWS-01 | PI04831 | Verified | ISO 1B-SWS-PD-P41-0320-01 bolts are too short at the UG flange connection | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-18 | Damon Turner | 2019-10-03 | Kelvin Cook
SWS-01 | SWS-01 | PI04832 | Verified | ISO 1B-SWS-PD-P41-0320-01 item 9 1B-SWS-QC-0320 is not installed | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04833 | Verified | ISO 1B-SWS-PD-P41-0321-01 item 9 1B-SWS-QC-0321 is not installed | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04834 | Verified | ISO 1B-SWS-PD-P41-0321-01 pipe support 1B-SWS-PD-HGR-0039 loose ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-23 | Bobby Williams | 2019-09-24 | Kelvin Cook
SWS-01 | SWS-01 | PI04835 | Verified | ISO 1B-SWS-PD-P41-0321-01 wrong size bolts at the UG flange connection | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-18 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04836 | Verified | ISO 1B-SWS-PD-P41-0324-02 pipe support 1B-SWS-PD-HGR-0011 & 0015 missing ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-30 | Bobby Williams | 2019-10-03 | Kelvin Cook
SWS-01 | SWS-01 | PI04837 | Verified | ISO 1B-SWS-PD-P41-0329-01 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-17 | Damon Turner | 2019-10-07 | Kelvin Cook
SWS-01 | SWS-01 | PI04838 | Verified | ISO 1B-SWS-PD-P41-0360-01 item 9 1B-SWS-QC-0360 is not installed | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-17 | Damon Turner | 2019-10-07 | Kelvin Cook
SWS-01 | SWS-01 | PI04839 | Verified | ISO 10-SWS-PD-P40-0232-01 pipe support 10-SWS-PD-HGR-0033 Is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04840 | Verified | ISO 10-SWS-PD-P40-0238-01 specialty item 10-SWS-QC-0238 is not installed | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const |  |  | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04841 | Verified | ISO 10-SWS-PD-P40-0242-01 pipe support 10-SWS-PD-HGR-0208 has loose 2 bolt clamp | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04842 | Verified | ISO 10-SWS-PD-P40-0244-01 pipe support 10-SWS-PD-HGR-0212 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04843 | Verified | ISO 10-SWS-PD-P41-0101-01 threaded cap for valve 10-SWS-V-0103A is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-18 | Damon Turner | 2019-09-24 | Kelvin Cook
SWS-01 | SWS-01 | PI04844 | Verified | ISO 10-SWS-PD-P41-0103-01 threaded cap for valve 10-SWS-V-0103B is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SWS-01 | SWS-01 | PI04845 | Verified | ISO 10-SWS-PD-P41-0106-02 threaded cap for valve 10-SWS-V-0119 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SWS-01 | SWS-01 | PI04846 | Verified | ISO 10-SWS-PD-P41-0108-03 instrument 10-SWS-PP-0108 I not intalled | A | I | Gonzalo Pena | McD | 2019-09-10 | Gonzalo Pena | Const | 2019-09-11 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
SWS-01 | SWS-01 | PI04847 | Verified | ISO 10-SWS-PD-P41-0223-01 Is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-03 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04848 | Verified | ISO 10-SWS-PD-P41-0242-01 install plug at valve 10-SWS-V-0442 | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-18 | Damon Turner | 2019-09-24 | Kelvin Cook
SWS-01 | SWS-01 | PI04849 | Verified | ISO 10-SWS-PD-P41-0244-01 install toe nipple and cap at valve 10-SWS-V-0441 | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-18 | Damon Turner | 2019-09-24 | Kelvin Cook
SWS-01 | SWS-01 | PI04850 | Verified | ISO 10-SWS-PD-P41-0260-01 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-03 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04851 | Verified | ISO 10-SWS-PD-P41-0260-02 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-03 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04852 | Verified | ISO 10-SWS-PD-P41-0261-01 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-03 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04853 | Verified | ISO 10-SWS-PD-P41-0262-01 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-03 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04854 | Verified | ISO 10-SWS-PD-P41-0263-01 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-03 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04855 | Verified | ISO 10-SWS-PD-P41-0263-02 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-03 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04856 | Verified | ISO 10-SWS-PD-P41-0263-03 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-03 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04857 | Verified | ISO 10-SWS-PD-P41-0264-01 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-03 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04858 | Verified | ISO 10-SWS-PD-P41-0270-01 is not intalled | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04859 | Verified | ISO 10-SWS-PD-P41-0332-01 missing valve handle stop at 10-SWS-V-0332 | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SWS-01 | SWS-01 | PI04860 | Verified | ISO 10-SWS-PD-P41-0332-01 install 4 steel bolt the same length at the UG flange connection | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SWS-01 | SWS-01 | PI04861 | Verified | ISO 10-SWS-PD-P41-0337-01 pipe support 10-SWS-PD-HGR-0045 & 0047 are not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04862 | Verified | ISO 10-SWS-PD-P41-0337-01 remove plastic flange cover. Install gasket and install stud bolts at the UG flange connection | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-09-18 | Kelvin Cook
SWS-01 | SWS-01 | PI04863 | Verified | ISO 10-SWS-PD-P41-0337-02 pipe support 10-SWS-PD-HGR-0048 loose 3 bolt clamp | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04864 | Verified | ISO 10-SWS-PD-P41-0337-02 pipe support 10-SWS-PD-HGR-0049 need full thread engagement at eyebolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04865 | Verified | ISO 10-SWS-PD-P41-0337-02 pipe support 10-SWS-PD-HGR-0052 need full thread engagement at eyebolt & tighten lock nuts at eyebolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04866 | Verified | ISO 10-SWS-PD-P41-0337-02 pipe support 10-SWS-PD-HGR-0050 has loose ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04867 | Verified | ISO 10-SWS-PD-P41-0337-02 pipe support 10-SWS-PD-HGR-0058 has loose clamp at shoe | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04868 | Verified | ISO 10-SWS-PD-P41-0337-03 pipe support 10-SWS-PD-HGR-0061 is not installed | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-07 | Bobby Williams | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04869 | Verified | ISO 10-SWS-PD-P41-0337-04 pipe support 10-SWS-PD-HGR-0066 tighten clamps | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04870 | Verified | ISO 10-SWS-PD-P41-0339-01 pipe support 10-SWS-PD-HGR-0071 eyebolt requires full thread engagement | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04871 | Verified | ISO 10-SWS-PD-P41-0339-01 pipe support 10-SWS-PD-HGR-0073 has loose 3 bolt clamp | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04872 | Verified | ISO 10-SWS-PD-P41-0339-01 pipe support 10-SWS-PD-HGR-0076 out plumb | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04873 | Verified | ISO 10-SWS-PD-P41-0339-03 pipe support 10-SWS-PD-HGR-0100 move all threaded rod 2" to the south to get off of side of SAS pipe | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04874 | Verified | ISO 10-SWS-PD-P41-0339-04 pipe support 10-SWS-PD-HGR-0109 has loose clamp on pipe | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04875 | Verified | ISO 10-SWS-PD-P41-0340-01 pipe support 10-SWS-PD-HGR-0041 has loose ubolt | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04876 | Verified | ISO 10-SWS-PD-P41-0340-01 item 9 10-SWS-QC-0340 is not installed | B | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04877 | Verified | ISO 10-SWS-PD-P41-0342-01 pipe support 10-SWS-PD-HGR-0062 extend HGR to the west, drill new holes and plumb pipe up. | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04878 | Verified | ISO 10-SWS-PD-P41-0345-01 rotate valve 10-SWS-V-0345 body to west for operator friendly | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-13 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04879 | Verified | ISO 10-SWS-PD-P41-0401-01 instrument 10-SWS-PI-0728A is not installed | A | I | Gonzalo Pena | McD | 2019-09-10 | Gonzalo Pena | Const | 2019-09-11 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
SWS-01 | SWS-01 | PI04880 | Verified | ISO 10-SWS-PD-P41-0401-02 instrument 10-SWS-PI-0728B is not installed | A | I | Gonzalo Pena | McD | 2019-09-10 | Gonzalo Pena | Const | 2019-09-11 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
SWS-01 | SWS-01 | PI04881 | Verified | ISO 10-SWS-PD-P41-0421-01 need to complete fit on item 4 | A | P | James Beech | McD | 2019-09-10 | James Beech | Const | 2019-10-07 | Bobby Williams | 2019-11-04 | Kelvin Cook
SWS-01 | SWS-01 | PI04882 | Verified | ISO 10-SWS-PD-P41-0422-01 need to complete fit on item 2 | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04883 | Verified | ISO 10-SWS-337 - sloping issue - level pipe. SE corner, N/S run in STG bldg. | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04884 | Verified | 1A-SWS-P41-013-01 - replace bent u-bolt. West side of HRSG 1A, at column 11A. | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-30 | Bobby Williams | 2019-10-03 | Kelvin Cook
SWS-01 | SWS-01 | PI04885 | Verified | 10-SWS-0244 - Fix flange at U/G connection. NE corner of water treatment bldg. | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04886 | Verified | 10-SWS-P41-0366-02 - complete installation. NW corner of cooling tower. | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-05 | Kelvin Cook
SWS-01 | SWS-01 | PI04887 | Verified | 1A-SWS-P41-0320-01 - Install proper olts at U/G flange connection. East side of HRSG 1A. | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-18 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04888 | Verified | 1A-SWS-P41-0321-01 - Install proper bolts at U/G flange connection. HRSG A ammonia skid. | A | P | Damon Turner | McD | 2019-09-10 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-08 | Kelvin Cook
SWS-01 | SWS-01 | PI04890 | Verified | Tag all valves. | C | P | James Beech | McD | 2019-09-10 | James Beech | Const | 2020-02-27 | James Beech | 2020-02-27 | Kelvin Cook
SWS-01 | SWS-01 | PI06099 | Verified | LK-10-SWS-PD-P40-0242-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Tom Noble
SWS-01 | SWS-01 | PI06100 | Verified | LK-10-SWS-PD-P41-0223-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Bobby Williams | 2019-10-07 | Tom Noble
SWS-01 | SWS-01 | PI06101 | Verified | LK-10-SWS-PD-P41-0260-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-10-02 | Tom Noble
SWS-01 | SWS-01 | PI06102 | Verified | LK-10-SWS-PD-P41-0262-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-10-01 | Tom Noble
SWS-01 | SWS-01 | PI06103 | Verified | LK-10-SWS-PD-P41-0263-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-04 | Tom Noble
SWS-01 | SWS-01 | PI06104 | Verified | LK-10-SWS-PD-P41-0263-03 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-09-25 | Tom Noble
SWS-01 | SWS-01 | PI06105 | Verified | LK-10-SWS-PD-P41-0264-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-09-25 | Tom Noble
SWS-01 | SWS-01 | PI06106 | Verified | LK-10-SWS-PD-P41-0270-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-10-08 | Tom Noble
SWS-01 | SWS-01 | PI06109 | Verified | LK-10-SWS-PD-P41-0346-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-07 | Damon Turner | 2019-10-07 | Tom Noble
SWS-01 | SWS-01 | PI06112 | Verified | LK-10-SWS-PD-P41-0376-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-07 | Damon Turner | 2019-10-07 | Tom Noble
SWS-01 | SWS-01 | PI06113 | Verified | LK-1B-SWS-PD-P41-0329-01 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Lucas Foster
SWS-01 | SWS-01 | PI06114 | Verified | LK-1B-SWS-PD-P41-0329-02 - Needs Welds Cleared | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-17 | Lucas Foster
SWS-01 | SWS-01 | PI09370 | Verified | Complete clean & close on 10-SWS-WS-0700A & B. | B | M | Shane Crowe | McD | 2019-10-09 | Shane Crowe | Const |  |  | 2019-11-01 | Joshua Sturgeon
SWS-01 | SWS-01 | PI09371 | Verified | Complete clean & close on 10-SWS-T-0700A & B. | B | M | Shane Crowe | McD | 2019-10-09 | Shane Crowe | Const |  |  | 2019-11-01 | Joshua Sturgeon
SWS-01 | SWS-01 | PI09372 | Verified | Complete hold downs on tanks 10-SWS-T-0700A & B. | B | M | Shane Crowe | McD | 2019-10-09 | Shane Crowe | Const |  |  | 2019-11-01 | Joshua Sturgeon
SWS-01 | SWS-01 | PI10255 | Verified | Install Service Water supply to Hydrogen Storage and Unloading Area, Line No. 1-10-SWS-0340, Isolation Valve; 10-SWS-V-0340, and Quick Disconnect Fitting; 10-SWS-QC-0340. | B | P | James Beech | McD | 2019-10-24 | James Beech | Comm |  |  | 2019-10-31 | J.L. Bickham
SWS-01 | SWS-01 | PI13707 | Verified | Remove paint splatter from10-SWS-V-0101; Service Water Pump Suction Isolation Valve, Line No. 8-10SWS-0115 | C | X | Jerry Smith | McD | 2019-12-01 | Jerry Smith | Comm | 2020-03-20 | Jerry Smith | 2020-04-08 | Bernard Stasse
SWS-01 | SWS-01 | PI13709 | Verified | Tag all system components . No tags at all on almost all components - All operating valves and components are need to be positively identified during the walk and traceable to drawings | C | P | Tim Green | McD | 2019-12-01 | Tim Green | Comm | 2021-01-22 | Eric Policarpio | 2021-01-22 | Eric Policarpio
SWS-01 | SWS-01 | PI13710 | Verified | Instrument tubing at 10-SWS-PI-0100A; Service Water Pump A Suction Pressure Indicator interferes with 10-SWS-V-0100A isolation valve operation, extend tubing, Line No. 8-10-SWS-0104 | C | I | Gonzalo Pena | McD | 2019-12-01 | Gonzalo Pena | Comm | 2020-01-15 | Gonzalo Pena | 2020-01-20 | Shannon Scott
SWS-01 | SWS-01 | PI13711 | Verified | Both A & B Service Water Pump Motors need tag | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-09 | Bobby Williams | 2020-01-13 | Shannon Scott
SWS-01 | SWS-01 | PI13712 | Verified | Install 10-SWS-PI-0106A; Service Water Pump A Discharge Pressure Indicator | B | I | Gonzalo Pena | McD | 2019-12-01 | Gonzalo Pena | Comm | 2019-12-05 | James Tanner | 2019-12-18 | Shannon Scott
SWS-01 | SWS-01 | PI13713 | Verified | 10-SWS-V-0112A; Service Water Pump A Catch Pan Drain Valve not installed, Line No. 0.5-10-SWS-0110 | B | P | James Tanner | McD | 2019-12-01 | James Tanner | Comm | 2020-02-12 | James Tanner | 2020-02-17 | Shannon Scott
SWS-01 | SWS-01 | PI13714 | Verified | 10-SWS-V-0112B; Service Water Pump b Catch Pan Drain Valve not installed, Line No. 0.5-SWS-0112 | B | P | James Tanner | McD | 2019-12-01 | James Tanner | Comm | 2020-02-12 | James Tanner | 2020-02-17 | Shannon Scott
SWS-01 | SWS-01 | PI13715 | Verified | Route 10-SWS-V-0103A; Service Water Pump A Suction Drain Valve to hub | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-08 | Bernard Stasse
SWS-01 | SWS-01 | PI13716 | Verified | Route 10-SWS-V-0103B; Service Water Pump B Suction Drain Valve to hub | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-08 | Bernard Stasse
SWS-01 | SWS-01 | PI13717 | Verified | Remove carbon contamination from SS tubing at 10-SWS-PI-0110; Service Water Pump B Discharge Pressure Indicator | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-20 | Shannon Scott
SWS-01 | SWS-01 | PI13718 | Verified | Tighten instrument tubing lock nut inside 10-SWS-PIT-0110; Service Water Pump B Discharge Pressure Indicating Transmitter inside instrument cabinet | B | I | Gonzalo Pena | McD | 2019-12-01 | Gonzalo Pena | Comm | 2019-12-05 | James Tanner | 2019-12-18 | Shannon Scott
SWS-01 | SWS-01 | PI13719 | Verified | Power cable conduit to 10-SWS-PIT-0110; Service Water Pump B Discharge Pressure Indicating Transmitter is missing condolet | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-04-29 | Matt Gilmore | 2020-07-10 | Dave Goldak
SWS-01 | SWS-01 | PI13720 | Verified | Straighten 10-SWS-PIT-0110; Service Water Pump B Discharge Pressure Indicating Transmitter conduit condulet cover | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-04-29 | Matt Gilmore | 2020-07-10 | Dave Goldak
SWS-01 | SWS-01 | PI13721 | Verified | Remove carbon contamination from SS IA tubing to 10-SWS-PC-0110; Service Water Pump Discharge Header Recirc Valve | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-20 | Shannon Scott
SWS-01 | SWS-01 | PI13722 | Verified | Pipe support U-Bolt needs double nuts downstream of 10-SWS-PC-0110; Service Water Pump Discharge Header Recirc Valve | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-09 | Bobby Williams | 2020-01-13 | Shannon Scott
SWS-01 | SWS-01 | PI13723 | Verified | Horizontal power cable conduit at N side of Service Water Pump Skid needs support | C | E | Chris Colvin | McD | 2019-12-01 | Chris Colvin | Comm | 2020-05-04 | Matt Gilmore | 2020-07-10 | Dave Goldak
SWS-01 | SWS-01 | PI13724 | Verified | Remove unused bolts, point and patch concrete at N side of Service Water Pump A foundation | C | C | Johnny Campbell | McD | 2019-12-01 | Johnny Campbell | Comm |  |  | 2019-12-14 | Jack Fields
SWS-01 | SWS-01 | PI13725 | Verified | Clean up Service Water Pump Skid | C | C | Johnny Campbell | McD | 2019-12-01 | Johnny Campbell | Comm |  |  | 2019-12-14 | Jack Fields
SWS-01 | SWS-01 | PI13726 | Verified | Remove rust and cold gal supports at Service Water Pump Skid | C | X | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-02-05 | Blake Boudreaux
SWS-01 | SWS-01 | PI13727 | Verified | Line No. 2-10-SWS-0333 to Thickener/Filter Press Polymer Skids needs support | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-02-12 | Shannon Scott
SWS-01 | SWS-01 | PI13728 | Verified | Line No. 3-10-SWS-0334 to Filter Press Feed Pumps needs support | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-02-12 | Shannon Scott
SWS-01 | SWS-01 | PI13729 | Verified | Line No. 1-10-SWS-0376 to Filter Press House Second Floor is missing nut on U-Bolt | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-09 | Bobby Williams | 2020-02-12 | Shannon Scott
SWS-01 | SWS-01 | PI13730 | Verified | Chicago Fitting missing at Makeup Water Treatment Area Utility Station, Line No. 1-10-SWS-0223 | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-09 | Bobby Williams | 2020-02-12 | Shannon Scott
SWS-01 | SWS-01 | PI13731 | Verified | Flange bolts are too long at 10-SWS-QC-0238; Temporary Demin Water Treatment Trailer quick disconnect fitting, Line No. 6-10-SWS-0238 | D | P | Tim Green | McD | 2019-12-01 | Tim Green | Comm | 2020-05-29 | James Beech | 2020-07-31 | Nelson Eichelberger
SWS-01 | SWS-01 | PI13732 | Verified | Pipe support base plate bolts too long at Temporary Demin Water Treatment Trailer, Line No. 6-10-SWS-0238 | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-09 | Bobby Williams | 2020-01-23 | Blake Boudreaux
SWS-01 | SWS-01 | PI13733 | Verified | Remove concrete splatter from Temporary Demin Water Treatment Trailer pipe support, Line No. 6-10-SWS-0238 | C | C | Alan Huntsman | McD | 2019-12-01 | Alan Huntsman | Comm | 2020-02-20 | Alan Huntsman | 2020-02-21 | Keith Pollock
SWS-01 | SWS-01 | PI13734 | Verified | Are bolts at first above ground flanges supposed to be teflon coated, engineering to verify - replace with teflon coated bolts at ground flange service water line outside of north east water treatment bldg | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-04-07 | Bernard Stasse
SWS-01 | SWS-01 | PI13735 | Verified | Pipe support base plate bolts too long at Hydrogen Storage and Unloading Area, Line No. 6-10-SWS-0340 | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2019-12-05 | Kelvin Cook | 2020-01-08 | Blake Boudreaux
SWS-01 | SWS-01 | PI13736 | Verified | Seal Service Water piping penetrations at N side of Demin Water Building | C | C | Alan Huntsman | McD | 2019-12-01 | Alan Huntsman | Comm | 2020-03-13 | Johnny Campbell | 2020-04-07 | Bernard Stasse
SWS-01 | SWS-01 | PI13737 | Verified | Back fill around Service Water piping stub ups at N side of Demin Water Building | C | C | Brooks Baker | McD | 2019-12-01 | Brooks Baker | Comm | 2020-04-01 | Brooks Baker | 2020-04-07 | Bernard Stasse
SWS-01 | SWS-01 | PI13738 | Verified | Line No. 3-1A-SWS-0324 support on W side of GT A Lube Oil Enclosure is inadequate, scrap angle iron welded to main support | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-25 | James Beech | 2020-02-12 | Shannon Scott
SWS-01 | SWS-01 | PI13739 | Verified | Pipe support base plate is loose at 1B-SWS-V-0308; Service Water Drop Isolation Valve, Line No. 1-1B-SWS-0308, NW side GT 1B | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-25 | James Beech | 2020-02-12 | Shannon Scott
SWS-01 | SWS-01 | PI13740 | Verified | Shorten pipe support base plate hold down anchors at 10-SWS-V-0330; Service Water Drop Isolation Valve, Line No. 1-10-SWS-0330, Cooling Tower Chemical Storage and Unloading Area | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-15 | Bobby Williams | 2020-01-23 | Blake Boudreaux
SWS-01 | SWS-01 | PI13741 | Verified | 10-SWS-V-0330; Service Water Drop Isolation Valve U-Bolt support needs double nuts, Line No.1-10-SWS-0331, Circ Water Pump Area | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-09 | Bobby Williams | 2020-01-23 | Blake Boudreaux
SWS-01 | SWS-01 | PI13742 | Verified | Remove pipe support plate from Cooling Tower Basin wall, repair concrete and replace support place at 10-SWS-V-0332; Service Water Drop Isolation Valve, Line No. 1-10-SWS-0332, Cooling Tower Area N side | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-03-13 | Johnny Campbell | 2020-04-08 | Bernard Stasse
SWS-01 | SWS-01 | PI13743 | Verified | Need additional support at Cooling Tower Sulfuric Acid Injection Line No. 0.75-10-SWS-0365, S end of Cooling Tower Basin | C | P | Kelvin Cook | McD | 2019-12-01 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-08 | Bernard Stasse
SWS-01 | SWS-01 | PI13744 | Verified | U-Bolt support missing nuts at 1A-SWS-V-0317; Service Water Drop Isolation Valve, Line No. 1-1A-SWS-0317, 1A Boiler Feed Pump Platform | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-25 | James Beech | 2020-02-12 | Shannon Scott
SWS-01 | SWS-01 | PI13745 | Verified | Valve handle plastic cover torn at 1A-SWS-V-0317; Service Water Drop Isolation Valve, Line No. 1-1A-SWS-0317, 1A Boiler Feed Pump Platform | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-25 | James Beech | 2020-02-12 | Shannon Scott
SWS-01 | SWS-01 | PI13746 | Verified | Chicago fitting missing at 1B Boiler Feed Pump Platform Service Water Drop, Line No. 1-1B-SWS-0329 | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-08 | Blake Boudreaux
SWS-01 | SWS-01 | PI13747 | Verified | Loose U-Bolt nuts at E Side 1A HRSG Service Water Drop, Line No. 1-SWS-0320 | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-25 | James Beech | 2020-02-12 | Shannon Scott
SWS-01 | SWS-01 | PI13748 | Verified | Chicago fitting missing at E Side 1A HRSG Service Water Drop, Line No. 1-SWS-0320 | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-02-24 | Tim Green | 2020-04-08 | Bernard Stasse
SWS-01 | SWS-01 | PI13749 | Verified | U-Bolt support needs double nuts at 10-SWS-V-0344; Service Water Drop Isolation Valve, Line No. 1-10-SWS-0344, NW side STG Bldg Ground Floor | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-08 | Blake Boudreaux
SWS-01 | SWS-01 | PI13750 | Verified | Isolation valve missing stop at 10SWS-V-0348; Service Water Drop Isolation Valve, Line No. 1-10-SWS-0348, SW Side STG Ground Floor | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-08 | Blake Boudreaux
SWS-01 | SWS-01 | PI13751 | Verified | Chicago fitting missing at 10-SWS-V-0347; Service Water Drop Isolation Valve, Line No. 1-10-SWS-0347, S side STG Bldg Mezzanine | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-08 | Blake Boudreaux
SWS-01 | SWS-01 | PI13752 | Verified | Chicago fitting missing at 10-SWS-V-0343; Service Water Drop Isolation Valve, Line No. 1-10-SWS-0343, NW side STG Mezzanine | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-08 | Blake Boudreaux
SWS-01 | SWS-01 | PI13753 | Verified | Need additional support at 10-SWS-V-0346; Service Water Drop Isolation Valve, Line No. 1-10-SWS-0346, E side STG Turbine Deck | D | P | Michael Law | McD | 2019-12-01 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-07-31 | Nelson Eichelberger
SWS-01 | SWS-01 | PI13754 | Verified | Repair leak at 10-SWS-PI-0728B; Line No. 2-10-SWS-0404, upstream of Softner Skid B, Demin Water Bldg | B | I | Gonzalo Pena | McD | 2019-12-01 | Gonzalo Pena | Comm | 2020-03-09 | Tim Green | 2020-04-08 | Bernard Stasse
SWS-01 | SWS-01 | PI13755 | Verified | Need additional support at 10-SWS-V-0202; Service Water Drop Isolation Valve, Line No. 1-10-SWS-0234, NW corner Demin Water Bldg | D | P | Michael Law | McD | 2019-12-01 | Michael Law | Comm | 2020-05-11 | Michael Law | 2020-07-10 | Dave Goldak
SWS-01 | SWS-01 | PI13756 | Verified | Need additional support at 10-SWS-V-0206; Service Water Drop Isolation Valve, Line No. 1-10-SWS-0227, Batch Neutraliation Area Utility Station, NW side Demin Water Bldg outside | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-05-08 | James Beech | 2020-07-10 | Dave Goldak
SWS-01 | SWS-01 | PI13757 | Verified | Incorrect shoe size on support at Line No. 2-10-MWS-0272 inside Clarifier Polymer Bldg | C | P | Kelvin Cook | McD | 2019-12-01 | Kelvin Cook | Comm | 2020-02-28 | Kelvin Cook | 2020-04-08 | Bernard Stasse
SWS-01 | SWS-01 | PI13758 | Verified | Line No. 2-10-MWS-0272 inside Clarifier Polymer Bldg is loose needs additional support | C | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-05-27 | James Beech | 2020-08-06 | Nelson Eichelberger
SWS-01 | SWS-01 | PI13759 | Verified | Seal all Service Water piping penetrations a Clarifier Polymer Bld | C | C | Alan Huntsman | McD | 2019-12-01 | Alan Huntsman | Comm | 2020-03-18 | Johnny Campbell | 2020-04-08 | Bernard Stasse
SWS-01 | SWS-01 | PI13760 | Verified | Need extra clamps on Line No. 0.75-10-SWS-0366, Service Water to Sodium Hypochlorite Injection, W end of Cooling Tower | D | P | James Beech | McD | 2019-12-01 | James Beech | Comm | 2020-05-27 | James Beech | 2020-08-06 | Nelson Eichelberger
SWS-01 | SWS-01 | PI14872 | Verified | SWS Line to the MWS Polymer Mixing Skid has pipe leak at the AG/UG connection. Pipe appears to be broken in the concrete (LK-10-SWS-ME-PID-0002) | B | P | James Beech | McD | 2019-12-24 | James Beech | Comm | 2020-02-27 | James Beech | 2020-04-07 | Bernard Stasse
SWS-01 | SWS-01 | PI18092 | Verified | 10-SWS-P-0100A, 10-SWS-P-0100B, 10-SWS-PV-0110 - SW Pumps P-100A/B control setpoint (105 psig) is higher than the deadhead pressure of 101.3 psig. Pump Reliability: Service Water Pumps P-100A/B minimum flow (i.e. deadhead) conditions are 101.3 psig at 191.5 gpm. 10-SWS-PV-0110 serves as minimum flow protection using pressure control. According to page 4 of the control narrative (LK-00-SWS-IC-LCN-0000), the valve remains cracked at 5% open until the pressure reaches set point of 105 psig. | C | M | Charles Worthington | McD | 2020-03-18 | Charles Worthington | Comm | 2020-07-20 | Bryan Sturgies | 2020-07-22 | John Watts
TSW-01 | TSW-01 | PI09829 | Verified | Test Package TSW-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-05 | Kelvin Cook
TSW-01 | TSW-01 | PI13856 | Verified | Install 10-TSW-AE-0011, 10-TSW-AIT-0011. | A | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Const | 2019-12-13 | Michael Law | 2019-12-14 | Mike Tabbert
TSW-01 | TSW-01 | PI13857 | Verified | Complete all conduit. | A | E | Chris Colvin | McD | 2019-12-03 | Chris Colvin | Const | 2019-12-09 | Michael Law | 2019-12-10 | Mike Tabbert
TSW-01 | TSW-01 | PI13858 | Verified | Tag 10-TSW-V-0004. | C | P | James Beech | McD | 2019-12-03 | James Beech | Const |  |  | 2020-02-07 | Kelvin Cook
TSW-01 | TSW-01 | PI13859 | Verified | Complete duct bank with concrete encasement. | A | E | Chris Colvin | McD | 2019-12-03 | Chris Colvin | Const | 2019-12-07 | Michael Law | 2019-12-10 | Mike Tabbert
TSW-01 | TSW-01 | PI13860 | Verified | Check area hazardous classification. | A | E | Bart Betz | McD | 2019-12-03 | Bart Betz | Const | 2019-12-06 | Michael Law | 2019-12-18 | Randy Carpenter
TSW-01 | TSW-01 | PI13861 | Verified | Level up conduit at 10-TSW-CAB-0001. | B | E | Chris Colvin | McD | 2019-12-03 | Chris Colvin | Const |  |  | 2019-12-20 | Fred Michael
TSW-01 | TSW-01 | PI13862 | Verified | Install all condulet covers. | B | E | Chris Colvin | McD | 2019-12-03 | Chris Colvin | Const |  |  | 2019-12-20 | Fred Michael
TSW-01 | TSW-01 | PI13863 | Verified | Clean & cold galvanize all conduit threads. | B | E | Chris Colvin | McD | 2019-12-03 | Chris Colvin | Const |  |  | 2019-12-14 | Mike Tabbert
TSW-01 | TSW-01 | PI13864 | Verified | Clean sanitary skid when all work is complete. | C | E | Chris Colvin | McD | 2019-12-03 | Chris Colvin | Const |  |  | 2019-12-14 | Mike Tabbert
TSW-01 | TSW-01 | PI13865 | Verified | Verify sanitary skid roof is complete. | B | S | Sheri Fritz | MOO | 2019-12-03 | Sheri Fritz | Const | 2019-12-14 | Michael Law | 2020-01-20 | Dave Goldak
TSW-01 | TSW-01 | PI13896 | Verified | 10TSWC0005, Pull Cable | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2019-12-13 | Michael Law | 2019-12-14 | Mike Tabbert
TSW-01 | TSW-01 | PI13897 | Verified | 10TSWC0001, From Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
TSW-01 | TSW-01 | PI13898 | Verified | 10TSWC0002, From Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
TSW-01 | TSW-01 | PI13899 | Verified | 10TSWC0003, From Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
TSW-01 | TSW-01 | PI13900 | Verified | 10TSWC0005, From Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-14 | Mike Tabbert
TSW-01 | TSW-01 | PI13901 | Verified | 10TSWK0004, From Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
TSW-01 | TSW-01 | PI13902 | Verified | 10TSWK0005, From Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
TSW-01 | TSW-01 | PI13903 | Verified | 10TSWX0001, From Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-14 | Mike Tabbert
TSW-01 | TSW-01 | PI13904 | Verified | 10TSWC0001, To Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
TSW-01 | TSW-01 | PI13905 | Verified | 10TSWC0002, To Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
TSW-01 | TSW-01 | PI13906 | Verified | 10TSWC0003, To Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
TSW-01 | TSW-01 | PI13907 | Verified | 10TSWC0005, To Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const | 2019-12-14 | Mike Tabbert | 2019-12-14 | Mike Tabbert
TSW-01 | TSW-01 | PI13908 | Verified | 10TSWK0004, To Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
TSW-01 | TSW-01 | PI13909 | Verified | 10TSWK0005, To Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-09 | Mike Tabbert
TSW-01 | TSW-01 | PI13910 | Verified | 10TSWK0010, To Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
TSW-01 | TSW-01 | PI13911 | Verified | 10TSWX0001, To Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-14 | Mike Tabbert
TSW-01 | TSW-01 | PI13912 | Verified | 10TSWX0002, To Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-14 | Mike Tabbert
TSW-01 | TSW-01 | PI13913 | Verified | 10TSWX0003, To Termination | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-07 | Mike Tabbert
TSW-01 | TSW-01 | PI13914 | Verified | Seal off conduits going to lift station tank. | A | E | Chris Colvin | McD | 2019-12-04 | Chris Colvin | Const |  |  | 2019-12-11 | Fred Michael
TSW-01 | TSW-01 | PI14413 | Verified | Add ground studs to pipe flanges 10-TSW-FIT-0010 | A | P | James Beech | McD | 2019-12-06 | James Beech | Const | 2019-12-15 | Michael Law | 2019-12-17 | James Tanner
TSW-01 | TSW-01 | PI16161 | Verified | 1.5" ball valve installed at 1.5-FP-2.0 to 10-TSW-AE-0011 is not shown on the P&ID, drawing needs redline | C | P | Charles Worthington | McD | 2020-01-20 | Charles Worthington | Comm | 2020-04-28 | Charles Worthington | 2020-06-16 | Dave Goldak
TSW-01 | TSW-01 | PI16162 | Verified | 1.5" ball valve installed at 1.5-FP-2.0 to 10-TSW-AE-0011 is not shown on the P&ID, need to assign tag number and install tag | C | P | Charles Worthington | McD | 2020-01-20 | Charles Worthington | Comm | 2020-04-28 | James Beech | 2020-06-16 | Dave Goldak
TSW-01 | TSW-01 | PI16163 | Verified | Seal unused 1.5" stub up on concrete pad at electrical cable supply to 10-TSW-AE-0011 | C | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
TSW-01 | TSW-01 | PI16164 | Verified | Line No. 4-10-TSW-0009 vertical support anchor pad is not installed per design, should be elevated and grouted | C | P | James Beech | McD | 2020-01-20 | James Beech | Comm | 2020-03-12 | James Beech | 2020-03-12 | John Watts
TSW-01 | TSW-01 | PI16165 | Verified | Conduit to 10-TSW-FIT-0010; TSW Analysis Indicating Transmitter missing condolet cover screw | C | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
TSW-01 | TSW-01 | PI16166 | Verified | Patch and paint Line No. 4-10-TSW-0009 | C | X | Jerry Smith | McD | 2020-01-20 | Jerry Smith | Comm | 2020-03-26 | Jerry Smith | 2020-04-07 | Bernard Stasse
TSW-01 | TSW-01 | PI16167 | Verified | 10-TSW-AE-0011; TSW Analysis Sensing Element vertical support needs cap | C | E | Gonzalo Pena | McD | 2020-01-20 | Gonzalo Pena | Comm | 2020-01-29 | Gonzalo Pena | 2020-01-30 | Fred Michael
TSW-01 | TSW-01 | PI16168 | Verified | Fasten Sanitary Lift Station manway cover to vessel flange | B | M | Shane Crowe | McD | 2020-01-20 | Shane Crowe | Comm | 2020-01-24 | Shane Crowe | 2020-02-11 | Dave Goldak
TSW-01 | TSW-01 | PI16169 | Verified | Tag 10-TSW-LE-0001; Sanitary Sewer Level Sensing Element | C | I | Gonzalo Pena | McD | 2020-01-20 | Gonzalo Pena | Comm | 2020-01-29 | Gonzalo Pena | 2020-01-30 | Fred Michael
TSW-01 | TSW-01 | PI16170 | Verified | Tag 10-TSW-CHK-0001A; Sanitary Sewer Lift Pump A discharge check valve | C | P | James Beech | McD | 2020-01-20 | James Beech | Comm | 2020-05-27 | James Beech | 2020-07-28 | Keith Pollock
TSW-01 | TSW-01 | PI16171 | Verified | Tag 10-TSW-CHK-0002A; Sanitary Sewer Lift Pump A discharge check valve | C | P | James Beech | McD | 2020-01-20 | James Beech | Comm | 2020-05-27 | James Beech | 2020-07-28 | Keith Pollock
TSW-01 | TSW-01 | PI16172 | Verified | Tag 10-TSW-CHK-0001B; Sanitary Sewer Lift Pump B discharge check valve | C | P | James Beech | McD | 2020-01-20 | James Beech | Comm | 2020-05-27 | James Beech | 2020-07-28 | Keith Pollock
TSW-01 | TSW-01 | PI16173 | Verified | Tag 10-TSW-CHK-0002B; Sanitary Sewer Lift Pump B discharge check valve | C | P | Kelvin Cook | McD | 2020-01-20 | Kelvin Cook | Comm |  |  | 2020-01-30 | Fred Michael
TSW-01 | TSW-01 | PI16174 | Verified | Sanitary Lift Station vessel 1" vent is not installed at manway cover | D | P | Kelvin Cook | McD | 2020-01-20 | Kelvin Cook | Comm | 2020-03-12 | Kelvin Cook | 2020-03-12 | John Watts
TSW-01 | TSW-01 | PI16175 | Verified | Point and patch unused anchors on control panel concrete foundation | C | C | Alan Huntsman | McD | 2020-01-20 | Alan Huntsman | Comm |  |  | 2020-01-30 | Fred Michael
TSW-01 | TSW-01 | PI16176 | Verified | Cap unused conduit stub at control panel concrete foundation | C | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
TSW-01 | TSW-01 | PI16179 | Verified | 10-TSW-CHK-0003A; Sanitary Packaged Treatment Blower A discharge check valve is not installed per P&ID, marked as removed on isometric, what is reason for removal | D | P | Charles Worthington | McD | 2020-01-20 | Charles Worthington | Comm | 2020-04-28 | Charles Worthington | 2020-06-16 | Dave Goldak
TSW-01 | TSW-01 | PI16180 | Verified | 10-TSW-CHK-0006A; Sanitary Packaged Treatment Blower A discharge check valve is not installed per P&ID, marked as removed on isometric, what is reason for removal | D | P | Charles Worthington | McD | 2020-01-20 | Charles Worthington | Comm | 2020-04-28 | Charles Worthington | 2020-06-16 | Dave Goldak
TSW-01 | TSW-01 | PI16181 | Verified | 10-TSW-CHK-0003B; Sanitary Packaged Treatment Blower B discharge check valve is not installed per P&ID, marked as removed on isometric, what is reason for removal | D | P | Charles Worthington | McD | 2020-01-20 | Charles Worthington | Comm | 2020-04-28 | Charles Worthington | 2020-06-16 | Dave Goldak
TSW-01 | TSW-01 | PI16182 | Verified | 10-TSW-CHK-0006B; Sanitary Packaged Treatment Blower B discharge check valve is not installed per P&ID, marked as removed on isometric, what is reason for removal | D | P | Charles Worthington | McD | 2020-01-20 | Charles Worthington | Comm | 2020-04-28 | Charles Worthington | 2020-06-16 | Dave Goldak
TSW-01 | TSW-01 | PI16183 | Verified | Seal inside GCB conduit fitting at Sanitary Packaged Treatment Blower A power supply | B | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm | 2020-01-29 | Jared Stimpson | 2020-01-30 | Fred Michael
TSW-01 | TSW-01 | PI16184 | Verified | Seal inside GCB conduit fitting at Sanitary Packaged Treatment Blower B power supply | B | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm | 2020-01-29 | Jared Stimpson | 2020-01-30 | Fred Michael
TSW-01 | TSW-01 | PI16185 | Verified | Sanitary Packaged Treatment Blower A needs tag | C | M | James Beech | McD | 2020-01-20 | James Beech | Comm | 2020-05-19 | Tim Green | 2020-07-07 | Nelson Eichelberger
TSW-01 | TSW-01 | PI16186 | Verified | Sanitary Packaged Treatment Blower B needs tag | C | M | James Beech | McD | 2020-01-20 | James Beech | Comm | 2020-05-19 | Tim Green | 2020-07-07 | Nelson Eichelberger
TSW-01 | TSW-01 | PI16187 | Verified | Sanitary Packaged Treatment Blower B sensing lines hose barbs are bent at crimp, possibly impeding signal | C | P | James Beech | McD | 2020-01-20 | James Beech | Comm | 2020-05-19 | Tim Green | 2020-07-07 | Nelson Eichelberger
TSW-01 | TSW-01 | PI16188 | Verified | Seal conduit penetrations inside TSW-CAB-0002 | B | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm | 2020-01-29 | Jared Stimpson | 2020-01-30 | Fred Michael
TSW-01 | TSW-01 | PI16189 | Verified | Paint conduit seal nut red at TSW-CAB-0002 | C | X | Jorge Alexander | McD | 2020-01-20 | Jorge Alexander | Comm |  |  | 2020-01-30 | Fred Michael
TSW-01 | TSW-01 | PI16190 | Verified | Heat shrink wire tags inside TSW-CAB-0002 | C | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-07 | Fred Michael
TSW-01 | TSW-01 | PI16191 | Verified | Need weatherproof panel schedule inside TSW-CAB-0002 | B | E | Mike Tabbert | McD | 2020-01-20 | Mike Tabbert | Comm |  |  | 2020-01-30 | Fred Michael
TSW-01 | TSW-01 | PI16192 | Verified | Seal conduit penetrations inside TSW-CAB-0001 | B | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm | 2020-01-29 | Jared Stimpson | 2020-02-07 | Fred Michael
TSW-01 | TSW-01 | PI16193 | Verified | Heat shrink wire tags inside TSW-CAB-0001 | C | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm | 2020-02-07 | Fred Michael | 2020-02-07 | Fred Michael
TSW-01 | TSW-01 | PI16194 | Verified | Flex conduit at TSW-CAB-0001 missing ground cable jumper | B | E | Chris Colvin | McD | 2020-01-20 | Chris Colvin | Comm |  |  | 2020-01-30 | Fred Michael
WPS-01 | WPS-01 | PI17034 | Verified | Cold galv all weld receptacle unistrut support ends. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-04-28 | Matt Gilmore | 2020-11-11 | Dave Goldak
WPS-01 | WPS-01 | PI17035 | Verified | Heat shrink cable tags in all weld receptacles and all junction boxes. | A | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-03-03 | Randy Carpenter
WPS-01 | WPS-01 | PI17036 | Verified | Ground hubs in all junction boxes. | A | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-03-03 | Randy Carpenter
WPS-01 | WPS-01 | PI17037 | Verified | Ground conduit bushing at cable tray for 1B-WPS-JB-0004. West side of 1B GT. | A | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-11-11 | Dave Goldak
WPS-01 | WPS-01 | PI17038 | Verified | Install bushing & ground on conduit at cable tray for 1B-WPS-WR-0002. West side of 1B HRSG. | A | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-11-11 | Dave Goldak
WPS-01 | WPS-01 | PI17039 | Verified | Clean up all left over material & trash at all weld receptacles & junction boxes. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-03-03 | Randy Carpenter
WPS-01 | WPS-01 | PI17040 | Verified | Cold galv all conduit threads at weld receptacles & junction boxes. | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI17041 | Verified | Install bushing & ground conduit at cable tray for 1A-WPS-JB-0001. East side of 1A HRSG. | A | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-11-11 | Dave Goldak
WPS-01 | WPS-01 | PI17042 | Verified | Need low point drain at conduit for 1A-WPS-WR-0001. East side of 1A HRSG. | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-03-03 | Randy Carpenter
WPS-01 | WPS-01 | PI17043 | Verified | Complete installation of 1A-WPS-WR-0001. East side of 1A HRSG. | A | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-03-03 | Randy Carpenter
WPS-01 | WPS-01 | PI17044 | Verified | Label 1A-WPS-WR-0001. East side of 1A HRSG. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-03-03 | Randy Carpenter
WPS-01 | WPS-01 | PI17045 | Verified | Label 1A-WPS-WR-0007. West side of 1A GT. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-03-03 | Randy Carpenter
WPS-01 | WPS-01 | PI17046 | Verified | Attach label to 1A-WPS-JB-0004 (label is inside JB). | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-03-03 | Randy Carpenter
WPS-01 | WPS-01 | PI17047 | Verified | Condulet cover missing screw at 1A-WPS-WR-0002. West side of 1A HRSG. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI17048 | Verified | 10-WPS-WR-0005 - support has short bolts / missing hardware. Sodium Hypo. Platform. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-04-01 | Chris Colvin | 2020-04-02 | Michael Law
WPS-01 | WPS-01 | PI17049 | Verified | Label 10-WPS-WR-0006. Circ Water pump platform. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-03-03 | Randy Carpenter
WPS-01 | WPS-01 | PI17050 | Verified | Re-locate 1C-WPS-WR-0001 to the west side of the steel column it is attached to. Conduit needs straps to unistrut after moving. STG ground floor north. | A | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI17051 | Verified | Missing condulet cover at 1C-WPS-JB-0001. STG ground floor near air compressors. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI17052 | Verified | Conduit for 10-WPS-WR-0001 needs grounding bushing and ground. West side of main PDC. | A | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-03-10 | Chris Colvin | 2020-11-11 | Dave Goldak
WPS-01 | WPS-01 | PI17053 | Verified | 1C-WPS-WR-0004 - conduit needs support 30" from box. STG mezz west side. | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI17054 | Verified | 1C-WPS-WR-0006 - receptacle housing broken at mounting ears. STG oper deck east side. | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-03-18 | Mike Tabbert | 2020-03-18 | Mike Tabbert
WPS-01 | WPS-01 | PI17055 | Verified | 1C-WPS-WR-0006 - grout supports. STG oper deck east side. | C | C | Alan Huntsman | McD | 2020-02-18 | Alan Huntsman | Const | 2020-03-13 | Johnny Campbell | 2020-03-16 | Mike Tabbert
WPS-01 | WPS-01 | PI17056 | Verified | 1C-WPS-WR-0005 - grout supports. STG oper deck west side. | C | C | Alan Huntsman | McD | 2020-02-18 | Alan Huntsman | Const | 2020-03-13 | Johnny Campbell | 2020-03-16 | Mike Tabbert
WPS-01 | WPS-01 | PI17057 | Verified | 1C-WPS-WR-0005 - conduit needs support 30" from box. STG oper deck west side. | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI17058 | Verified | 1A-WPS-WR-0004 - conduit needs support 30" from box. Top of 1A HRSG. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-04-14 | Chris Colvin | 2020-04-29 | Mike Tabbert
WPS-01 | WPS-01 | PI17059 | Verified | 1A-WPS-WR-0003 - missing condulet cover. Top of 1A HRSG. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI17060 | Verified | 1B-WPS-WR-0004 - missing condulet cover. Top of 1B HRSG. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI17061 | Verified | 1B-WPS-WR-0004 - cable hanging out of LB. Top of 1B HRSG. | A | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI17062 | Verified | 1B-WPS-WR-0004 - relocate label. Top of 1B HRSG. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI17063 | Verified | 1B-WPS-WR-0004 - LB cover missing screws. Top of 1B HRSG. | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI17064 | Verified | 1B-WPS-WR-0003 - missing label. Top of 1B HRSG. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI17065 | Verified | 1B-WPS-WR-0003 - missing drain. Top of 1B HRSG. | B | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI17066 | Verified | 1B-WPS-WR-0001 - missing label. East side of 1B HRSG ground level. | C | E | Chris Colvin | McD | 2020-02-18 | Chris Colvin | Const | 2020-02-20 | Chris Caywood | 2020-02-21 | Mike Tabbert
WPS-01 | WPS-01 | PI18076 | Verified | 1B-WPS-JB-0003 - The equipment tag reads, "18-WPS-JB-0003", and it should read, "1B-WPS-JB-0003". | C | E | Chris Colvin | McD | 2020-03-18 | Chris Colvin | Comm | 2020-04-01 | Chris Colvin | 2020-07-28 | Keith Pollock
WTD-01 | WTD-01 | PI00547 | Verified | Complete wiring to all Equipment. | A | E | Luis Cantu | McD | 2019-04-15 | Luis Cantu | Const | 2019-06-14 | Ed Gober | 2019-06-14 | Ed Gober
WTD-01 | WTD-01 | PI00545 | Verified | Grout all equipment to Pads. | A | C | Johnny Campbell | McD | 2019-04-15 | Johnny Campbell | Const | 2019-08-08 | Johnny Campbell | 2019-12-12 | Michael Law
WTD-01 | WTD-01 | PI02656 | Verified | LK-10-WTD-PD-P40-0030-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02657 | Verified | LK-10-WTD-PD-P40-0038-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02658 | Verified | LK-10-WTD-PD-P40-0042-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02659 | Verified | LK-10-WTD-PD-P40-0060-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02660 | Verified | LK-10-WTD-PD-P40-0070-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02661 | Verified | LK-10-WTD-PD-P40-0090-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02662 | Verified | LK-10-WTD-PD-P40-0090-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02663 | Verified | LK-10-WTD-PD-P40-0090-04 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02664 | Verified | LK-10-WTD-PD-P40-0120-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02665 | Verified | LK-10-WTD-PD-P40-0130-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02666 | Verified | LK-10-WTD-PD-P40-0270-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02667 | Verified | LK-10-WTD-PD-P41-0010-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02668 | Verified | LK-10-WTD-PD-P41-0012-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-13 | Terry Deaton | 2019-08-13 | Tom Noble
WTD-01 | WTD-01 | PI02669 | Verified | LK-10-WTD-PD-P41-0013-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02670 | Verified | LK-10-WTD-PD-P41-0014-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02671 | Verified | LK-10-WTD-PD-P41-0020-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02672 | Verified | LK-10-WTD-PD-P41-0022-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02673 | Verified | LK-10-WTD-PD-P41-0026-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02674 | Verified | LK-10-WTD-PD-P41-0026-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02675 | Verified | LK-10-WTD-PD-P41-0030-01 - Need Welds Cleared | A | P | James Beech | McD | 2019-07-23 | James Beech | Const |  |  | 2019-10-24 | Tom Noble
WTD-01 | WTD-01 | PI02676 | Verified | LK-10-WTD-PD-P41-0032-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02677 | Verified | LK-10-WTD-PD-P41-0042-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02678 | Verified | LK-10-WTD-PD-P41-0044-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02679 | Verified | LK-10-WTD-PD-P41-0060-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02680 | Verified | LK-10-WTD-PD-P41-0090-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02681 | Verified | LK-10-WTD-PD-P41-0090-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02682 | Verified | LK-10-WTD-PD-P41-0090-03 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02683 | Verified | LK-10-WTD-PD-P41-0090-04 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02684 | Verified | LK-10-WTD-PD-P41-0160-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02685 | Verified | LK-10-WTD-PD-P41-0240-01 - Need Welds Cleared | A | P | James Beech | McD | 2019-07-23 | James Beech | Const |  |  | 2019-10-24 | Tom Noble
WTD-01 | WTD-01 | PI02686 | Verified | LK-10-WTD-PD-P41-0270-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02687 | Verified | LK-10-WTD-PD-P41-0272-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02688 | Verified | LK-10-WTD-PD-P41-0276-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02689 | Verified | LK-10-WTD-PD-P41-0282-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02690 | Verified | LK-10-WTD-PD-P41-0286-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02691 | Verified | LK-10-WTD-PD-P41-0310-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02692 | Verified | LK-10-WTD-PD-P41-0310-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02693 | Verified | LK-10-WTD-PD-P41-0310-03 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02694 | Verified | LK-10-WTD-PD-P41-0310-04 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02695 | Verified | LK-10-WTD-PD-P41-0500-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02696 | Verified | LK-10-WTD-PD-P41-0500-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02697 | Verified | LK-10-WTD-PD-P42-0214-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
WTD-01 | WTD-01 | PI02698 | Verified | LK-10-WTD-PD-P42-0214-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-13 | Tom Noble
WTD-01 | WTD-01 | PI02699 | Verified | LK-10-WTD-PD-P42-0430-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-23 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-13 | Tom Noble
WTD-01 | WTD-01 | PI02795 | Verified | 10DCSX0104, Pull Cable | A | E | Dustin Futrell | McD | 2019-07-25 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-11 | Mike Tabbert
WTD-01 | WTD-01 | PI02799 | Verified | 10DCSX0104, Terminate Cable | A | E | Sheri Fritz | ITS | 2019-07-25 | Sheri Fritz | Const | 2019-09-11 | Mike Tabbert | 2019-09-11 | Mike Tabbert
WTD-01 | WTD-01 | PI03418 | Verified | 10WTDC0008, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03419 | Verified | 10WTDK0001, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03420 | Verified | 10WTDK0025, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03421 | Verified | 10WTDK0029, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03422 | Verified | 10WTDK0037, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03423 | Verified | 10WTDK0040, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03424 | Verified | 10WTDK0049, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03425 | Verified | 10WTDK0050, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03426 | Verified | 10WTDK0051, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03427 | Verified | 10WTDK0053, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03428 | Verified | 10WTDK0063, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03429 | Verified | 10WTDK0064, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03430 | Verified | 10WTDX0028, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03431 | Verified | 10WTDX0031, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03432 | Verified | 10WTDX0032, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03433 | Verified | 10WTDX0033, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03434 | Verified | 10WTDX0080, Pull Cable | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03435 | Verified | 10DCSX0104, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-05 | Mike Tabbert | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03436 | Verified | 10NJSL0005A, To Termination | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-18 | Mike Tabbert
WTD-01 | WTD-01 | PI03437 | Verified | 10NJSL0005B, To Termination | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-18 | Mike Tabbert
WTD-01 | WTD-01 | PI03438 | Verified | 10NJSL0005C, To Termination | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-18 | Mike Tabbert
WTD-01 | WTD-01 | PI03439 | Verified | 10NJSL0005G, To Termination | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-18 | Mike Tabbert
WTD-01 | WTD-01 | PI03440 | Verified | 10SWSX0003, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03441 | Verified | 10SWSX0004, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03442 | Verified | 10WTDC0008, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
WTD-01 | WTD-01 | PI03443 | Verified | 10WTDK0001, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03444 | Verified | 10WTDK0011, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03445 | Verified | 10WTDK0018, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-18 | Mike Tabbert
WTD-01 | WTD-01 | PI03446 | Verified | 10WTDK0025, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03447 | Verified | 10WTDK0028, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03448 | Verified | 10WTDK0029, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03449 | Verified | 10WTDK0037, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03450 | Verified | 10WTDK0040, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
WTD-01 | WTD-01 | PI03451 | Verified | 10WTDK0043, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
WTD-01 | WTD-01 | PI03452 | Verified | 10WTDK0045, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03453 | Verified | 10WTDK0046, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03454 | Verified | 10WTDK0049, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
WTD-01 | WTD-01 | PI03455 | Verified | 10WTDK0050, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
WTD-01 | WTD-01 | PI03456 | Verified | 10WTDK0051, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
WTD-01 | WTD-01 | PI03457 | Verified | 10WTDK0053, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03460 | Verified | 10WTDK0062, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03461 | Verified | 10WTDK0063, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
WTD-01 | WTD-01 | PI03462 | Verified | 10WTDK0064, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
WTD-01 | WTD-01 | PI03463 | Verified | 10WTDL0001A, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03464 | Verified | 10WTDL0001B, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03465 | Verified | 10WTDL0001C, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03466 | Verified | 10WTDL0001G, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03467 | Verified | 10WTDL0005A, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03468 | Verified | 10WTDL0005B, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03469 | Verified | 10WTDL0005C, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03470 | Verified | 10WTDL0005G, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03472 | Verified | 10WTDX0003, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-09-24 | Mike Tabbert
WTD-01 | WTD-01 | PI03473 | Verified | 10WTDX0004, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-24 | Mike Tabbert
WTD-01 | WTD-01 | PI03474 | Verified | 10WTDX0005, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-09-24 | Mike Tabbert
WTD-01 | WTD-01 | PI03475 | Verified | 10WTDX0028, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03476 | Verified | 10WTDX0031, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03477 | Verified | 10WTDX0032, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
WTD-01 | WTD-01 | PI03478 | Verified | 10WTDX0033, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
WTD-01 | WTD-01 | PI03479 | Verified | 10WTDX0037, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-09-24 | Mike Tabbert
WTD-01 | WTD-01 | PI03480 | Verified | 10WTDX0038, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-09-24 | Mike Tabbert
WTD-01 | WTD-01 | PI03481 | Verified | 10WTDX0041, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03482 | Verified | 10WTDX0042, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03483 | Verified | 10WTDX0046, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03484 | Verified | 10WTDX0047, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
WTD-01 | WTD-01 | PI03485 | Verified | 10WTDX0048, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
WTD-01 | WTD-01 | PI03486 | Verified | 10WTDX0049, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
WTD-01 | WTD-01 | PI03487 | Verified | 10WTDX0053, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
WTD-01 | WTD-01 | PI03488 | Verified | 10WTDX0054, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
WTD-01 | WTD-01 | PI03489 | Verified | 10WTDX0055, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
WTD-01 | WTD-01 | PI03490 | Verified | 10WTDX0065, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03492 | Verified | 10WTDX0074, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-09-24 | Michael Law
WTD-01 | WTD-01 | PI03493 | Verified | 10WTDX0076, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03494 | Verified | 10WTDX0079, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-24 | Michael Law | 2019-10-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03495 | Verified | 10WTDX0080, To Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-11 | Mike Tabbert
WTD-01 | WTD-01 | PI03496 | Verified | 10DCSX0104, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-11 | Dustin Futrell | 2019-09-11 | Mike Tabbert
WTD-01 | WTD-01 | PI03497 | Verified | 10SWSX0003, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
WTD-01 | WTD-01 | PI03498 | Verified | 10WTDC0003, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-18 | Mike Tabbert
WTD-01 | WTD-01 | PI03499 | Verified | 10WTDC0008, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
WTD-01 | WTD-01 | PI03500 | Verified | 10WTDK0001, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03501 | Verified | 10WTDK0025, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03502 | Verified | 10WTDK0029, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03503 | Verified | 10WTDK0032, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03504 | Verified | 10WTDK0040, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
WTD-01 | WTD-01 | PI03505 | Verified | 10WTDK0041, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-20 | Dustin Futrell | 2019-08-21 | Mike Tabbert
WTD-01 | WTD-01 | PI03506 | Verified | 10WTDK0045, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const |  |  | 2019-11-16 | Mike Tabbert
WTD-01 | WTD-01 | PI03507 | Verified | 10WTDK0053, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03508 | Verified | 10WTDK0054, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-23 | Mike Tabbert | 2019-08-23 | Mike Tabbert
WTD-01 | WTD-01 | PI03509 | Verified | 10WTDK0055, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-23 | Mike Tabbert | 2019-08-23 | Mike Tabbert
WTD-01 | WTD-01 | PI03510 | Verified | 10WTDK0063, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03511 | Verified | 10WTDK0064, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03512 | Verified | 10WTDL0001A, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03513 | Verified | 10WTDL0001B, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03514 | Verified | 10WTDL0001C, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03515 | Verified | 10WTDL0001G, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03516 | Verified | 10WTDL0005A, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-20 | Dustin Futrell | 2019-09-20 | Mike Tabbert
WTD-01 | WTD-01 | PI03517 | Verified | 10WTDL0005B, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-20 | Dustin Futrell | 2019-09-20 | Mike Tabbert
WTD-01 | WTD-01 | PI03518 | Verified | 10WTDL0005C, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-20 | Dustin Futrell | 2019-09-20 | Mike Tabbert
WTD-01 | WTD-01 | PI03519 | Verified | 10WTDL0005G, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-20 | Dustin Futrell | 2019-09-20 | Mike Tabbert
WTD-01 | WTD-01 | PI03520 | Verified | 10WTDX0001, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
WTD-01 | WTD-01 | PI03521 | Verified | 10WTDX0021, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03522 | Verified | 10WTDX0025, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-05 | Mike Tabbert
WTD-01 | WTD-01 | PI03523 | Verified | 10WTDX0028, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03524 | Verified | 10WTDX0031, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Mike Tabbert
WTD-01 | WTD-01 | PI03525 | Verified | 10WTDX0032, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03526 | Verified | 10WTDX0033, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03527 | Verified | 10WTDX0072, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-23 | Mike Tabbert
WTD-01 | WTD-01 | PI03528 | Verified | 10WTDX0080, From Termination | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-13 | Dustin Futrell | 2019-08-13 | Mike Tabbert
WTD-01 | WTD-01 | PI03567 | Verified | On ISO 10-WTD-PD-P40-0012-01 on pipe support 10-WTD-PD-HRG-0245 eyebolt needs to full threaded engagement. | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03568 | Verified | On ISO 10-WTD-PD-P40-0013-01 pipe support 10-WTD-PD-HGR-0247 has loose nut at eye bolt & needs full threaded engagement at eye bolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03569 | Verified | On ISO 10-WTD-PD-P40-0013-01 pipe support 10-WTD-PD-HGR-0236 needs to have full threaded engagement on turnbuckle and eye bolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03570 | Verified | On ISO 10-WTD-PD-P40-0020-01 pipe support 10-WTD-PD-HGR-0013 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03571 | Verified | On ISO 10-WTD-PD-P40-0020-02 pipe support 10-WTD-PD-HGR-0200 snug ubolt down for anchor | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03572 | Verified | On ISO 10-WTD-PD-P40-0020-02 pipe support 10-WTD-PD-HGR-0202 has loose nuts | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03573 | Verified | On ISO 10-WTD-PD-P40-0020-03 pipe support 10-WTD-PD-HGR-0206 has no ubolt | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-15 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03574 | Verified | On ISO 10-WTD-PD-P40-0020-03 pipe support 10-WTD-PD-HGR-0205 has loose ubolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03575 | Verified | On ISO 10-WTD-PD-P40-0020-04 pipe support 10-WTD-PD-HGR-0207 has loose ubolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03576 | Verified | On ISO 10-WTD-PD-P40-0020-04 pipe supports need to be cold galved | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03577 | Verified | On ISO 10-WTD-PD-P40-0020-05 pipe support 10-WTD-PD-HGR-0272 needs to be cold galved | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03578 | Verified | On ISO 10-WTD-PD-P40-0020-05 pipe support 10-WTD-PD-HGR-0272 needs to be grouted | B | C | Johnny Campbell | McD | 2019-08-09 | Johnny Campbell | Const | 2019-08-20 | Johnny Campbell | 2019-09-18 | Kelvin Cook
WTD-01 | WTD-01 | PI03579 | Verified | On ISO 10-WTD-PD-P40-0022-01 connection to 10-WTD-SKD-0500/G has loose bolt & bolts missing | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03580 | Verified | On ISO 10-WTD-PD-P40-0022-01 flanges connection to 10-WTD-V-0022 has loose bolts | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03581 | Verified | On ISO 10-WTD-PD-P40-0022-01 pipe support 10-WTD-PD-HGR-0252 has missing clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03582 | Verified | On ISO 10-WTD-PD-P40-0022-01 pipe support 10-WTD-PD-HGR-0251 missing ss wrap and clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03583 | Verified | On ISO 10-WTD-PD-P40-0030-01 pipe support 10-WTD-PD-HGR-0228 has loose ubolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03584 | Verified | On ISO 10-WTD-PD-P40-0030-01 pipe support 10-WTD-PD-HGR-0229 missing clamps | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03585 | Verified | On ISO 10-WTD-PD-P40-0030-01 pipe support 10-WTD-PD-HGR-0229 needs to be have full threaded engagement plus 2 threaded at turnbuckle and eyebolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03586 | Verified | On ISO 10-WTD-PD-P40-0038-01 connection to 10-WTD-T-0610/N7 has missing bolts | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03587 | Verified | On ISO 10-WTD-PD-P40-0040-01 connection to 10-WTD-SKD-0100/A needs to even up bolts | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03588 | Verified | On ISO 10-WTD-PD-P40-0060-01 pipe support 10-WTD-PD-HGR-0233 need full threaded engagement of 2 thread. Required at turnbuckle and eye bolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03589 | Verified | On ISO 10-WTD-PD-P40-0070-01 pipe support 10-WTD-PD-HGR-0257 plumb all threaded rods | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03590 | Verified | On ISO 10-WTD-PD-P40-0070-01 pipe support 10-WTD-PD-HGR-0257 missing hose clamps & needs to have full threaded engagement at turnbuckle and eye bolts | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03591 | Verified | On ISO 10-WTD-PD-P40-0070-01 pipe support 10-WTD-PD-HGR-0258 ss wrap needs to cover the entire top of support | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03592 | Verified | On ISO 10-WTD-PD-P40-0070-01 pipe support 10-WTD-PD-HGR-0258 missing hose clamp. | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03593 | Verified | On ISO 10-WTD-PD-P40-0070-01 pipe support 10-WTD-PD-HGR-0258 ubolts nuts need to be at top and bottom | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03594 | Verified | On ISO 10-WTD-PD-P40-0070-01 vendor supplied valve 10-WTD-V-0075 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03595 | Verified | On ISO 10-WTD-PD-P40-0090-01 pipe support 10-WTD-PD-HGR-0209 missing hose clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03596 | Verified | On ISO 10-WTD-PD-P40-0090-02 pipe support 10-WTD-PD-HGR-0210 missing hose clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03597 | Verified | On ISO 10-WTD-PD-P40-0090-02 pipe support 10-WTD-PD-HGR-0211 missing hose clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03598 | Verified | On ISO 10-WTD-PD-P40-0090-02 pipe support 10-WTD-PD-HGR-0212 missing hose clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03599 | Verified | On ISO 10-WTD-PD-P40-0090-02 pipe support 10-WTD-PD-HGR-0213 missing hose clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03600 | Verified | On ISO 10-WTD-PD-P40-0090-03 pipe support 10-WTD-PD-HGR-0214 missing hose clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03601 | Verified | On ISO 10-WTD-PD-P40-0090-03 pipe support 10-WTD-PD-HGR-0215 missing hose clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03602 | Verified | On ISO 10-WTD-PD-P40-0090-04 pipe support 10-WTD-PD-HGR-0216 has loose 3 bolt clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03603 | Verified | On ISO 10-WTD-PD-P40-0090-04 pipe support 10-WTD-PD-HGR-0216 missing hose clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03604 | Verified | On ISO 10-WTD-PD-P40-0090-04 pipe support 10-WTD-PD-HGR-0216 needs full threaded engagement at turnbuckle and eye bolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03605 | Verified | On ISO 10-WTD-PD-P40-0090-04 pipe support 10-WTD-PD-HGR-0239 missing hose clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03606 | Verified | On ISO 10-WTD-PD-P40-0130-01 pipe support 10-WTD-PD-HGR-0239 and is out plumb | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03607 | Verified | On ISO 10-WTD-PD-P40-0160-01 pipe support 10-WTD-PD-HGR-0250 missing hose clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03608 | Verified | On ISO 10-WTD-PD-P40-0160-01 pipe support 10-WTD-PD-HGR-0249 missing ss wrap & missing hose clamp and has loose ubolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03609 | Verified | On ISO 10-WTD-PD-P40-0160-01 instrument 10-WTD-FSL-0503 is not installed | A | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-11-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03610 | Verified | On ISO 10-WTD-PD-P40-0213-01 valve 10-WTD-V-0215 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03611 | Verified | On ISO 10-WTD-PD-P40-0220-01 valve 10-WTD-V-0220 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03612 | Verified | On ISO 10-WTD-PD-P40-0220-01 specialty item 10-WTD-QC-0220 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-20 | Kelvin Cook
WTD-01 | WTD-01 | PI03613 | Verified | On ISO 10-WTD-PD-P40-0240-01 pipe support 10-WTD-PD-HGR-0248 needs full thread engagement required at turnbuclke and eye bolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-20 | Damon Turner | 2019-08-27 | Kelvin Cook
WTD-01 | WTD-01 | PI03614 | Verified | On ISO 10-WTD-PD-P40-0240-01 connection to 10-WTD-SKD-0600/H is not is not made | A | P | James Beech | McD | 2019-08-09 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-11-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03615 | Verified | On ISO 10-WTD-PD-P40-0280-01 missing gasket at connection to 10-WTD-SKD-0500/Q | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03616 | Verified | On ISO 10-WTD-PD-P41-0026-01 pipe support 10-WTD-PD-HGR-0254 missing hose clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03617 | Verified | On ISO 10-WTD-PD-P41-0026-01 pipe support 10-WTD-PD-HGR-0255 missing ss wrap & clamps & ubolts | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03618 | Verified | On ISO 10-WTD-PD-P41-0026-01 pipe support 10-WTD-PD-HGR-0256 missing ss wrap & clamp | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03619 | Verified | On ISO 10-WTD-PD-P41-0026-01 pipe support 10-WTD-PD-HGR-0253 missing hose clamps | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03620 | Verified | On ISO 10-WTD-PD-P41-0026-01 connectioin to 10-WTD-T-0610/N9 has loose bolts | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-27 | Kelvin Cook
WTD-01 | WTD-01 | PI03621 | Verified | On ISO 10-WTD-PD-P41-0034-01 is not installed | A | P | James Beech | McD | 2019-08-09 | James Beech | Const | 2019-11-07 | James Beech | 2019-11-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03622 | Verified | On ISO 10-WTD-PD-P41-0044-01 pipe support 10-WTD-PD-HGR-0103 has loose ubolt | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03623 | Verified | On ISO 10-WTD-PD-P41-0044-01 loose union at nipple | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03624 | Verified | On ISO 10-WTD-PD-P41-0090-01 instrument 10-WTD-SV-0082 is not installed | A | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-11-11 | Gonzalo Pena | 2019-11-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03625 | Verified | On ISO 10-WTD-PD-P41-0090-02 instrument 10-WTD-SV-0081 is not installed | A | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-11-11 | Gonzalo Pena | 2019-11-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03626 | Verified | On ISO 10-WTD-PD-P41-0090-03 instrument 10-WTD-SV-0080 is not installed | A | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-11-11 | Gonzalo Pena | 2019-11-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03627 | Verified | On ISO 10-WTD-PD-P41-0090-05 on added support mssing ss wrap & hose clamp and ubolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03628 | Verified | On ISO 10-WTD-PD-P41-0100-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03629 | Verified | On ISO 10-WTD-PD-P41-0100-02 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03630 | Verified | On ISO 10-WTD-PD-P41-0110-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03631 | Verified | On ISO 10-WTD-PD-P41-0110-02 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03632 | Verified | On ISO 10-WTD-PD-P41-0171-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03633 | Verified | On ISO 10-WTD-PD-P41-0170-02 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03634 | Verified | On ISO 10-WTD-PD-P41-0180-01 valve 10-WTD-V-0180 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03635 | Verified | On ISO 10-WTD-PD-P41-0190-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03636 | Verified | On ISO 10-WTD-PD-P41-0190-02 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03637 | Verified | On ISO 10-WTD-PD-P41-0200-02 pipe supports 10-WTD-HGR-0158 needs double nuts at bottom of ubolt anchor | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03638 | Verified | On ISO 10-WTD-PD-P41-0200-02 pipe supports 10-WTD-HGR-0263 needs double nuts at bottom of ubolt anchor | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03639 | Verified | On ISO 10-WTD-PD-P41-0200-02 pipe supports 10-WTD-HGR-0262 needs double nuts at bottom of ubolt anchor | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03640 | Verified | On ISO 10-WTD-PD-P41-0200-02 pipe supports 10-WTD-HGR-0261 needs double nuts at bottom of ubolt anchor | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03641 | Verified | On ISO 10-WTD-PD-P41-0205-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03642 | Verified | On ISO 10-WTD-PD-P41-0205-02 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03643 | Verified | On ISO 10-WTD-PD-P41-0210-01 valve 10-WTD-V-0210-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03644 | Verified | On ISO 10-WTD-PD-P41-0210-01 valve 10-WTD-PCV-0112 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03645 | Verified | On ISO 10-WTD-PD-P41-0276-01 pipe support 10-WTD-HGR-0105 missing ubolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03646 | Verified | On ISO 10-WTD-PD-P41-0278-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03647 | Verified | On ISO 10-WTD-PD-P41-0282-01 pipe support 10-WTD-PD-HGR-0107 & 0108 missing ubolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03648 | Verified | On ISO 10-WTD-PD-P41-0288-01 pipe support 10-WTD-PD-HGR-0113 fix ss wrap & double nut ubolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03649 | Verified | On ISO 10-WTD-PD-P41-0300-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03650 | Verified | On ISO 10-WTD-PD-P41-0300-02 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-20 | Kelvin Cook
WTD-01 | WTD-01 | PI03651 | Verified | On ISO 10-WTD-PD-P41-0310-01 pipe support 10-WTD-PD-HGR-0218 missing clamps | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03652 | Verified | On ISO 10-WTD-PD-P41-0310-01 pipe support 10-WTD-PD-HGR-0217 missing ubolt | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03653 | Verified | On ISO 10-WTD-PD-P41-0310-02 pipe support 10-WTD-PD-HGR-0219 missing clamps | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03654 | Verified | On ISO 10-WTD-PD-P41-0310-02 pipe support 10-WTD-PD-HGR-0220 missing clamps | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03655 | Verified | On ISO 10-WTD-PD-P41-0310-02 pipe support 10-WTD-PD-HGR-0221 missing clamps | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03656 | Verified | On ISO 10-WTD-PD-P41-0310-02 pipe support 10-WTD-PD-HGR-0222 missing clamps | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03657 | Verified | On ISO 10-WTD-PD-P41-0310-02 pipe support 10-WTD-PD-HGR-0223 missing clamps | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03658 | Verified | On ISO 10-WTD-PD-P41-0310-02 pipe support 10-WTD-PD-HGR-0224 missing clamps | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03659 | Verified | On ISO 10-WTD-PD-P41-0310-03 pipe support 10-WTD-PD-HGR-0225 missing clamps | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03660 | Verified | On ISO 10-WTD-PD-P41-0310-03 connection 10-WTD-T-0610/N10 has loose bolts | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-20 | Damon Turner | 2019-08-27 | Kelvin Cook
WTD-01 | WTD-01 | PI03661 | Verified | On ISO 10-WTD-PD-P41-0315-01 connection to 10-WTD-SKD-0600/G is out plumb | B | P | James Beech | McD | 2019-08-09 | James Beech | Const | 2019-09-05 | Damon Turner | 2019-11-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03662 | Verified | On ISO 10-WTD-PD-P41-0610-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03663 | Verified | On ISO 10-WTD-PD-P41-0620-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03664 | Verified | On ISO 10-WTD-PD-P41-0640-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03665 | Verified | On ISO 10-WTD-PD-P41-0650-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03666 | Verified | On ISO 10-WTD-PD-P41-0670-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03667 | Verified | On ISO 10-WTD-PD-P41-0680-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03668 | Verified | On ISO 10-WTD-PD-P41-0700-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03669 | Verified | On ISO 10-WTD-PD-P41-0710-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03670 | Verified | On ISO 10-WTD-PD-P41-0730-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03671 | Verified | On ISO 10-WTD-PD-P41-0740-01 is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03672 | Verified | Suez fix doc. # 503818-AP-01 Rev. C needs to update Dwg showing comments location is incorrect | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Kelvin Cook | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03673 | Verified | 10-WTD-SRV-0028 needs to be reset a relief after 75 psi after redlines are completed. | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Kelvin Cook | 2019-08-16 | Kelvin Cook
WTD-01 | WTD-01 | PI03674 | Verified | Pipe support WTD-P40-0020-01 HGR-13 not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03675 | Verified | Install all AOV's Indicators per engineering change order | B | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-11-18 | James Tanner | 2019-11-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03676 | Verified | Clean drain containment. | B | P | James Beech | McD | 2019-08-09 | James Beech | Const | 2019-08-19 | Damon Turner | 2019-11-07 | Shannon Scott
WTD-01 | WTD-01 | PI03677 | Verified | Sodium Bisulfite feed missing PCV-0112 | A | P | James Beech | McD | 2019-08-09 | James Beech | Const | 2019-08-16 | Damon Turner | 2020-01-22 | Michael Law
WTD-01 | WTD-01 | PI03678 | Verified | No access ladder on Permeate/Backwash Tank | A | M | Jorge Alexander | McD | 2019-08-09 | Jorge Alexander | Const | 2019-08-28 | Joshua Sturgeon | 2020-01-22 | Michael Law
WTD-01 | WTD-01 | PI03679 | Verified | 10-WTD-TT-0126 not installed, spool connection for instrument is damaged, replace spool | A | P | James Beech | McD | 2019-08-09 | James Beech | Const | 2019-11-07 | James Beech | 2019-11-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03680 | Verified | Verify oil and grease on Permeate Pumps | A | P | Shane Crowe | McD | 2019-08-09 | Shane Crowe | Const | 2019-09-13 | Joshua Sturgeon | 2020-01-22 | Michael Law
WTD-01 | WTD-01 | PI03681 | Verified | Loose bolt on Permeate pump 120 suction side | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03682 | Verified | Install all tank trim CIP Tank | A | P | Kelvin Cook | McD | 2019-08-09 | Kelvin Cook | Const |  |  | 2019-11-18 | Kelvin Cook
WTD-01 | WTD-01 | PI03683 | Verified | All high point vents require threaded plugs | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-10-09 | Damon Turner | 2019-10-09 | Kelvin Cook
WTD-01 | WTD-01 | PI03684 | Verified | Install all tank trim UF Permeate Tank | A | P | James Beech | McD | 2019-08-09 | James Beech | Const | 2019-08-19 | Damon Turner | 2019-11-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03685 | Verified | 10-WTD-0036 missing bolts at CIP connection | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-22 | Damon Turner | 2019-08-27 | Kelvin Cook
WTD-01 | WTD-01 | PI03686 | Verified | RO CIP Chemical addition line is not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03687 | Verified | AE-618 drain is not installed | A | P | James Beech | McD | 2019-08-09 | James Beech | Const | 2019-08-22 | Damon Turner | 2019-11-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03688 | Verified | 10-WTD-0016 loose bolt | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const |  |  | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03689 | Verified | 10-WTD-0018 install bolt | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03690 | Verified | All instrument connections on RO skid that contain CP/VC nipples need to be replace with SS nipples | A | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-13 | Michael Law
WTD-01 | WTD-01 | PI03691 | Verified | All instrument connections on CIP skid that contain CP/VC nipples need to be replace with SS nipples | A | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-13 | Michael Law
WTD-01 | WTD-01 | PI03692 | Verified | All instrument connections on UF Filter skid that contain CP/VC nipples need to be replace with SS nipples | A | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-13 | Michael Law
WTD-01 | WTD-01 | PI03693 | Verified | All instrument connections on UF Permeate skid that contain CP/VC nipples need to be replace with SS nipples | A | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-08-13 | Gonzalo Pena | 2019-08-13 | Michael Law
WTD-01 | WTD-01 | PI03694 | Verified | 10-WTD-P41-0213-01 loose U-bolt, SS wrap and hose clamp required | B | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Kelvin Cook
WTD-01 | WTD-01 | PI03695 | Verified | 10-WTD-P41-0213-01 high point vent valve not installed | A | P | Damon Turner | McD | 2019-08-09 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-19 | Albert Burge
WTD-01 | WTD-01 | PI03696 | Verified | 10-WTD-P40-0160-01 relocate WTD-FSL-0053 from skid 500 and install per ISO, plug olet skid 500 | A | I | Gonzalo Pena | McD | 2019-08-09 | Gonzalo Pena | Const | 2019-08-29 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
WTD-01 | WTD-01 | PI03697 | Verified | Vertical tray, SE corner, hvy duty Tray clips, cut tie wraps, File smooth field cut, lower right corner on tray, | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
WTD-01 | WTD-01 | PI03698 | Verified | overhead tray, SE corner, Support under tray reducers, cut/dispose tie wraps, cold galv field cut supports, anchor bolts, and all thread | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
WTD-01 | WTD-01 | PI03699 | Verified | Install kick box barrier around bottom of vert tray from stub-ups, bonding jumpers, ground stub-ups from duc-bank | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-09-06 | Dustin Futrell | 2019-09-11 | Fred Michael
WTD-01 | WTD-01 | PI03700 | Verified | RO Filter Skid, Mtr's 0510/0520, Modify conduit, flex, grounding on flex, to motors | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
WTD-01 | WTD-01 | PI03701 | Verified | Ground NW corner of RO Filter Skid, remove fire blanket SE corner of skid. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
WTD-01 | WTD-01 | PI03702 | Verified | Add additional phenolic tag to 10-WTD-CP-0011 w/more info,conduit covers under Pnl, clean and close panel | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03703 | Verified | Ground bushings/hubs inside JB's 10-WTD-PSW-0510/0520, loose seal-tite, Covers on condulets to boxes | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Fred Michael
WTD-01 | WTD-01 | PI03704 | Verified | Hi-pressure pumps 0510-0520 need grounded | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-28 | Mike Tabbert
WTD-01 | WTD-01 | PI03705 | Verified | Cable tray above Hi-pressure pumps need supports, straighten form-up and tie down rat nest cables, clean tray free of trash and debris | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Fred Michael
WTD-01 | WTD-01 | PI03706 | Verified | Aerator blower skid, Aerator 10-WTD-R-900, needs grounded, NW corner | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-28 | Mike Tabbert
WTD-01 | WTD-01 | PI03707 | Verified | Aerator blower skid, Aerator needs grounded, NW corner | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Fred Michael | 2019-08-19 | Fred Michael
WTD-01 | WTD-01 | PI03708 | Verified | Aerator blower skid, Reactor needs flex tightened, grounded and tie wrapped | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
WTD-01 | WTD-01 | PI03709 | Verified | Aerator Blower needs exterior accessability panel to internal motor term box | A | E | Mike Tabbert | McD | 2019-08-09 | Mike Tabbert | Const | 2019-08-15 | Mike Tabbert | 2019-08-15 | Mike Tabbert
WTD-01 | WTD-01 | PI03710 | Verified | Aerator Blower needs phenolic tag on outer casing and CP that are visible. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Fred Michael
WTD-01 | WTD-01 | PI03711 | Verified | Aerator Blower CP needs fuses installed | B | E | Chris Boudreaux | McD | 2019-08-09 | Chris Boudreaux | Const | 2019-12-07 | Michael Law | 2019-12-07 | Michael Law
WTD-01 | WTD-01 | PI03712 | Verified | Aerator Blower Skid, Vertical conduits need floater or support | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Fred Michael
WTD-01 | WTD-01 | PI03713 | Verified | UF R/O CIP Pump Skid, 10-WTD-P-0600, Reactor and motor need grounded | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-28 | Mike Tabbert
WTD-01 | WTD-01 | PI03714 | Verified | UF R/O CIP Pump Skid, 10-WTD-CP-0012, Interior bushing/hubs need grounding in panel, ground panel. | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Fred Michael
WTD-01 | WTD-01 | PI03715 | Verified | UF R/O CIP Pump Skid, Add phenolic tag to panel w/ more info, close and clean panel. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03716 | Verified | UF R/O CIP Pump Skid, No support on vertical cinduit w/90 degree bend from tray to panel, condulet covers missing, | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
WTD-01 | WTD-01 | PI03717 | Verified | Self Cleaning Filter Skid, Install condulet covers on skid and overhead | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03718 | Verified | Self Cleaning Filter Skid, Loose flex, flex not grounded, | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03719 | Verified | Self Cleaning Filter Skid, Need phenolic tag on 10-WTD-PNL-0001 and clean and close. | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03720 | Verified | Self Cleaning Filter Skid, Need cable tag (1C-10-WTD-C000K48) in PNL, Curent tag unreadable, clean and close. | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03721 | Verified | Self Cleaning Filter Skid, Skid ground needs repaired NW corner | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Fred Michael
WTD-01 | WTD-01 | PI03722 | Verified | Self Cleaning Filter Skid, Cables in overhead cable tray need formed up, tie wrapped. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Fred Michael
WTD-01 | WTD-01 | PI03723 | Verified | Self Cleaning Filter Skid, All-thread on overhead tray supports need cut-off and dividers need top connectors in tray. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Fred Michael
WTD-01 | WTD-01 | PI03724 | Verified | Self Cleaning Filter Skid, 10-WTD-K0006-1 cable not termed in 10-WTD-PNL-0001 | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03725 | Verified | Permeate Backwash Skid, Motors, Storage tank, and Reactor R0120 need grounded | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
WTD-01 | WTD-01 | PI03726 | Verified | Permeate Backwash Skid, Cables in overhead tray need reworked, rat nested, dividers need adjusted and connections on top | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Fred Michael
WTD-01 | WTD-01 | PI03727 | Verified | Permeate Backwash Skid, wrong lug on ground in MTBox, bolt on ground loose | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-29 | Dustin Futrell | 2019-09-18 | Mike Tabbert
WTD-01 | WTD-01 | PI03728 | Verified | Permeate Backwash Skid, Ground bushing/hubs in JB-0002, tighten flex to JB | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-19 | Dustin Futrell | 2019-08-19 | Fred Michael
WTD-01 | WTD-01 | PI03729 | Verified | Permeate Backwash Skid, Need to install low point drain on vertical conduit extending from J Box BRB10120 and floater uni-strut on conduit | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03730 | Verified | Permeate Backwash Skid, Anchor bolts on support stands need cut-off | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
WTD-01 | WTD-01 | PI03731 | Verified | Permeate Backwash Skid, Install condulet covers where missing on skid. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03732 | Verified | Permeate Backwash Skid, Install grounds to skids. | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
WTD-01 | WTD-01 | PI03733 | Verified | Permeate Backwash Skid, Install Phenolic Tag and ground Relay/Control Box. | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03734 | Verified | Elevated Area in West end of Demin Bldg, Ground all isolated skids on grating. | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03735 | Verified | Elevated Area in West end of Demin Bldg, Install grounds on all seal-tite flex and tighten flex connections. | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03736 | Verified | Elevated Area in West end of Demin Bldg, All JB's on isolated skids need phenolic tags. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03737 | Verified | Elevated Area in West end of Demin Bldg, Receptacle cover and condulet covers need installed on 10-WTD-LSL-0530. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03738 | Verified | Elevated Area in West end of Demin Bldg, install caps on uni-strut ends throughout area where missing. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
WTD-01 | WTD-01 | PI03739 | Verified | Demin Bldg, Overhead tray needs triple supports on all 90° turns, 1 center, within 2' of each outer end. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-20 | Dustin Futrell | 2019-08-20 | Fred Michael
WTD-01 | WTD-01 | PI03740 | Verified | Demin Bldg, Overhead tray needs cables in tray formed and tie-wrapped to rungs in good workmanship manner. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-20 | Dustin Futrell | 2019-08-20 | Fred Michael
WTD-01 | WTD-01 | PI03741 | Verified | Demin Bldg, Overhead tray barriers needs top conectors on all tray . | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-20 | Dustin Futrell | 2019-08-20 | Fred Michael
WTD-01 | WTD-01 | PI03743 | Verified | Demin Bldg, Trapeze supports for cable tray above West end elevated platform needs scabbed uni-strut extender removed and replaced with continuous coupled all -thread/unistrut trapeze, "NO SCABBING or SISTERING". | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
WTD-01 | WTD-01 | PI03744 | Verified | Demin Bldg, Cable tray needs labels throughout building. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
WTD-01 | WTD-01 | PI03745 | Verified | Demin Bldg, Cable tray needs bonding jumpers and/or grounding between upper and lower overhead cable tray throughout building. | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
WTD-01 | WTD-01 | PI03746 | Verified | Demin Bldg, Vertical conduit behind CP-0001 needs floating strut replaced with floater that includes all conduit above panel. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03747 | Verified | Demin Bldg, Conduit covers/low point drains need installed on conduit LB's behind CP-0001. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03748 | Verified | Demin Bldg, Loose cable connection on 10-WTD-X0041-2 in CP-0001. | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
WTD-01 | WTD-01 | PI03749 | Verified | Demin Bldg, plug hole in CP-0001, clean/close and add phenolic tag to outer door with more info. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03750 | Verified | Demin Bldg, External ground to CP-0001. | A | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-28 | Dustin Futrell | 2019-08-28 | Mike Tabbert
WTD-01 | WTD-01 | PI03751 | Verified | Demin Bldg, Fiber Patch Panel needs phenolic tag. 10-WTD-PNL-0001. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-14 | Dustin Futrell | 2019-08-14 | Mike Tabbert
WTD-01 | WTD-01 | PI03752 | Verified | Demin Bldg, Overhead cable tray on SW wall needs support, no supposrt last 12', previous support removed. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-16 | Dustin Futrell | 2019-08-16 | Fred Michael
WTD-01 | WTD-01 | PI03753 | Verified | Demin Bldg, Need all trash, debris, construction material and rope removed from all overhead cable tray. | B | E | Dustin Futrell | McD | 2019-08-09 | Dustin Futrell | Const | 2019-08-20 | Dustin Futrell | 2019-08-20 | Fred Michael
WTD-01 | WTD-01 | PI03762 | Verified | SV0075 NOT INSTALLED DRWG SHEET 14 OF 503818-AP01 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-16 | James Tanner | 2019-12-31 | Albert Burge
WTD-01 | WTD-01 | PI03763 | Verified | AE AND AIT 0080 NOT INTALLED SHEET 14 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-14 | James Tanner | 2019-12-31 | Albert Burge
WTD-01 | WTD-01 | PI03764 | Verified | AE AND AIT 0081 NOT INSTALLED SHEET 14 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-14 | James Tanner | 2019-12-31 | Albert Burge
WTD-01 | WTD-01 | PI03765 | Verified | AE AND AIT 0082 NOT INSTALLED SHEET 14 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-14 | James Tanner | 2019-12-31 | Albert Burge
WTD-01 | WTD-01 | PI03766 | Verified | LSL 0700 NOT INSTALLED SHEET 16 | B | I | Mike Tabbert | McD | 2019-08-12 | Mike Tabbert | Const | 2019-11-16 | James Tanner | 2019-12-31 | Albert Burge
WTD-01 | WTD-01 | PI03767 | Verified | PI 0701 NO METAL ID TAG | C | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-19 | Gonzalo Pena | 2019-08-19 | Albert Burge
WTD-01 | WTD-01 | PI03768 | Verified | LSL 200 NOT INSTALLED SHEET 17 | B | I | Mike Tabbert | McD | 2019-08-12 | Mike Tabbert | Const | 2019-11-16 | James Tanner | 2019-12-31 | Albert Burge
WTD-01 | WTD-01 | PI03769 | Verified | PI 201 NO METAL ID TAG SHEET 17 | C | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-19 | Gonzalo Pena | 2019-08-19 | Albert Burge
WTD-01 | WTD-01 | PI03770 | Verified | P-200A NO METAL ID TAG SHEET 17 | C | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-19 | Gonzalo Pena | 2019-08-19 | Albert Burge
WTD-01 | WTD-01 | PI03771 | Verified | DMP909B NOT INSTALLED SHEET 17 | A | P | James Beech | McD | 2019-08-12 | James Beech | Const | 2019-11-16 | James Beech | 2019-11-18 | Michael Law
WTD-01 | WTD-01 | PI03772 | Verified | P-200B NO METAL ID TAG SHEET 17 | C | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-19 | Gonzalo Pena | 2019-08-19 | Albert Burge
WTD-01 | WTD-01 | PI03773 | Verified | LSL 300 NOT INSTALLED SHEET 18 | B | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-16 | James Tanner | 2019-12-31 | Albert Burge
WTD-01 | WTD-01 | PI03774 | Verified | P-300A NO METAL ID TAG SHEET 18 | C | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-19 | Gonzalo Pena | 2019-08-19 | Albert Burge
WTD-01 | WTD-01 | PI03775 | Verified | P-300B NOT METAL ID TAG | C | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-19 | Gonzalo Pena | 2019-08-19 | Albert Burge
WTD-01 | WTD-01 | PI03776 | Verified | PI 301 NO METAL ID TAG SHEET 18 | C | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-19 | Gonzalo Pena | 2019-08-19 | Albert Burge
WTD-01 | WTD-01 | PI03777 | Verified | LSL0400 NOT INSTALLED SHEET 19 | B | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-16 | James Tanner | 2019-12-31 | Albert Burge
WTD-01 | WTD-01 | PI03778 | Verified | P-400A NOT METAL ID TAG SHEET 19 | C | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-19 | Gonzalo Pena | 2019-08-19 | Albert Burge
WTD-01 | WTD-01 | PI03779 | Verified | PI 400 NO METAL ID TAG SHEET 19 | C | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-19 | Gonzalo Pena | 2019-08-19 | Albert Burge
WTD-01 | WTD-01 | PI03780 | Verified | LSL 530 NOT INSTALLED SHEET 20 | B | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-16 | James Tanner | 2019-12-31 | Albert Burge
WTD-01 | WTD-01 | PI03781 | Verified | P-530A NO METAL ID TAG SHEET 20 | C | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-19 | Gonzalo Pena | 2019-08-19 | Albert Burge
WTD-01 | WTD-01 | PI03782 | Verified | P-530B NO METAL ID TAG SHEET 20 | C | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-19 | Gonzalo Pena | 2019-08-19 | Albert Burge
WTD-01 | WTD-01 | PI03783 | Verified | PI 565 NO METAL ID TAG SHEET 20 | C | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-19 | Gonzalo Pena | 2019-08-19 | Albert Burge
WTD-01 | WTD-01 | PI03784 | Verified | FSL 503 NEEDS TO BE RELOCATED PER SHEET 12 DRAWING 503818-AP01 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-09-06 | Gonzalo Pena | 2019-09-23 | Albert Burge
WTD-01 | WTD-01 | PI03785 | Verified | FV 547 CHANGE WESTLOCK INDICATOR TO RED FOR OPEN AND GREEN FOR CLOSED SHEET 1 | B | P | Kelvin Cook | McD | 2019-08-12 | Kelvin Cook | Const | 2019-11-18 | James Tanner | 2019-12-31 | Albert Burge
WTD-01 | WTD-01 | PI03786 | Verified | PSH 122 CHANGE PLASTIC NIPPLE TO SS NIPPLE SHEET 11 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Fred Michael
WTD-01 | WTD-01 | PI03787 | Verified | TT 126 NOT INSTALLED SHEET 11 | A | I | Mike Tabbert | McD | 2019-08-12 | Mike Tabbert | Const | 2019-09-06 | Mike Tabbert | 2019-10-09 | Albert Burge
WTD-01 | WTD-01 | PI03788 | Verified | LIT 110 NOT INSTALLED SHEET 11 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-11 | Gonzalo Pena | 2019-12-19 | Albert Burge
WTD-01 | WTD-01 | PI03789 | Verified | PT 504 NOT INSTALLED SHEET 3 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-10-09 | Albert Burge
WTD-01 | WTD-01 | PI03790 | Verified | AE 509A NOT INSTALLED SHEET4 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-10 | Martin Perry
WTD-01 | WTD-01 | PI03791 | Verified | AE 509B | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-10 | Martin Perry
WTD-01 | WTD-01 | PI03792 | Verified | PSH 532 REPLACE PLASTIC NIPPLE WITH SS NIPPLE SHEET 6 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Fred Michael
WTD-01 | WTD-01 | PI03793 | Verified | PLS 537 REPLACE PLASTIC NIPPLE WITH SS NIPPLE SHEET 8 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Fred Michael
WTD-01 | WTD-01 | PI03794 | Verified | PI 553 NOT INSTALLED SHEET 9 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-10 | Martin Perry
WTD-01 | WTD-01 | PI03795 | Verified | PI 554 NOT INSTALLED SHEET 9 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-09-10 | Martin Perry
WTD-01 | WTD-01 | PI03796 | Verified | PSH 564 REPLACE PLASTIC NIPPLE WITH SS NIPPLE SHEET 10 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Fred Michael
WTD-01 | WTD-01 | PI03797 | Verified | TIT 625 NOT INSTALLED SHEET 13 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-14 | James Tanner | 2019-12-19 | Albert Burge
WTD-01 | WTD-01 | PI03798 | Verified | LIT 624 NOT INSTALLED SHEET 13 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-12-19 | Albert Burge
WTD-01 | WTD-01 | PI03799 | Verified | LSL 628 NOT INSTALLED SHEET 13 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-16 | James Tanner | 2019-12-19 | Albert Burge
WTD-01 | WTD-01 | PI03800 | Verified | TW 627 NOT INSTALLED SHEET 13 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-12-19 | Albert Burge
WTD-01 | WTD-01 | PI03801 | Verified | TSH 627 NOT INSTALLED SHEET 13 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-12-19 | Albert Burge
WTD-01 | WTD-01 | PI03802 | Verified | TE 626 NOT INSTALLED SHEET 13 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-12-19 | Albert Burge
WTD-01 | WTD-01 | PI03803 | Verified | PSH 605 REPLACE PASTIC NIPPLE WITH SS NIPPLE | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Fred Michael
WTD-01 | WTD-01 | PI03804 | Verified | PT 606 REPLACE PLASTIC NIPPLE WITH SS NIPPLE | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Fred Michael
WTD-01 | WTD-01 | PI03805 | Verified | PI 607 PEPLACE PLASTIC NIPPLE WITH SS NIPPLE | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena |  | 2019-08-16 | Gonzalo Pena | 2019-08-21 | Fred Michael
WTD-01 | WTD-01 | PI03806 | Verified | TIGHTEN UNIONS IN PVC PIPE CLOSE TO QUIL 814 AND QUIL 815 ON CIP PUMP SKID. SHEET 2 | A | I | Gonzalo Pena | McD | 2019-08-12 | Gonzalo Pena | Const | 2019-08-28 | Gonzalo Pena | 2019-09-03 | Martin Perry
WTD-01 | WTD-01 | PI03825 | Verified | Complete pipe test & submit CCFs to turnover. | A | P | James Beech | McD | 2019-08-13 | James Beech | Const | 2019-11-07 | James Beech | 2019-11-19 | Ed Gober
WTD-01 | WTD-01 | PI03385 | Verified | Flex conduit not grounded for 10-WTD-FIT-0176 | A | E | Dustin Futrell | McD | 2019-08-08 | Dustin Futrell | Const | 2019-09-04 | Dustin Futrell | 2019-09-10 | Martin Perry
WTD-01 | WTD-01 | PI03387 | Verified | 10-WTD-FIT-0170 transmitter not wired | A | E | Dustin Futrell | McD | 2019-08-08 | Dustin Futrell | Const | 2019-11-18 | Dustin Futrell | 2019-11-21 | Albert Burge
WTD-01 | WTD-01 | PI03388 | Verified | Flex conduit not grounded for 10-WTD-FIT-0170 | A | E | Dustin Futrell | McD | 2019-08-08 | Dustin Futrell | Const | 2019-08-23 | Dustin Futrell | 2019-08-26 | Albert Burge
WTD-01 | WTD-01 | PI04347 | Verified | 10-WTD-PCV-0113 - NOT INSTALLED. | A | I | Eddie Vannoy | McD | 2019-08-20 | Eddie Vannoy | Const | 2019-09-11 | Eddie Vannoy | 2019-09-25 | Shannon Scott
WTD-01 | WTD-01 | PI08451 | Verified | 10-WTD-PI-0109 - has broken piping nipple, needs replaced. | A | I | Gonzalo Pena | McD | 2019-10-02 | Gonzalo Pena | Const | 2019-10-16 | Gonzalo Pena | 2019-11-07 | Shannon Scott
WTD-01 | WTD-01 | PI09830 | Verified | Test Package WTD-T-02 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-11 | Kelvin Cook
WTD-01 | WTD-01 | PI09831 | Verified | Test Package WTD-T-10 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-11 | Kelvin Cook
WTD-01 | WTD-01 | PI09832 | Verified | Test Package WTD-T-12 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-11 | Kelvin Cook
WTD-01 | WTD-01 | PI09833 | Verified | Test Package WTD-T-26 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-11 | Kelvin Cook
WTD-01 | WTD-01 | PI09834 | Verified | Test Package WTD-T-27 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-11 | Kelvin Cook
WTD-01 | WTD-01 | PI12622 | Verified | Install UF filter rack. | A | P | James Beech | McD | 2019-10-29 | James Beech | Const | 2019-11-16 | James Beech | 2019-11-21 | Albert Burge
WTD-01 | WTD-01 | PI12623 | Verified | Install vcuum breakers and air release valves. | A | P | James Beech | McD | 2019-10-29 | James Beech | Const | 2019-11-07 | James Beech | 2020-01-22 | Michael Law
WTD-01 | WTD-01 | PI12624 | Verified | Install piping to chemical feed tanks. | B | P | James Beech | McD | 2019-10-29 | James Beech | Const | 2019-12-07 | Michael Law | 2020-01-22 | Michael Law
WTD-01 | WTD-01 | PI12885 | Verified | 10-WTD-SKD-0700: need to install 10-WTD-DMP-0902A & 0902B "Pulsation Dampener" | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-14 | Kelvin Cook
WTD-01 | WTD-01 | PI12886 | Verified | 10-WTD-SKD-0200: need to install 10-WTD-DMP-0909A & 0909B "Pulsation Dampener" | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-02 | James Beech | 2019-12-14 | Kelvin Cook
WTD-01 | WTD-01 | PI12887 | Verified | 10-WTD-SKD-0300: missing valve handle | A | P | James Beech | McD | 2019-11-11 | James Beech | Const |  |  | 2019-11-19 | Kelvin Cook
WTD-01 | WTD-01 | PI15574 | Verified | 10-WTD-V-0545 - Inoperable valve, handle needs rotated | C | P | Tim Green | McD | 2020-01-08 | Tim Green | Comm | 2020-05-29 | James Beech | 2020-11-25 | Dave Goldak
WTD-01 | WTD-01 | PI15575 | Verified | 10-WTD-T-0200 - The sodium hypochlorite tote in the demin building has a crack on the top. It is above the liquid level, so it is not leaking out. It has been circled with a sharpie to help identify the area of concern. | C | P | William Mitchell | McD | 2020-01-08 | William Mitchell | Comm |  |  | 2020-01-15 | Nelson Eichelberger
WTD-01 | WTD-01 | PI15910 | Verified | RO Membranes ladder - On one side of the ladder, the top rung is 2" from the platform; and, on the other side, the rung is 3" from the platform. Also, the actual platform creates a potential hazard for a head injury. | C | S | Tim Gallegos | McD | 2020-01-13 | Tim Gallegos | Comm | 2020-05-07 | Tim Gallegos | 2020-07-10 | Dave Goldak
WTD-01 | WTD-01 | PI15911 | Verified | 10-WTD-V-0877 - Valve is missing label | C | P | James Beech | McD | 2020-01-13 | James Beech | Comm | 2020-05-27 | James Beech | 2020-11-25 | Dave Goldak
WTD-01 | WTD-01 | PI15912 | Verified | Demin Bldg Plant north door not working properly | C | S | Sheri Fritz | MOO | 2020-01-13 | Sheri Fritz | Comm | 2020-02-05 | Tim Mills | 2020-02-10 | Shannon Scott
WTD-01 | WTD-01 | PI15913 | Verified | 10-WTD-V-0879 (UF Backwash Pump Outlet) - Pump discharge piping has a crack in it. | B | P | James Beech | McD | 2020-01-13 | James Beech | Comm | 2020-01-21 | Tim Green | 2020-01-23 | Shannon Scott
WTD-01 | WTD-01 | PI15914 | Verified | 10-WTD-V-0883 (UF Forwarding Pump Outlet) - The pump outlet piping has a crack in it. | B | P | James Beech | McD | 2020-01-13 | James Beech | Comm | 2020-01-21 | Tim Green | 2020-01-23 | Shannon Scott
WTD-01 | WTD-01 | PI15915 | Verified | 10-WTD-P-0600 (CIP Pump) - packing glands need guard for rotating equipment | C | M | Shane Crowe | McD | 2020-01-13 | Shane Crowe | Comm | 2020-01-20 | Shane Crowe | 2020-02-02 | Shannon Scott
WTD-01 | WTD-01 | PI15916 | Verified | 10-WTD-P-0120 (UF Backwash Pump) - packing glands need guard for rotating equipment | C | M | Shane Crowe | McD | 2020-01-13 | Shane Crowe | Comm | 2020-01-20 | Shane Crowe | 2020-02-02 | Shannon Scott
WTD-01 | WTD-01 | PI15917 | Verified | 10-WTD-P-0110 (UF Permeate Forwarding Pump) - packing glands need guard for rotating equipment | C | M | Shane Crowe | McD | 2020-01-13 | Shane Crowe | Comm | 2020-01-20 | Shane Crowe | 2020-02-02 | Shannon Scott
WTD-01 | WTD-01 | PI16684 | Verified | 25% Caustic Tote Skid Valve - 10-WTD-SKID-0530 - "A" discharge drain valve is leaking by & Caustic is dripping on the ground | B | M | William Mitchell | McD | 2020-02-07 | William Mitchell | Comm | 2020-03-17 | William Mitchell | 2020-04-07 | Bernard Stasse
WTD-01 | WTD-01 | PI17455 | Verified | 10-WTD-SV-0507 Solenoid Valve tubing missing clamp at South side of RO skid | C | I | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-19 | Tim Green | 2020-08-17 | Dave Goldak
WTD-01 | WTD-01 | PI17456 | Verified | Tubing drain added to 10-WTD-0603; Service Water to UF Air Release Valve is not indicated on Suez P&ID | C | P | Charles Worthington | McD | 2020-03-03 | Charles Worthington | Comm | 2020-04-28 | James Beech | 2020-07-22 | John Watts
WTD-01 | WTD-01 | PI17457 | Verified | Reinstall phenolic label to Demin Water Silica Analyzer | C | P | Tim Green | McD | 2020-03-03 | Tim Green | Comm | 2020-05-29 | James Beech | 2020-08-17 | Dave Goldak
WTD-01 | WTD-01 | PI17458 | Verified | 10-WTD-AE-0508; SDI Analyzer is not working | B | I | Albert Burge | McD | 2020-03-03 | Albert Burge | Comm | 2020-03-10 | Albert Burge | 2021-05-24 | Keith Pollock
WTD-01 | WTD-01 | PI17459 | Verified | Demin Water Sodium analyzer has not been commissioned - 3/27 in progress and parts on order | C | I | Albert Burge | McD | 2020-03-03 | Albert Burge | Comm | 2020-07-21 | Mike Tabbert | 2021-04-26 | Keith Pollock
WTD-01 | WTD-01 | PI17460 | Verified | Change wording on phenolic label to read Resistivity instead of Conductivity at 10-WTD-AIT-0082; Analysis Indicating Transmitter | C | P | Mike Tabbert | McD | 2020-03-03 | Mike Tabbert | Comm | 2020-04-07 | Mike Tabbert | 2020-04-16 | Keith Pollock
WTD-01 | WTD-01 | PI17461 | Verified | Tubing fitting leak at inlet side of 10-WTD-AE-1002; Demin Mixed Bed Resistivity Analyzer, currently wrapped with electrical tape | C | I | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-04-09 | James Beech | 2020-04-16 | Keith Pollock
WTD-01 | WTD-01 | PI17462 | Verified | 10-WTD-PI-0543; Demin Self Cleaning Filter Inlet Pressure Gauge needs to be straightened, currently cocked to one side causing poor visibility | C | I | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-05 | James Beech | 2020-05-12 | Stacey Thibodeaux
WTD-01 | WTD-01 | PI17463 | Verified | Door lock missing at East entrance to Demin Bldg | C | C | Tim Gallegos | McD | 2020-03-03 | Tim Gallegos | Comm | 2020-05-11 | Tim Gallegos | 2020-08-17 | Dave Goldak
WTD-01 | WTD-01 | PI17464 | Verified | Tag all system components | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-07 | James Beech | 2021-01-22 | Eric Policarpio
WTD-01 | WTD-01 | PI17465 | Verified | Seal all piping penetrations in the Demin Water Bldg | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-08-20 | Tim Green | 2020-11-25 | Dave Goldak
WTD-01 | WTD-01 | PI17466 | Verified | 1" high point vent valve located on 4" RO CIP Feed line is not indicated on Suez P&ID's, vent valve located between 10-WTD-V-0813; RO CIP Feed Butterlfy Valve and 10-WTD-V-0817; RO CIP Butterfly Valve | C | P | Charles Worthington | McD | 2020-03-03 | Charles Worthington | Comm | 2020-06-10 | Charles Worthington | 2020-07-29 | John Watts
WTD-01 | WTD-01 | PI17467 | Verified | 1" high point vent valve located on 4" RO CIP Feed line, located between 10-WTD-V-0813; RO CIP Feed Butterlfy Valve and 10-WTD-V-0817; RO CIP Butterfly Valve valve cannot be fully closed, valve handle manipulation interferred with by adjacent potable water line, | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-05-19 | Tim Green | 2020-08-17 | Dave Goldak
WTD-01 | WTD-01 | PI17468 | Verified | Draw down tube vent needs to be run through grating at RO Caustic Injection Skid | C | P | James Beech | McD | 2020-03-03 | James Beech | Comm | 2020-08-20 | Tim Green | 2020-11-25 | Dave Goldak
WTD-01 | WTD-01 | PI18090 | Verified | 10-WTD-SKD-0100, 10-WTD-SKD-0500, and 10-WTD-SKD-0600 - Drains/trenches need to be added at the bottom of the frame for the UF/RO System Skid, CIP Forwarding Skid, and Permeate/Backwash Skid. The areas fill with water and have no way to be drained. | C | M | Johnny Campbell | McD | 2020-03-18 | Johnny Campbell | Comm | 2020-04-28 | Johnny Campbell | 2020-04-28 | Mark Williamson
WTD-01 | WTD-01 | PI18144 | Verified | 10-WTD-SRV-0020 - The Safety Relief Valve located on the incoming service water header in the Demin Building, 10-WTD-SRV-0020, has a constant leak by. | C | P | Charles Worthington | McD | 2020-03-20 | Charles Worthington | Comm | 2020-06-18 | Jason Ezell | 2020-06-18 | Jason Ezell
WTD-01 | WTD-01 | PI18152 | Verified | Demin Water Production - The demin plant cannot keep up during startup. The demin tank is emptied during cold fill. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-03-31 | William Mitchell | 2020-11-25 | Dave Goldak
WTD-01 | WTD-01 | PI18200 | Verified | Suez Commissioning Field Service Report to submit | C | M | William Mitchell | McD | 2020-03-30 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2020-04-15 | Eric Policarpio
WTD-02 | WTD-02 | PI02700 | Verified | LK-10-WTD-PD-P40-0092-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-07-24 | Damon Turner | 2019-07-24 | Tom Noble
WTD-02 | WTD-02 | PI02701 | Verified | LK-10-WTD-PD-P40-0450-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-08 | Damon Turner | 2019-08-12 | Tom Noble
WTD-02 | WTD-02 | PI02702 | Verified | LK-10-WTD-PD-P41-0179-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-06 | Damon Turner | 2019-08-06 | Tom Noble
WTD-02 | WTD-02 | PI02703 | Verified | LK-10-WTD-PD-P41-0250-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-12 | Damon Turner | 2019-08-12 | Tom Noble
WTD-02 | WTD-02 | PI02704 | Verified | LK-10-WTD-PD-P41-0250-03 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-08 | Damon Turner | 2019-08-12 | Tom Noble
WTD-02 | WTD-02 | PI02705 | Verified | LK-10-WTD-PD-P41-0255-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-08 | Damon Turner | 2019-08-12 | Tom Noble
WTD-02 | WTD-02 | PI02706 | Verified | LK-10-WTD-PD-P41-0437-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-08 | Damon Turner | 2019-08-12 | Tom Noble
WTD-02 | WTD-02 | PI02829 | Verified | 10-WTD-0370A & 0370B replace plastic plug with vent | A | I | Gonzalo Pena | McD | 2019-07-27 | Gonzalo Pena | Const | 2019-08-14 | Gonzalo Pena | 2019-08-15 | Albert Burge
WTD-02 | WTD-02 | PI02830 | Verified | 10-WTD-PIT-0373 tubing need to be connected to instrument and at root valve when reinstated | A | I | Gonzalo Pena | McD | 2019-07-27 | Gonzalo Pena | Const | 2019-08-07 | Gonzalo Pena | 2019-08-12 | Albert Burge
WTD-02 | WTD-02 | PI02831 | Verified | 10-WTD-FIT-0421 needs a tag and replace plastic plug with permanent plug | B | I | Gonzalo Pena | McD | 2019-07-27 | Gonzalo Pena | Const | 2019-08-08 | Gonzalo Pena | 2019-08-08 | Fred Michael
WTD-02 | WTD-02 | PI02832 | Verified | 10-WTD-M-0800A & 0800B needs tags | B | I | Gonzalo Pena | McD | 2019-07-27 | Gonzalo Pena | Const | 2019-08-01 | Gonzalo Pena | 2019-08-16 | Logan Holland
WTD-02 | WTD-02 | PI02833 | Verified | 10-WTD-M-0800A & 0800B seal tight & ductbank grounded | B | E | Dustin Futrell | McD | 2019-07-27 | Dustin Futrell | Const | 2019-08-01 | Ken Mundy | 2019-08-16 | Logan Holland
WTD-02 | WTD-02 | PI02834 | Verified | WTD Foundation supports need to be grouted | B | C | Johnny Campbell | McD | 2019-07-27 | Johnny Campbell | Const | 2019-08-20 | Johnny Campbell | 2019-08-21 | Fred Michael
WTD-02 | WTD-02 | PI02835 | Verified | 10-WTD-PI-0363A & 0363B need to be installed | A | I | Gonzalo Pena | McD | 2019-07-27 | Gonzalo Pena | Const | 2019-08-07 | Gonzalo Pena | 2019-08-12 | Albert Burge
WTD-02 | WTD-02 | PI02836 | Verified | 10-WTD-PI-0363A & 0363B replace plastic plugs with vents | A | I | Gonzalo Pena | McD | 2019-07-27 | Gonzalo Pena | Const | 2019-08-14 | Gonzalo Pena | 2019-08-15 | Albert Burge
WTD-02 | WTD-02 | PI02837 | Verified | Wrong hardware for flange 10-WTD-LIT-0800 | B | I | Eddie Vannoy | McD | 2019-07-27 | Eddie Vannoy | Const |  |  | 2019-10-05 | J.L. Bickham
WTD-02 | WTD-02 | PI02838 | Verified | Tighten and torque 10-WTD-LIT-0800 | B | I | Gonzalo Pena | McD | 2019-07-27 | Gonzalo Pena | Const |  |  | 2019-10-05 | J.L. Bickham
WTD-02 | WTD-02 | PI02839 | Verified | Tag 10-WTD-LIT-0800 | B | I | Gonzalo Pena | McD | 2019-07-27 | Gonzalo Pena | Const | 2019-08-01 | Gonzalo Pena | 2019-08-12 | Albert Burge
WTD-02 | WTD-02 | PI02840 | Verified | 10-WTD-LIT-0800 remove plastic cap and install gasket | A | I | Gonzalo Pena | McD | 2019-07-27 | Gonzalo Pena | Const | 2019-08-01 | Gonzalo Pena | 2019-08-12 | Albert Burge
WTD-02 | WTD-02 | PI02845 | Verified | Tag all valves. | B | P | Justin Houdeshell | McD | 2019-07-29 | Justin Houdeshell | Const | 2019-08-08 | Justin Houdeshell | 2019-08-12 | Albert Burge
WTD-02 | WTD-02 | PI02955 | Verified | Coating repair needed inside Demin. Tank. | A | X | Michael Law | McD | 2019-08-01 | Michael Law | Const | 2019-08-27 | Michael Law | 2019-08-27 | Michael Law
WTD-02 | WTD-02 | PI03377 | Verified | 10-WTD-PI-0363A not installed | A | I | Gonzalo Pena | McD | 2019-08-08 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-12 | Albert Burge
WTD-02 | WTD-02 | PI03378 | Verified | 10-WTD-PI-0370A not installed | A | I | Gonzalo Pena | McD | 2019-08-08 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-12 | Albert Burge
WTD-02 | WTD-02 | PI03379 | Verified | 10-WTD-PI-0363B not installed | A | I | Gonzalo Pena | McD | 2019-08-08 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-12 | Albert Burge
WTD-02 | WTD-02 | PI03380 | Verified | Discharge piping missing from 10-WTD-P-0800A | A | P | Terry Deaton | McD | 2019-08-08 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-15 | Albert Burge
WTD-02 | WTD-02 | PI03381 | Verified | Discharge piping missing from 10-WTD-P-0800B | A | P | Terry Deaton | McD | 2019-08-08 | Terry Deaton | Const | 2019-08-09 | Terry Deaton | 2019-08-15 | Albert Burge
WTD-02 | WTD-02 | PI03382 | Verified | Tubing not connected for 10-WTD-PIT-0373 | A | I | Gonzalo Pena | McD | 2019-08-08 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-12 | Albert Burge
WTD-02 | WTD-02 | PI03383 | Verified | 10-WTD-LIT-0800 bolts are too short no threads showing past nut | A | I | Gonzalo Pena | McD | 2019-08-08 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-21 | Fred Michael
WTD-02 | WTD-02 | PI03384 | Verified | Piping to tank 10-WTD-T-0800 not complete | A | P | Damon Turner | McD | 2019-08-08 | Damon Turner | Const | 2019-08-09 | Terry Deaton | 2019-08-21 | Fred Michael
WTD-02 | WTD-02 | PI03386 | Verified | 10-WTD-FIT-0176 has a plastic plug in electronic housing | A | I | Gonzalo Pena | McD | 2019-08-08 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-15 | Martin Perry
WTD-02 | WTD-02 | PI03389 | Verified | 10-WTD-FIT-0170 thas a plastic plug in electronic housing | A | I | Gonzalo Pena | McD | 2019-08-08 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-15 | Martin Perry
WTD-02 | WTD-02 | PI03390 | Verified | Bolts for 10-WTD-CHK-0450 are too short | B | P | Eddie Vannoy | McD | 2019-08-08 | Eddie Vannoy | Const |  |  | 2019-10-05 | J.L. Bickham
WTD-02 | WTD-02 | PI03391 | Verified | 10-WTD-CHK-0450 has no tag | B | I | Gonzalo Pena | McD | 2019-08-08 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-21 | Fred Michael
WTD-02 | WTD-02 | PI03392 | Verified | 10-WTD-V-0452 has no tag | B | I | Gonzalo Pena | McD | 2019-08-08 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-21 | Fred Michael
WTD-02 | WTD-02 | PI03393 | Verified | 10-WTD-V-0451 has no tag | B | I | Gonzalo Pena | McD | 2019-08-08 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-21 | Fred Michael
WTD-02 | WTD-02 | PI03394 | Verified | 10-WTD-V-0454 has no tag | B | I | Gonzalo Pena | McD | 2019-08-08 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-21 | Fred Michael
WTD-02 | WTD-02 | PI03395 | Verified | 10-WTD-AOV-0453 has no tag and no tubing | A | I | Gonzalo Pena | McD | 2019-08-08 | Gonzalo Pena | Const | 2019-08-09 | Gonzalo Pena | 2019-08-21 | Fred Michael
WTD-02 | WTD-02 | PI03396 | Verified | 10-WTD-AOV-0453 not wired | A | E | Dustin Futrell | McD | 2019-08-08 | Dustin Futrell | Const | 2019-09-05 | Dustin Futrell | 2019-09-20 | Martin Perry
WTD-02 | WTD-02 | PI03397 | Verified | 10-WTD-V-0340 handle is too long, cannot fully operate | A | P | Terry Deaton | McD | 2019-08-08 | Terry Deaton | Const | 2019-08-19 | Terry Deaton | 2019-08-21 | Fred Michael
WTD-02 | WTD-02 | PI03826 | Verified | Complete pipe test & submit CCFs to turnover. | A | P | Damon Turner | McD | 2019-08-13 | Damon Turner | Const | 2019-09-16 | Damon Turner | 2019-09-16 | Ed Gober
WTD-02 | WTD-02 | PI04349 | Verified | After Comm. Motor run-ins install pump motor couplings and covers | B | M | Shane Crowe | McD | 2019-08-21 | Shane Crowe | Const | 2019-08-28 | Shane Crowe | 2019-08-28 | Joshua Sturgeon
WTD-02 | WTD-02 | PI04350 | Verified | Replace ty-wraps with hose clamp around poison pads | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-26 | Terry Deaton | 2019-09-18 | Kelvin Cook
WTD-02 | WTD-02 | PI04351 | Verified | 10-WTD-TI-0370 swap tags | C | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-12-12 | Michael Law
WTD-02 | WTD-02 | PI04352 | Verified | All threaded connections need teflon tape removed and use teflon paste. | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-26 | Terry Deaton | 2019-09-18 | Kelvin Cook
WTD-02 | WTD-02 | PI04353 | Verified | 10-WTD-CHK-0411 installed backwards | A | P | Terry Deaton | McD | 2019-08-21 | Terry Deaton | Const | 2019-08-26 | Terry Deaton | 2019-08-29 | Kelvin Cook
WTD-02 | WTD-02 | PI04354 | Verified | Grout around pipe support on demin pumps skid foundation | C | C | Johnny Campbell | McD | 2019-08-21 | Johnny Campbell | Const | 2019-09-12 | Jack Fields | 2019-10-03 | Kelvin Cook
WTD-02 | WTD-02 | PI04355 | Verified | Carbon contamination at branch from 10-WTD-0410 - Line WTD-0420 | C | X | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-26 | Terry Deaton | 2019-10-03 | Nelson Eichelberger
WTD-02 | WTD-02 | PI04356 | Verified | Pump B drain line needs readjusting so it can lay on support | B | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-09-04 | Gonzalo Pena | 2019-10-04 | Joshua Sturgeon
WTD-02 | WTD-02 | PI04357 | Verified | Support for power feed to 10-WTD-FIT-0241 needs to be tighten | C | E | Chris Colvin | McD | 2019-08-21 | Chris Colvin | Const | 2019-10-25 | Dustin Futrell | 2019-12-05 | Kelvin Cook
WTD-02 | WTD-02 | PI04358 | Verified | Clean all concrete debris and tape from pipe | C | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-26 | Terry Deaton | 2019-10-05 | Kelvin Cook
WTD-02 | WTD-02 | PI04359 | Verified | Connect instrument tubing to valve 10-WTD-PIT-0373 | A | I | Gonzalo Pena | McD | 2019-08-21 | Gonzalo Pena | Const | 2019-08-27 | Gonzalo Pena | 2019-08-29 | Kelvin Cook
WTD-02 | WTD-02 | PI04360 | Verified | 10-WTD-P40-0450 missing S.S wrap and clamps HGR0022, HGR 0021, HGR 0020 | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-22 | Damon Turner | 2019-08-27 | Kelvin Cook
WTD-02 | WTD-02 | PI04361 | Verified | 10-WTD-CHK-0450 change bolts | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-05 | Michael Law | 2019-09-05 | Michael Law
WTD-02 | WTD-02 | PI04362 | Verified | 10-WTD-PD-P40-0175-04 10-WTD-V-0175 missing valve handle | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-22 | Damon Turner | 2019-08-29 | Kelvin Cook
WTD-02 | WTD-02 | PI04363 | Verified | No control wire for 10-WTD-FIT-0176 | A | I | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-26 | Dustin Futrell | 2019-09-26 | Albert Burge
WTD-02 | WTD-02 | PI04364 | Verified | No control wire for 10-WTD-FIT-0170 | A | I | Dustin Futrell | McD | 2019-08-21 | Dustin Futrell | Const | 2019-09-26 | Dustin Futrell | 2019-09-26 | Albert Burge
WTD-02 | WTD-02 | PI04366 | Verified | 10-WTD-PD-P41-0437-01 Install HGR-0034 | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-26 | Damon Turner | 2019-10-03 | Kelvin Cook
WTD-02 | WTD-02 | PI04367 | Verified | 1C Sample Panel Building 10-WTD-P41-0460 connection incomplete | A | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-28 | Terry Deaton | 2019-09-03 | Kelvin Cook
WTD-02 | WTD-02 | PI04368 | Verified | 1A Sample Panel Building install 2" x 1" tee and valve | D | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-26 | Terry Deaton | 2019-10-03 | Kelvin Cook
WTD-02 | WTD-02 | PI04369 | Verified | 1B Sample Panel Building install 2" x 1" tee and valve. (1" gate valve). | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-03 | Kelvin Cook
WTD-02 | WTD-02 | PI04370 | Verified | Flange connection has to much amount of thread on bolts on the top of the blade wash skid | B | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-22 | Damon Turner | 2019-10-03 | Kelvin Cook
WTD-02 | WTD-02 | PI04371 | Verified | Rework spool 10-WTD-0440. Incorrect plum in East, West, North and South direction | C | P | Damon Turner | McD | 2019-08-21 | Damon Turner | Const | 2019-08-26 | Damon Turner | 2019-10-03 | Nelson Eichelberger
WTD-02 | WTD-02 | PI04372 | Verified | Line 10-WTD-0440 install threaded cap and seal weld after tightening | A | P | Terry Deaton | McD | 2019-08-21 | Terry Deaton | Const | 2019-08-26 | Terry Deaton | 2019-08-28 | Kelvin Cook
WTD-02 | WTD-02 | PI04373 | Verified | 10-WTD-0255-52X1-FP-2.0 Underground first support on riser -Verify installation is correct | B | P | Kelvin Cook | McD | 2019-08-21 | Kelvin Cook | Const | 2019-09-06 | Kelvin Cook | 2019-09-06 | Kelvin Cook
WTD-02 | WTD-02 | PI04374 | Verified | Tag all valves | C | P | James Beech | McD | 2019-08-21 | James Beech | Const | 2020-05-04 | Michael Law | 2020-05-04 | Michael Law
WTD-02 | WTD-02 | PI06841 | Verified | 10-WTD-PD-P40-0390-02 - 10-WTD-V-0372B need to swap out the CS cap screws with PTFE | B | I | James Beech | McD | 2019-09-23 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
WTD-02 | WTD-02 | PI06842 | Verified | 10-WTD-PD-P40-0370-02 - 10-WTD-V-0372A need to swap out the CS cap screws with PTFE | B | P | James Beech | McD | 2019-09-23 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
WTD-02 | WTD-02 | PI06843 | Verified | 10+-WTD-PD-P40-0510-01 - 10-WTD-V-0510A and 0510B need to change out the CS cap screws aith PTFE | B | P | James Beech | McD | 2019-09-23 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
WTD-02 | WTD-02 | PI08452 | Verified | 110-WTD-P-800A/B - Demin forwarding pumps missing guard around packing gland, rotating equipment hazard”. | B | M | Shane Crowe | McD | 2019-10-02 | Shane Crowe | Const | 2020-02-07 | Shane Crowe | 2020-02-10 | Shannon Scott
WTD-02 | WTD-02 | PI09141 | Verified | 10-WTD-V-0530 and 10-WTD-CHK-0532 - red line P&ID WTD-03 to show as installed in field & per ISO. | C | P | Kelvin Cook | McD | 2019-10-05 | Kelvin Cook | Comm | 2019-11-05 | J.L. Bickham | 2019-12-14 | J.L. Bickham
WTD-02 | WTD-02 | PI18097 | Verified | 10-WTD-P-0800A, 10-WTD-P-0800B, 10-WTD-FV-0421 - Demin forwarding pump P-800 and min flow control valve FV-421 design. The max flow through the min flow bypass valve FV-421 (per spec sheet) is 331 gpm (average flow of 166 gpm). The control description says the setpoint for the bypass valve is 390 gpm. Does it really make sense for the setpoint to be above the max capacity of the valve? | C | M | Charles Worthington | McD | 2020-03-18 | Charles Worthington | Comm | 2020-06-23 | Dale Carroll | 2020-07-22 | John Watts
WTD-02 | WTD-02 | PI18201 | Verified | Suez Commissioning Field Service Report to submit | C | M | William Mitchell | McD | 2020-03-30 | William Mitchell | Comm | 2020-04-15 | William Mitchell | 2020-04-15 | Eric Policarpio
WWT-01 | WWT-01 | PI02707 | Verified | LK-10-WWT-PD-P41-0115-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-20 | Damon Turner | 2019-08-20 | Tom Noble
WWT-01 | WWT-01 | PI02708 | Verified | LK-10-WWT-PD-P41-0140-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-22 | Damon Turner | 2019-08-22 | Tom Noble
WWT-01 | WWT-01 | PI02709 | Verified | LK-10-WWT-PD-P41-0150-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-07 | Damon Turner | 2019-08-07 | Tom Noble
WWT-01 | WWT-01 | PI02710 | Verified | LK-10-WWT-PD-P41-0160-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-28 | Damon Turner | 2019-08-28 | Tom Noble
WWT-01 | WWT-01 | PI02711 | Verified | LK-10-WWT-PD-P41-0160-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-22 | Damon Turner | 2019-08-22 | Tom Noble
WWT-01 | WWT-01 | PI02712 | Verified | LK-10-WWT-PD-P41-0160-03 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-28 | Damon Turner | 2019-08-28 | Bijo Varghese
WWT-01 | WWT-01 | PI02713 | Verified | LK-10-WWT-PD-P41-0160-04 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-09-05 | Damon Turner | 2019-09-05 | Lucas Foster
WWT-01 | WWT-01 | PI02714 | Verified | LK-10-WWT-PD-P41-0160-05 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-28 | Damon Turner | 2019-09-09 | Tom Noble
WWT-01 | WWT-01 | PI02715 | Verified | LK-10-WWT-PD-P41-0165-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-28 | Damon Turner | 2019-09-09 | Tom Noble
WWT-01 | WWT-01 | PI02716 | Verified | LK-10-WWT-PD-P41-0165-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-20 | Damon Turner | 2019-08-20 | Tom Noble
WWT-01 | WWT-01 | PI02717 | Verified | LK-10-WWT-PD-P41-0165-03 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-28 | Damon Turner | 2019-09-09 | Tom Noble
WWT-01 | WWT-01 | PI02718 | Verified | LK-10-WWT-PD-P41-0170-01 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-16 | Terry Deaton
WWT-01 | WWT-01 | PI02719 | Verified | LK-10-WWT-PD-P41-0170-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-16 | Terry Deaton
WWT-01 | WWT-01 | PI02720 | Verified | LK-10-WWT-PD-P41-0170-03 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-16 | Damon Turner | 2019-08-16 | Terry Deaton
WWT-01 | WWT-01 | PI02721 | Verified | LK-10-WWT-PD-P41-0170-04 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-06 | Tom Noble
WWT-01 | WWT-01 | PI02722 | Verified | LK-10-WWT-PD-P41-0170-05 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-09-06 | Damon Turner | 2019-09-06 | Tom Noble
WWT-01 | WWT-01 | PI02723 | Verified | LK-10-WWT-PD-P41-0172-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-13 | Tom Noble
WWT-01 | WWT-01 | PI02724 | Verified | LK-10-WWT-PD-P41-0172-03 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-13 | Tom Noble
WWT-01 | WWT-01 | PI02725 | Verified | LK-10-WWT-PD-P41-0172-04 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-28 | Damon Turner | 2019-09-05 | Tom Noble
WWT-01 | WWT-01 | PI02726 | Verified | LK-10-WWT-PD-P41-0176-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-13 | Damon Turner | 2019-08-13 | Tom Noble
WWT-01 | WWT-01 | PI02727 | Verified | LK-10-WWT-PD-P41-0176-03 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-28 | Damon Turner | 2019-08-29 | Bijo Varghese
WWT-01 | WWT-01 | PI02728 | Verified | LK-10-WWT-PD-P41-0176-04 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-28 | Damon Turner | 2019-09-05 | Tom Noble
WWT-01 | WWT-01 | PI02729 | Verified | LK-10-WWT-PD-P42-0180-02 - Need Welds Cleared | A | P | Damon Turner | McD | 2019-07-23 | Damon Turner | Const | 2019-08-28 | Damon Turner | 2019-09-06 | Tom Noble
WWT-01 | WWT-01 | PI04606 | Verified | Install stilling well for 10-WWT-LIT-0001 at Wate water collection sump | A | I | Gonzalo Pena | McD | 2019-08-24 | Gonzalo Pena | Const | 2019-09-13 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
WWT-01 | WWT-01 | PI05805 | Verified | Ground cable trays. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-10-02 | Richard Cruz | 2019-10-05 | Mike Tabbert
WWT-01 | WWT-01 | PI05807 | Verified | Trim ty-wraps in cable trays and ty-wrap cables where needed. | B | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-13 | Dustin Futrell | 2019-09-13 | Fred Michael
WWT-01 | WWT-01 | PI05808 | Verified | Check for missing divider plates in cable trays. | B | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-10-02 | Fred Michael
WWT-01 | WWT-01 | PI05809 | Verified | Couple up pumps after commissioning motor run-ins. | B | M | Shane Crowe | McD | 2019-09-13 | Shane Crowe | Const | 2019-10-18 | Shane Crowe | 2019-10-18 | Joshua Sturgeon
WWT-01 | WWT-01 | PI05810 | Verified | Trim checker plate around bolts at the WWT sump pumps. | B | M | Shane Crowe | McD | 2019-09-13 | Shane Crowe | Const | 2019-09-17 | Shane Crowe | 2019-10-04 | Joshua Sturgeon
WWT-01 | WWT-01 | PI05811 | Verified | Sump pump motors seal tite grounds are wrong size. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-20 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI05812 | Verified | Sump pump motors space heaters need seal tite. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-20 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI05813 | Verified | Ground seal tite on all instrumentation. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI05814 | Verified | Cable tray penetration on north side of the water treatment building needs flashing. | B | S | Tim Gallegos | McD | 2019-09-13 | Tim Gallegos | Const | 2019-09-13 | Mike Tabbert | 2019-09-13 | Mike Tabbert
WWT-01 | WWT-01 | PI05815 | Verified | Grout cable tray supports. | C | C | Johnny Campbell | McD | 2019-09-13 | Johnny Campbell | Const | 2019-12-05 | Johnny Campbell | 2019-12-14 | Michael Law
WWT-01 | WWT-01 | PI05816 | Verified | Install 10-WWT-FE-0015. | B | P | William Mitchell | McD | 2019-09-13 | William Mitchell | Const | 2019-12-10 | William Mitchell | 2019-12-10 | J.L. Bickham
WWT-01 | WWT-01 | PI05817 | Verified | Complete all instrumentation tubing. | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-11-05 | Albert Burge
WWT-01 | WWT-01 | PI05818 | Verified | Complete all instrumentation installation on Batch Neutralization Tanks. | A | P | Kelvin Cook | McD | 2019-09-13 | Kelvin Cook | Const | 2019-10-16 | Gonzalo Pena | 2019-11-05 | Albert Burge
WWT-01 | WWT-01 | PI05819 | Verified | Grout instrumentaion supports. | C | C | Johnny Campbell | McD | 2019-09-13 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2019-12-14 | Michael Law
WWT-01 | WWT-01 | PI05820 | Verified | Tighten & ground seal tite on 10-WWT-AOV-0014A. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
WWT-01 | WWT-01 | PI05821 | Verified | Conduit vertical risers require more support. | B | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI05822 | Verified | Batch Neutralization Tank containment needs clean up. | B | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-10-02 | Fred Michael
WWT-01 | WWT-01 | PI05823 | Verified | Several condulet covers missing throughout subsystem. | B | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-10-07 | Kelvin Cook
WWT-01 | WWT-01 | PI05824 | Verified | Conduit "T" (2) against south side of tank containment wall are facing wall. No maint. access. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-20 | Dustin Futrell | 2019-09-27 | Shannon Scott
WWT-01 | WWT-01 | PI05825 | Verified | 10-WWT-PI-0010B has broken gauge. | B | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-11-09 | James Tanner | 2019-12-12 | Joshua Sturgeon
WWT-01 | WWT-01 | PI05826 | Verified | Seal pipe pentrations at pumps / containment wall. | A | C | Johnny Campbell | McD | 2019-09-13 | Johnny Campbell | Const | 2019-09-25 | Johnny Campbell | 2019-12-19 | J.L. Bickham
WWT-01 | WWT-01 | PI05827 | Verified | Raise instrument stand for 10-WWT-PDIT-0005A (before grout). | B | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-25 | Shannon Scott
WWT-01 | WWT-01 | PI05828 | Verified | Remove unused anchor bolts in the Neut. Tanks containment. | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-07 | Kelvin Cook
WWT-01 | WWT-01 | PI05829 | Verified | Ground Neut. Tanks 10-WWT-T-0001A & B. Two (2) grounds each. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI05830 | Verified | Grout all supports in the Neut. Tanks containment. | B | C | Johnny Campbell | McD | 2019-09-13 | Johnny Campbell | Const | 2019-12-06 | Jack Fields | 2019-12-14 | Michael Law
WWT-01 | WWT-01 | PI05831 | Verified | Tie-off support to column at 10-WWT-AOV-0011A. | B | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI05832 | Verified | Move conduit away from pipe at 10-WWT-AOV-0011B. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI05833 | Verified | Tag all valves & instruments. | C | P | James Beech | McD | 2019-09-13 | James Beech | Const |  |  | 2020-01-30 | Fred Michael
WWT-01 | WWT-01 | PI05834 | Verified | Missing condulet covers on the caustic skid in the WTB. | B | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-10-14 | Fred Michael | 2019-10-14 | Fred Michael
WWT-01 | WWT-01 | PI05835 | Verified | Clean out the sulfuric acid control panel. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-10-10 | Dustin Futrell | 2019-11-07 | Mike Tabbert
WWT-01 | WWT-01 | PI05836 | Verified | Clean up all debris at the acid & caustic skids. | C | E | Chris Colvin | McD | 2019-09-13 | Chris Colvin | Const |  |  | 2020-01-30 | Fred Michael
WWT-01 | WWT-01 | PI05837 | Verified | In the acid control panel - wires for 10WWTX0002 should be labeled 1, 2, 3 & 4. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
WWT-01 | WWT-01 | PI05838 | Verified | In the caustic control panel - wires for 10WWTX0001 should be labeled 1, 2, 3 & 4. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
WWT-01 | WWT-01 | PI05839 | Verified | Cooling Tower PDC - clean out 10-NJS-MCC-0006B; cubicles 4C & 8K, including bottoms & tops. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
WWT-01 | WWT-01 | PI05840 | Verified | Cooling tower PDC - clean out 10-NJS-MCC-0006A; cubicles 4J & 8J, including bottoms & tops. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
WWT-01 | WWT-01 | PI05841 | Verified | Cooling tower PDC - shrink down wire tags that are loose / sliding. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
WWT-01 | WWT-01 | PI05842 | Verified | Cable 10WWTC0001 is stripped but not landed or wire tagged. | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-27 | Dustin Futrell | 2019-09-27 | Fred Michael
WWT-01 | WWT-01 | PI05872 | Verified | On ISO 10-WWT-PD-P40-0110-01 missing cap screws, handle at valve 10-WWT-V-0001A | A | P | James Beech | McD | 2019-09-13 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05873 | Verified | On ISO 10-WWT-PD-P40-0110-01 missing bolts at valve 10-WWT-CHK-0001A | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05874 | Verified | On ISO 10-WWT-PD-P40-0110-01 missing bolts to connection to 10-WWT-P-0001A/Dis | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05875 | Verified | On ISO 10-WWT-PD-P40-0110-02 missing cap screws at 10-WWT-AOV-0011A | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05876 | Verified | On ISO 10-WWT-PD-P40-0110-02 pipe support 10-WWT-PD-HGR-0002 no clamps | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05877 | Verified | On ISO 10-WWT-PD-P40-0110-02 pipe support 10-WWT-PD-HGR-0001 No ss wrap clamp and ubolt | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05878 | Verified | On ISO 10-WWT-PD-P40-0110-03 missing bolts and gasket on connection to 10-WWT-T-0001-A/A1 | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05879 | Verified | On ISO 10-WWT-PD-P40-0110-03 pipe support 10-WWT-PD-HGR-0003 missing clamps | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05880 | Verified | On ISO 10-WWT-PD-P40-0110-03 mising cap screws at 10-WWT-AOV-0011A | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05881 | Verified | On ISO 10-WWT-PD-P40-0115-01 missing cap screws at 10-WWT-V-0001B | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05882 | Verified | On ISO 10-WWT-PD-P40-0115-01 missing bolts at 10-WWT-CHK-0001B | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05883 | Verified | On ISO 10-WWT-PD-P40-0115-01 missing bolts at connection to 10-WWT-P-0001B/Dis | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05884 | Verified | ISO 10-WWT-PD-P40-0120-01 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05885 | Verified | ISO 10-WWT-PD-P40-0120-02 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05886 | Verified | ISO 10-WWT-PD-P40-0120-03 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05887 | Verified | ISO 10-WWT-PD-P40-0130-01 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05888 | Verified | On ISO 10-WWT-PD-P40-0140-01 missing bolts to connection to 10-WWT-STN-0005A/N2 inlet | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05889 | Verified | On ISO 10-WWT-PD-P40-0140-01 missing cap screws and gasket at 10-WWT-V-0014A | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05890 | Verified | On ISO 10-WWT-PD-P40-0140-01 missing bolts to connection to 10-WWT-T-0001-A/B1 | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Albert Burge
WWT-01 | WWT-01 | PI05891 | Verified | On ISO 10-WWT-PD-P40-0140-01 missing bolts at 10-WWT-EJ-0140 | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-09-25 | Damon Turner | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05892 | Verified | On ISO 10-WWT-PD-P40-0140-02 missing bolts to connection 10-WWT-STN-0005A/N1 outlet | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05893 | Verified | On ISO 10-WWT-PD-P40-0140-02 pipe support 10-WWT-PD-HGR-0013 missing 1 clamp. Guides not welded | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05894 | Verified | On ISO 10-WWT-PD-P40-0140-02 missing bolts at 10-WWT-EJ-0141 | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05895 | Verified | On ISO 10-WWT-PD-P40-0140-02 missing cap screws at connection to 10-WWT-P-0002A/N1 suct | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05896 | Verified | On IfSO 10-WWT-PD-P40-0150-01 missing bolts at connection 10-WWT-STN-0005B/N2 inlet | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-10-07 | Kelvin Cook
WWT-01 | WWT-01 | PI05897 | Verified | On IfSO 10-WWT-PD-P40-0150-01 missing bolts at 10-WWT-EJ-0150 | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05898 | Verified | On ISO 10-WWT-PD-P40-0150-01 missing bolts at connection 10-WWT-T-0001-B/B1 | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05899 | Verified | On ISO 10-WWT-PD-P40-0150-02 missing bolts to connection 10-WWT-STN-0005B/N1 outlet | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-10-07 | Kelvin Cook
WWT-01 | WWT-01 | PI05900 | Verified | On ISO 10-WWT-PD-P40-0150-02 pipe support 10-WWT-PD-HGR-0015 has no clamps | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05901 | Verified | On ISO 10-WWT-PD-P40-0150-02 missing bolts at 10-WWT-EJ-0151 | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05902 | Verified | On ISO 10-WWT-PD-P40-0150-02 missing cap screws at connection to 10-WWTD-P-0002B/N1 suct | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05903 | Verified | ISO 10-WWT-PD-P40-0155-01 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05904 | Verified | On ISO 10-WWT-PD-P40-0160-01 on valve 10-WWT-AOV-0013B missing valve handle | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-09-26 | Damon Turner | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05905 | Verified | On ISO 10-WWT-PD-P40-0160-01 on valve 10-WWT-AOV-0013B missing cap screws | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05906 | Verified | On ISO 10-WWT-PD-P40-0160-01 on valve 10-WWT-V-0017B missing cap screws | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05907 | Verified | On ISO 10-WWT-PD-P40-0160-01 on valve 10-WWT-V-0026 missing cap screws | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05908 | Verified | On ISO 10-WWT-PD-P40-0160-01 on valve 10-WWT-CHK-0006B missing botls | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05909 | Verified | On ISO 10-WWT-PD-P40-0160-01 missing bolts at 10-WWT-EJ-0160 | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05910 | Verified | On ISO 10-WWT-PD-P40-0160-01 missing bolts at connection to 10-WWT-P-0002B/N2 dis | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05911 | Verified | On ISO 10-WWT-PD-P40-0160-02 missing gasket and bolts at connection to 10-WWT-T-0001-B/A2 | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05912 | Verified | On ISO 10-WWT-PD-P40-0160-02 pipe support 10-WWT-PD-HGR-0010 has no clamp | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05913 | Verified | On ISO 10-WWT-PD-P40-0160-02 pipe support 10-WWT-PD-HGR-0009 has no clamp and ss wrap | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05914 | Verified | On ISO 10-WWT-PD-P40-0160-02 no gasket and missing bolts on 10-WWT-MXR-00118 | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-29 | James Beech | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05915 | Verified | On ISO 10-WWT-PD-P40-0160-02 missing isolation kit and missing bolts on 10-WWT-MXR-00119 | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05916 | Verified | On ISO 10-WWT-PD-P40-0160-02 missing bolts at 10-WWT-FO-0018 and needs a second gasket | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05917 | Verified | On ISO 10-WWT-PD-P40-0160-02 instrument 10-WWT-FO-0019 is not installed | B | P | William Mitchell | McD | 2019-09-13 | William Mitchell | Const | 2019-12-10 | William Mitchell | 2019-12-10 | J.L. Bickham
WWT-01 | WWT-01 | PI05918 | Verified | On ISO 10-WWT-PD-P40-0160-02 missing cap screws at 10-WWT-AOV-0013B | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05919 | Verified | On 10-WWT-PD-P40-0165-01 pipe support 10-WWT-PD-HGR-0016 has no clamps and no ss wrap | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05920 | Verified | On 10-WWT-PD-P41-0165-01 missing cap screws and no gasket installed at 10-WWT-AOV-0014B | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05921 | Verified | On ISO 10-WWT-PD-P40-0165-02 pipe support 10-WWT-PD-HGR-0020 has no clamp | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05922 | Verified | On ISO 10-WWT-PD-P40-0165-02 missing cap screws and no gasket installed on 10-WWT-AOV-HGR-0014A | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05923 | Verified | On ISO 10-WWT-PD-P40-0165-03 missing cap screw and no gasket installed on 10-WWT-AOV-14B | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05924 | Verified | On ISO 10-WWT-PD-P40-0165-03 pipe support 10-WWT-PD-HGR-0018 has no clamps | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05925 | Verified | On ISO 10-WWT-PD-P40-0165-03 missing cap screws and no gasket installed at connection to 10-WWT-AOV-0014A | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05926 | Verified | On ISO 10-WWT-PD-P40-0165-03 missing bolts to connection to 10-WWT-FE-0015 & needs another gasket | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05927 | Verified | On ISO 10-WWT-PD-P40-0165-04 instrument 10-WWT-FE-0015 is not installed | B | P | William Mitchell | McD | 2019-09-13 | William Mitchell | Const | 2019-12-10 | William Mitchell | 2019-12-10 | J.L. Bickham
WWT-01 | WWT-01 | PI05928 | Verified | On ISO 10-WWT-PD-P40-0165-04 instrument 10-WWT-AE-0012 is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-10-16 | Gonzalo Pena | 2019-10-19 | Kelvin Cook
WWT-01 | WWT-01 | PI05929 | Verified | On ISO 10-WWT-PD-P40-0165-04 valve 10-WWT-V-0010 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05930 | Verified | On ISO 10-WWT-PD-P40-0165-04 rework spool 0165-1 due to sloping issue ( to high) should fix gap at HGR 21 | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05931 | Verified | On ISO 10-WWT-PD-P40-0165-04 missing bolts at connection to UG | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05932 | Verified | On ISO 10-WWT-PD-P40-0170-01 missing cap screws at 10-WWT-AOV-0013A | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05933 | Verified | On ISO 10-WWT-PD-P40-0170-01 missing cap screws at 10-WWT-V-0026 | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05934 | Verified | On ISO 10-WWT-PD-P40-0170-01 missing cap screws at 10-WWT-V-0017A | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-23 | James Beech | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05935 | Verified | On ISO 10-WWT-PD-P40-0170-01 missing valve handle at 10-WWT-V-0017A | A | P | James Beech | McD | 2019-09-13 | James Beech | Const |  |  | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05936 | Verified | On ISO 10-WWT-PD-P40-0170-01 missing bolts at 10-WWT-CHK-0006A | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05937 | Verified | On ISO 10-WWT-PD-P40-0170-01 missing bolts at 10-WWT-EJ-0170 | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05938 | Verified | On ISO 10-WWT-PD-P40-0170-01 missing bolts at connection to 10-WWT-P-0002A/N2 disc | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05939 | Verified | On ISO 10-WWT-PD-P40-0170-01 pipe support 10-WWT-PD-HGr-0019 has no ss wrap and no clamp | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05940 | Verified | On ISO 10-WWT-PD-P40-0170-02 missing gasket and bolts at connection to 10-WWT-T-0001-A/A2 | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05941 | Verified | On ISO 10-WWT-PD-P40-0170-02 pipe support 10-WWT-PD-HGR-0022 has no ss wrap and clamp | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05942 | Verified | On ISO 10-WWT-PD-P40-0170-02 no isolation kit and missing bolts at connection to 10-WWT-MXR-0011A | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05943 | Verified | On ISO 10-WWT-PD-P40-0170-02 missing cap screws at connection to 10-WWT-AOV-0013A | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05944 | Verified | On 10-WWT-PD-P40-0185-01 missing cap screws at connection to 10-WWT-AOV-0011B | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05945 | Verified | On ISO 10-WWT-PD-P40-0185-02 missing bolts and missing gasket to connection to 10-WWT-T-0001-B/A1 | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05946 | Verified | On ISO 10-WWT-PD-P40-0185-02 pipe support 10-WWT-PD-HGR-0004 missing clamps | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05947 | Verified | On ISO 10-WWT-PD-P40-0185-02 missing cap screws to connection to 10-WWT-AOV-0011B | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05948 | Verified | ISO 10-WWT-PD-P40-0190-01 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05949 | Verified | ISO 10-WWT-PD-P40-0190-02 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-26 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05950 | Verified | On ISO 10-WWT-PD-P41-0016-01 install iso per detail | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05951 | Verified | On ISO 10-WWT-PD-P41-0017-01 install iso per detail | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05952 | Verified | On ISO 10-WWT-PD-P41-0110-01 valve 10-WWT-V-0002A is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05953 | Verified | On ISO 10-WWT-PD-P41-0110-01 Instrument 10-WWT-PI-0002A is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
WWT-01 | WWT-01 | PI05954 | Verified | ISO 10-WWT-PD-P41-0110-02 is not installed | B | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-19 | Kelvin Cook
WWT-01 | WWT-01 | PI05955 | Verified | On ISO 10-WWT-PD-P41-0115-01 valve 10-WWT-V-0002B is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05956 | Verified | On ISO 10-WWT-PD-P41-0115-01 Instrument 10-WWT-PI-0002B is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
WWT-01 | WWT-01 | PI05957 | Verified | ISO 10-WWT-PD-P41-0115-02 is not installed | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-19 | Kelvin Cook
WWT-01 | WWT-01 | PI05958 | Verified | On ISO 10-WWT-PD-P41-0140-01 Instrument 10-WWT-PI-0009A is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
WWT-01 | WWT-01 | PI05959 | Verified | On ISO 10-WWT-PD-P41-0140-02 valve 10-WWT-V-0005A is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05960 | Verified | On ISO 10-WWT-PD-P41-0140-01 Instrument 10-WWT-PDIT-0005A is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05961 | Verified | On ISO 10-WWT-PD-P41-0140-03 Instrument 10-WWT-PDIT-0005B is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05962 | Verified | On ISO 10-WWT-PD-P41-0140-03 valve 10-WWT-V-0005A2 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05963 | Verified | ISO 10-WWT-PD-P41-0140-04 is not installed | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-15 | James Beech | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05964 | Verified | ISO 10-WWT-PD-P41-0140-05 is not installed | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-19 | Kelvin Cook
WWT-01 | WWT-01 | PI05965 | Verified | ISO 10-WWT-PD-P41-0150-01 rotate valve handle for operator friendly | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05966 | Verified | On ISO 10-WWT-PD-P41-0150-01 Instrument 10-WWT-PI-0009B is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
WWT-01 | WWT-01 | PI05967 | Verified | ISO 10-WWT-PD-P41-0150-02 Instrument 10-WWT-PDIT-0005B is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05968 | Verified | On ISO 10-WWT-PD-P41-0150-02 valve 10-WWT-V-0005A1 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05969 | Verified | On ISO 10-WWT-PD-P41-0150-03 Instrument 10-WWT-PDIT-0005A is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05970 | Verified | On ISO 10-WWT-PD-P41-0150-03 valve 10-WWT-V-0005A2 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05971 | Verified | ISO 10-WWT-PD-P41-0150-04 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05972 | Verified | ISO 10-WWT-PD-P41-0150-05 is not installed | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-19 | Kelvin Cook
WWT-01 | WWT-01 | PI05973 | Verified | On ISO 10-WWT-PD-P41-0160-01 rotate valve 10-WWT-V-00188 | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05974 | Verified | On ISO 10-WWT-PD-P41-0160-02 threaded cap is not installed | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-19 | Kelvin Cook
WWT-01 | WWT-01 | PI05975 | Verified | ISO 10-WWT-PD-P41-0160-03 rotate valve handle for operator friedly 10-WWT-V-0010B | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05976 | Verified | ISO 10-WWT-PD-P41-0160-03 Instrument 10-WWT-PI-0010B is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
WWT-01 | WWT-01 | PI05977 | Verified | ISO 10-WWT-PD-P41-0160-04 is not installed | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-19 | Kelvin Cook
WWT-01 | WWT-01 | PI05978 | Verified | On ISO 10-WWT-PD-P41-0160-05 valve 10-WWT-V-001982 is not installed | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-19 | Kelvin Cook
WWT-01 | WWT-01 | PI05979 | Verified | On ISO 10-WWT-PD-P41-0160-05 10-WWT-FP-0001B is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05980 | Verified | On ISO 10-WWT-PD-P41-0160-06 specialty item 10-WWT-QUIL-0001B Is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const |  |  | 2019-09-18 | Kelvin Cook
WWT-01 | WWT-01 | PI05981 | Verified | On ISO 10-WWT-PD-P41-0160-06 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05982 | Verified | ISO 10-WWT-PD-P41-0165-01 is not installed | B | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-19 | Kelvin Cook
WWT-01 | WWT-01 | PI05983 | Verified | ISO 10-WWT-PD-P41-0165-02 is not installed pipe needs to be reworked | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05984 | Verified | ISO 10-WWT-PD-P41-0165-03 is not installed pipe needs to be reworked | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-19 | Kelvin Cook
WWT-01 | WWT-01 | PI05985 | Verified | ISO 10-WWT-PD-P41-0170-01 rotate handle 10-WWT-V-0018A for operator friendly | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05986 | Verified | ISO 10-WWT-PD-P41-0170-02 threaded cap is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05987 | Verified | ISO 10-WWT-PD-P41-0170-03 instrument 10-WWT-PI-0010A is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-09-18 | Kelvin Cook
WWT-01 | WWT-01 | PI05988 | Verified | ISO 10-WWT-PD-P41-0170-04 instrument 10-WWT-FP-0010A is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05989 | Verified | ISO 10-WWT-PD-P41-0170-04 instrument 10-WWT-FP-0010A is not installed | A | I | Gonzalo Pena | McD | 2019-09-13 | Gonzalo Pena | Const | 2019-09-16 | Gonzalo Pena | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05990 | Verified | ISO 10-WWT-PD-P41-0170-05 is not installed | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-10-19 | Kelvin Cook
WWT-01 | WWT-01 | PI05991 | Verified | ISO 10-WWT-PD-P41-0170-06 is not installed | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-15 | James Beech | 2019-10-19 | Kelvin Cook
WWT-01 | WWT-01 | PI05992 | Verified | ISO 10-WWT-PD-P41-0171-01 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05993 | Verified | ISO 10-WWT-PD-P41-0171-02 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05994 | Verified | ISO 10-WWT-PD-P41-0171-03 is not installed | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI05995 | Verified | ISO 10-WWT-PD-P41-0172-01 on spool 172-2 missing ss wrap and clamps | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05996 | Verified | On ISO 10-WWT-PD-P41-0172-02 on spool 0172-2 install tie wraps every 6" | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05997 | Verified | On ISO 10-WWT-PD-P41-0172-02 spool 0172-1 after wall penetration no ss wrap and no clamps | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05998 | Verified | On ISO 10-WWT-PD-P41-0172-02 spool 0172-4 missing clamps | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI05999 | Verified | ISO 10-WWT-PD-P41-0172-04 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI06000 | Verified | On ISO 10-WWT-PD-P41-0175-01 missing clamps & unistrut | B | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI06001 | Verified | On ISO 10-WWT-PD-P41-0175-01 low point in pipe adjust support in vent to make level | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI06002 | Verified | On ISO 10-WWT-PD-P41-0175-01 missing ss wrap and clamps | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI06003 | Verified | On ISO 10-WWT-PD-P41-0175-01 support is out square. & cold galve | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI06004 | Verified | On ISO 10-WWT-PD-P41-0175-02 low point adjust pipe | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI06005 | Verified | ISO 10-WWT-PD-P41-0175-03 is not installed | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI06006 | Verified | On ISO 10-WWT-PD-P41-0176-01 on spool 0176-2 no ss wrap and no clamps | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI06007 | Verified | On ISO 10-WWT-PD-P41-0176-02 spool 0176-2 way out of plumb rework to correct | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI06008 | Verified | On ISO 10-WWT-PD-P41-0176-02 spool 0176-3 install tie wire every 6" | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-10-04 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI06009 | Verified | On ISO 10-WWT-PD-P41-0176-02 spool 0176-1 just after wall penetration no ss wrap and no clamps | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI06010 | Verified | On ISO 10-WWT-PD-P41-0176-02 spool 0176-4 fix ss wrap ( thickten up) and I clamp missing | B | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI06011 | Verified | On ISO 10-WWT-PD-P41-0176-03 spool 0176-1 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI06012 | Verified | ISO 10-WWT-PD-P41-0176-04 is not installed | A | P | Damon Turner | McD | 2019-09-13 | Damon Turner | Const | 2019-09-27 | Damon Turner | 2019-10-05 | Kelvin Cook
WWT-01 | WWT-01 | PI06013 | Verified | 10WWTX0005, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06014 | Verified | 10WWTX0006, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06015 | Verified | 10WWTX0007, From Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06016 | Verified | 10WWTK0002, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06017 | Verified | 10WWTX0001, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06018 | Verified | 10WWTX0005, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06019 | Verified | 10WWTX0006, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06020 | Verified | 10WWTX0007, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06021 | Verified | 10WWTX0008, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06022 | Verified | 10WWTX0009, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06023 | Verified | 10WWTX0010, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06024 | Verified | 10WWTX0012, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06025 | Verified | 10WWTX0013, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06026 | Verified | 10WWTX0014, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06027 | Verified | 10WWTX0015, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06028 | Verified | 10WWTX0016, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06029 | Verified | 10WWTX0017, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06030 | Verified | 10WWTX0018, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06031 | Verified | 10WWTX0019, To Termination | A | E | Dustin Futrell | McD | 2019-09-13 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-28 | Mike Tabbert
WWT-01 | WWT-01 | PI06215 | Verified | WWT-P-0001A, install permanent heater wiring. | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Shannon Scott
WWT-01 | WWT-01 | PI06216 | Verified | WWT-P-0001B, install permanent heater wiring. | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-09-23 | Dustin Futrell | 2019-09-25 | Shannon Scott
WWT-01 | WWT-01 | PI06217 | Verified | Install pipe wrapper and bands at pipe support 10-WWT-PD-HRG-0001 | C | P | James Beech | McD | 2019-09-16 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-11-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06218 | Verified | Complete wiring Valve WWT-AOV-0011A | A | E | Dustin Futrell | McD | 2019-09-16 | Dustin Futrell | Const | 2019-10-17 | Dustin Futrell | 2019-11-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06219 | Verified | Install instrument air WWT-AOV-0011A | A | P | James Beech | McD | 2019-09-16 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-11-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06220 | Verified | Repair containment sump coating. | B | C | Sheri Fritz | BRA | 2019-09-16 | Sheri Fritz | Const | 2019-12-10 | William Mitchell | 2019-12-10 | J.L. Bickham
WWT-01 | WWT-01 | PI06221 | Verified | 10-WWT-V-0008A Valve not installed | A | P | James Beech | McD | 2019-09-16 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-11-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06222 | Verified | 10-WWT-V-0028A Valve not installed | A | P | James Beech | McD | 2019-09-16 | James Beech | Const | 2019-10-30 | James Beech | 2019-11-19 | Shannon Scott
WWT-01 | WWT-01 | PI06223 | Verified | 10-WWT-V-0016A Valve not installed | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-09-25 | Shannon Scott
WWT-01 | WWT-01 | PI06224 | Verified | 10-WWT-V-0026 Valve handle missing. | A | P | James Beech | McD | 2019-09-16 | James Beech | Const | 2019-11-04 | Kelvin Cook | 2019-11-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06225 | Verified | 10-WWT-PIT-0018B Clean out instrument enclosure | B | I | Gonzalo Pena | McD | 2019-09-16 | Gonzalo Pena | Const | 2019-09-27 | Gonzalo Pena | 2019-10-03 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06226 | Verified | 10-WWT-V-0016B Valve not installed | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const | 2019-09-25 | Damon Turner | 2019-09-25 | Shannon Scott
WWT-01 | WWT-01 | PI06227 | Verified | 10-WWT-V-0028B Valve not installed | A | P | James Beech | McD | 2019-09-16 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-11-19 | Shannon Scott
WWT-01 | WWT-01 | PI06228 | Verified | 10-WWT-V-0005B2 Valve not installed | B | P | James Beech | McD | 2019-09-16 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-11-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06229 | Verified | 10-WWT-STN-0005B - Needs rust removed and coated | C | P | Jorge Alexander | McD | 2019-09-16 | Jorge Alexander | Const | 2020-01-28 | Jorge Alexander | 2020-02-10 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06230 | Verified | 10-WWT-AOV-0013B Valve not accessible | D | P | Michael Law | McD | 2019-09-16 | Michael Law | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
WWT-01 | WWT-01 | PI06231 | Verified | 10-WWT-V-0019B1 wrong valve type used | D | P | James Beech | McD | 2019-09-16 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-11-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06232 | Verified | 10-WWT-FO-0001B FO not accessible | D | P | Michael Law | McD | 2019-09-16 | Michael Law | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
WWT-01 | WWT-01 | PI06233 | Verified | 10-WWT-V-0020B Valve not installed | D | P | Michael Law | McD | 2019-09-16 | Michael Law | Const | 2019-12-05 | Kelvin Cook | 2020-01-03 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06234 | Verified | 10-WWT-QUIL-0002B Quil not accessible | D | P | Michael Law | McD | 2019-09-16 | Michael Law | Const | 2020-05-11 | Michael Law | 2020-07-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06235 | Verified | 10-WWT-V-0021 Valve, verify weld to main pipe (undercut) | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const | 2019-09-30 | Tom Noble | 2019-09-30 | Tom Noble
WWT-01 | WWT-01 | PI06236 | Verified | 10-WWT-V-0015A wrong valve type used | A | P | James Beech | McD | 2019-09-16 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-11-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06237 | Verified | 10-WWT-QUIL-0002A Quil not accessible | D | P | Michael Law | McD | 2019-09-16 | Michael Law | Const | 2020-05-11 | Michael Law | 2020-07-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06238 | Verified | 10-WWT-FO-0001A FO not accessible | D | P | Michael Law | McD | 2019-09-16 | Michael Law | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
WWT-01 | WWT-01 | PI06239 | Verified | 10-WWT-FP-0001A FP not installed | A | P | Damon Turner | McD | 2019-09-16 | Damon Turner | Const | 2019-09-26 | Gonzalo Pena | 2019-10-03 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06240 | Verified | 10-WWT-V-0020A Valve not installed | A | P | James Beech | McD | 2019-09-16 | James Beech | Const | 2019-10-04 | Damon Turner | 2019-11-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06241 | Verified | 10-WWT-V-0019A1 wrong valve type installed | A | P | James Beech | McD | 2019-09-16 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-11-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06242 | Verified | 10-WWT-V-0019A2 wrong valve type installed | A | P | James Beech | McD | 2019-09-16 | James Beech | Const | 2019-10-09 | Damon Turner | 2019-11-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI06243 | Verified | Verify 10-WWT-T-001A & 1B nameplates are on correct tanks. | B | M | Shane Crowe | McD | 2019-09-16 | Shane Crowe | Const | 2019-09-27 | Gonzalo Pena | 2019-10-03 | Nelson Eichelberger
WWT-01 | WWT-01 | PI09170 | Verified | 10-WWT-AIT-0008A and B both covers are broken due to over tightening need to replace | B | I | Mike Tabbert | McD | 2019-10-07 | Mike Tabbert | Const |  |  | 2020-01-22 | Albert Burge
WWT-01 | WWT-01 | PI09719 | Verified | Add support for stilling well for level transmitter 10-WWT-LIT-0001. | B | P | Michael Law | McD | 2019-10-17 | Michael Law | Const | 2020-02-27 | Michael Law | 2020-03-09 | Michael Law
WWT-01 | WWT-01 | PI09835 | Verified | Test Package WWT-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI09836 | Verified | Test Package WWT-T-02 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI09837 | Verified | Test PackageWWT-T-03 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI09838 | Verified | Test Package WWT-T-04 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-08 | Kelvin Cook
WWT-01 | WWT-01 | PI09839 | Verified | Test Package WWT-T-05 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-07 | Kelvin Cook
WWT-01 | WWT-01 | PI09840 | Verified | Test Package WWT-T-07 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-11-04 | Kelvin Cook
WWT-01 | WWT-01 | PI10254 | Verified | Valve 10-WWT-V-0026 not accessible. | D | P | Michael Law | McD | 2019-10-24 | Michael Law | Const | 2020-05-11 | Michael Law | 2020-07-07 | Nelson Eichelberger
WWT-01 | WWT-01 | PI12600 | Verified | Complete installation of strainer basket. | B | M | William Mitchell | McD | 2019-10-29 | William Mitchell | Const | 2019-12-10 | William Mitchell | 2019-12-10 | J.L. Bickham
WWT-01 | WWT-01 | PI12601 | Verified | 10-WWT-P-0002B - Suction pipe on downstream side of strainer needs repair, major fish mouth. | A | P | James Beech | McD | 2019-10-29 | James Beech | Const | 2019-11-04 | Kelvin Cook | 2019-12-09 | J.L. Bickham
WWT-01 | WWT-01 | PI12602 | Verified | Batch Neutralization Tanks A&B - Flange on top of tank is wire tied on, no bolts. | A | P | James Beech | McD | 2019-10-29 | James Beech | Const | 2019-11-04 | Kelvin Cook | 2019-12-09 | J.L. Bickham
WWT-01 | WWT-01 | PI12603 | Verified | 10-WWT-P-0001A & B - Pumps missing coupling guard. | A | M | Shane Crowe | McD | 2019-10-29 | Shane Crowe | Const | 2019-11-04 | Joshua Sturgeon | 2019-12-09 | J.L. Bickham
WWT-01 | WWT-01 | PI12604 | Verified | Overflow pipe from neutralization tanks to sump have argon hose stuck in pipe. | A | P | James Beech | McD | 2019-10-29 | James Beech | Const | 2019-11-04 | Kelvin Cook | 2019-12-09 | J.L. Bickham
WWT-01 | WWT-01 | PI12605 | Verified | Probe 10-WWT-AE-0012 - wire not terminated. | A | E | Dustin Futrell | McD | 2019-10-29 | Dustin Futrell | Const | 2019-11-07 | Dustin Futrell | 2019-11-21 | Albert Burge
WWT-01 | WWT-01 | PI12606 | Verified | WWT discharge - Sample port on common discharge not installed as needed for permit. | A | P | James Beech | McD | 2019-10-29 | James Beech | Const | 2019-11-04 | Kelvin Cook | 2019-12-09 | J.L. Bickham
WWT-01 | WWT-01 | PI12607 | Verified | Final discharge pipe to discharge ditch has blank flange on pipe end. Remove flange. | A | P | James Beech | McD | 2019-10-29 | James Beech | Const | 2019-11-06 | James Beech | 2019-12-09 | J.L. Bickham
WWT-01 | WWT-01 | PI12608 | Verified | Repair coating in containment. | C | C | Sheri Fritz | BRA | 2019-10-29 | Sheri Fritz | Const | 2020-04-28 | Johnny Campbell | 2020-04-28 | Michael Law
WWT-01 | WWT-01 | PI12857 | Verified | Provide static head test for Batch Neut. Tanks A & B. | B | M | William Mitchell | McD | 2019-11-09 | William Mitchell | Const | 2019-12-10 | William Mitchell | 2019-12-10 | J.L. Bickham
WWT-01 | WWT-01 | PI15576 | Verified | 10-WWT-P-0003A/B, 10-WWT-P-0004A/B - The tie-ins circled in red on the Tie-Ins Picture haven’t been installed in the field. Without the tie-ins, A Caustic Pump only pumps to BNS A Tank. If A Caustic Pump were to fail and BNS A Tank has low pH, we would not be able to raise the pH in A Tank. This applies to both acid and caustic for both A and B tank. | C | P | Tim Green | McD | 2020-01-08 | Tim Green | Const | 2020-09-15 | Jason Ezell | 2021-01-05 | Keith Pollock
WWT-01 | WWT-01 | PI15624 | Verified | 10-WWT-P-0003A; WWT Sulfuric Acid Pump A trips after 2 minute run time, gets a "Fail to Start" error at DCS, when pump is reset locally and at DCS it can be restarted, possible problem with timer, needs to be evaluated | B | I | James Wooley | McD | 2020-01-08 | James Wooley | Comm |  |  | 2020-01-23 | Shannon Scott
WWT-01 | WWT-01 | PI15625 | Verified | Install uni-strut end caps throughout WWT-01 System | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-04-28 | Matt Gilmore | 2020-07-10 | Dave Goldak
WWT-01 | WWT-01 | PI15626 | Verified | Clean up WWT Sulfuric Acid Pump Skid | C | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Comm | 2020-03-13 | Johnny Campbell | 2020-04-07 | Bernard Stasse
WWT-01 | WWT-01 | PI15627 | Verified | Terminate or remove unused cable to 10-WWT-CP-0003; Sulfuric Acid Control Panel | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2021-01-15 | Dave Goldak
WWT-01 | WWT-01 | PI15628 | Verified | Conduit to 10-WWT-CP-0003; Sulfuric Acid Control Panel missing condolet covers | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-04-21 | Matt Gilmore | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15629 | Verified | Clean up top of 10-WWT-CP-0003; Sulfuric Acid Control Panel | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-07 | Bernard Stasse
WWT-01 | WWT-01 | PI15630 | Verified | 10-WWT-V-0172; Sulfuric Acid Drain Header Drain Valve needs to be threaded and plug installed | C | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-07-20 | Jason Ezell | 2020-11-11 | Dave Goldak
WWT-01 | WWT-01 | PI15631 | Verified | 10-WWT-V-0176; Sulfuric Acid Drain Header Drain Valve needs to be threaded and plug installed | C | P | Tim Green | McD | 2020-01-08 | Tim Green | Comm | 2020-07-24 | Jason Ezell | 2020-11-11 | Dave Goldak
WWT-01 | WWT-01 | PI15632 | Verified | Need support under flex connection to WWT Sulfuric Acid Chemical Tote | C | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15633 | Verified | Install drain from 10-WWT-LSL-0016; Sulfuric Acid Level Switch vent to sump | D | P | Michael Law | McD | 2020-01-08 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-06-17 | John Watts
WWT-01 | WWT-01 | PI15634 | Verified | Install drain from Sulfuric Acid Calibration Column to sump | D | P | Michael Law | McD | 2020-01-08 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-06-17 | John Watts
WWT-01 | WWT-01 | PI15635 | Verified | Replace all Sulfuric Acid Skid plastic flex connections with metal connections | D | E | Michael Law | McD | 2020-01-08 | Michael Law | Comm | 2020-04-06 | Michael Law | 2020-04-07 | Bernard Stasse
WWT-01 | WWT-01 | PI15636 | Verified | Reroute Sulfuric Acid Skid frame ground cable under skid frame, east and west side, currently routed over top | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-05-04 | Matt Gilmore | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15637 | Verified | Reroute Caustic Skid frame ground cable under skid frame, east and west side, currently routed over top | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-05-04 | Matt Gilmore | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15638 | Verified | Shorten Caustic Skid frame anchor bolts | C | M | Shane Crowe | McD | 2020-01-08 | Shane Crowe | Comm | 2020-01-15 | Shane Crowe | 2020-01-20 | Shannon Scott
WWT-01 | WWT-01 | PI15639 | Verified | Clean up Caustic Skid | C | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Comm | 2020-03-13 | Johnny Campbell | 2020-04-06 | Bernard Stasse
WWT-01 | WWT-01 | PI15640 | Verified | Determine if level indicator is necessary for Caustic Chemical Tote | D | P | Kevin Leppert | McD | 2020-01-08 | Kevin Leppert | Comm | 2020-01-31 | Michael Law | 2020-02-19 | Keith Pollock
WWT-01 | WWT-01 | PI15641 | Verified | Panel door at 10-WWT-CP-0004; Caustic Control Panel needs hinge pin and top hinge | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-04-29 | Matt Gilmore | 2020-08-10 | Nelson Eichelberger
WWT-01 | WWT-01 | PI15642 | Verified | Need support under flex connection to Caustic Chemical Tote | C | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15643 | Cleared | Install drain from 10-WWT-LSL-0017; Caustic Level Switch vent to sump | D | P | Michael Law | McD | 2020-01-08 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-07-22 | John Watts
WWT-01 | WWT-01 | PI15644 | Verified | Install drain from Caustic Calibration Column to sump | D | P | Michael Law | McD | 2020-01-08 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-06-17 | John Watts
WWT-01 | WWT-01 | PI15645 | Verified | Seal chemical injection piping penetrations at NW side of Demin Water Bldg | C | C | Tim Gallegos | McD | 2020-01-08 | Tim Gallegos | Comm | 2020-03-30 | Bobby Williams | 2020-04-07 | Bernard Stasse
WWT-01 | WWT-01 | PI15646 | Verified | Need additional uni-strut/u-bolt support between 1.5" Caustic chemical injection lines, upstream of drain valves 10-WWT-V-0171 and 10-WWT-V-0175, at horizontal just past first 90, inside Demin Water Bldg at skid | C | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15647 | Verified | Remove temporary tie-wrap from Caustic chemical injection line and replace with permanent clamp, at first horizontal pipe support upstream of drain valves 10-WWT-V-0171 and 10-WWT-V-0175, inside Demin Water Bldg at skid | C | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15648 | Verified | Both 1.5" Caustic chemical injection lines are rubbing against each other, separate with uni-strut/u-bolts between vertical sections, near building penetration, NW side Demin Water Bldg | C | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15649 | Verified | Need additional support for Acid chemical injection Line no. 0.75-10-WWT-0172, horizontal section just upstream of tie-in to SS 10" to Batch Neutralization Tank A | C | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15650 | Verified | Need additional tie-wraps for Acid and Caustic chemical injection piping at horizontal tray support, from Demin Water Bldg to Batch Neutralization Tank Containment | C | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-05-07 | James Beech | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15651 | Verified | Seal all concrete joints at Batch Neutralization Containment wall | C | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Comm | 2020-01-20 | Alan Huntsman | 2020-02-02 | Shannon Scott
WWT-01 | WWT-01 | PI15652 | Verified | Remove all wire, tape, rope, and old temporary tags from WWT-01 System components | C | C | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-01-13 | Tim Green | 2020-02-02 | Shannon Scott
WWT-01 | WWT-01 | PI15653 | Verified | Shorten all I-Beam support baseplate anchor bolts inside Batch Neutralization Containment | C | M | Shane Crowe | McD | 2020-01-08 | Shane Crowe | Comm | 2020-01-15 | Shane Crowe | 2020-01-20 | Shannon Scott
WWT-01 | WWT-01 | PI15654 | Verified | Check all I-Beam support baseplate anchor bolt nuts for tightnes inside Batch Neutralization Containment | C | M | Shane Crowe | McD | 2020-01-08 | Shane Crowe | Comm | 2020-01-15 | Shane Crowe | 2020-01-20 | Shannon Scott
WWT-01 | WWT-01 | PI15655 | Verified | Install washers in man-way covers at Batch Neutralization Tank A & B | C | M | Shane Crowe | McD | 2020-01-08 | Shane Crowe | Comm | 2020-01-15 | Shane Crowe | 2020-01-20 | Shannon Scott
WWT-01 | WWT-01 | PI15656 | Verified | Remove unused bolt from horizontal chemical injection piping support at S side of Batch Neutralization Containment | C | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-01-16 | Bobby Williams | 2020-01-20 | Shannon Scott
WWT-01 | WWT-01 | PI15657 | Verified | Need to inspect and repair Batch Neutralization Containment coating as necessary, numerous areas of exposed concrete exist | C | C | Sheri Fritz | BRA | 2020-01-08 | Sheri Fritz | Comm | 2020-04-28 | Johnny Campbell | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15658 | Verified | Remove and plug unused conduit connector at 10-WWT-LIT-0007B; Batch Neutralization Tank B Level Transmitter | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-05-04 | Matt Gilmore | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15659 | Verified | 10-WWT-V-0027B; LIT Isolation Valve cannot open fully, valve handle hard against 10-WWT-LIT-0007B | B | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-01-17 | Tim Green | 2020-01-20 | Shannon Scott
WWT-01 | WWT-01 | PI15660 | Verified | Cable not terminated to 10-WWT-AIT-0008B; Batch Neutralization Tank B Analysis Indicating Transmitter | B | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-01-28 | Jared Stimpson | 2020-02-02 | Shannon Scott
WWT-01 | WWT-01 | PI15661 | Verified | 10-WWT-AIT-0008B; Batch Neutralization Tank B Analysis Indicating Transmitter probe is broken | B | I | Albert Burge | McD | 2020-01-08 | Albert Burge | Comm | 2020-01-16 | Albert Burge | 2020-01-16 | Albert Burge
WWT-01 | WWT-01 | PI15662 | Verified | Tighten Batch Neutralization Tank A hold down anchor nut, W side of tank | C | M | Shane Crowe | McD | 2020-01-08 | Shane Crowe | Comm | 2020-01-15 | Shane Crowe | 2020-01-20 | Shannon Scott
WWT-01 | WWT-01 | PI15663 | Verified | 10-WWT-V-0027A; LIT Isolation Valve cannot open fully, valve handle hard against 10-WWT-LIT-0007A | B | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-01-17 | Tim Green | 2020-01-20 | Shannon Scott
WWT-01 | WWT-01 | PI15664 | Verified | Secure cable to 10-WWT-LIT-0007A; Batch Neutralization Tank B Level Transmitter | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-05-04 | Matt Gilmore | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15665 | Verified | Entergy replaced 10-WWT-AIT-0008A; Batch Neutralization Tank B Analysis Indicating Transmitter, McDermott to reimburse | D | P | Michael Law | McD | 2020-01-08 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
WWT-01 | WWT-01 | PI15666 | Verified | Install missing anchor screws for Batch Neutralization Tank nameplate | C | M | Shane Crowe | McD | 2020-01-08 | Shane Crowe | Comm | 2020-01-15 | Shane Crowe | 2020-01-20 | Shannon Scott
WWT-01 | WWT-01 | PI15667 | Verified | Clean off rust and paint 10-WWT-STN-0005B; WWT Pump Suction Strainer B | C | C | Jorge Alexander | McD | 2020-01-08 | Jorge Alexander | Comm | 2020-01-28 | Jorge Alexander | 2020-02-02 | Shannon Scott
WWT-01 | WWT-01 | PI15668 | Verified | Need cap at WWT Recirc /Forwarding Pump Pump B casing drain, Line No. 0.5-10-WWT-0017 | C | M | Shane Crowe | McD | 2020-01-08 | Shane Crowe | Comm | 2020-03-19 | Shane Crowe | 2020-04-07 | Bernard Stasse
WWT-01 | WWT-01 | PI15669 | Verified | Clean up WWT Recirc/Forwarding Pump A & B containment | C | M | Shane Crowe | McD | 2020-01-08 | Shane Crowe | Comm | 2020-01-15 | Shane Crowe | 2020-01-20 | Shannon Scott
WWT-01 | WWT-01 | PI15670 | Verified | Tighten condolet cover at WWT Recirc/Forwarding Pump B | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-04-29 | Matt Gilmore | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15671 | Verified | Cold gal all rusty supports throughout WWT-01 system | C | X | Johnny Campbell | McD | 2020-01-08 | Johnny Campbell | Comm | 2020-04-21 | Chris Colvin | 2020-04-24 | Mark Williamson
WWT-01 | WWT-01 | PI15672 | Verified | Need cap at WWT Recirc /Forwarding Pump Pump A casing drain, Line No. 0.5-10-WWT-0016 | C | M | Shane Crowe | McD | 2020-01-08 | Shane Crowe | Comm | 2020-03-19 | Shane Crowe | 2020-04-07 | Bernard Stasse
WWT-01 | WWT-01 | PI15673 | Verified | Need packing gland cover for WWT Recirc/Forwarding Pump A & B | C | M | Shane Crowe | McD | 2020-01-08 | Shane Crowe | Comm | 2020-02-11 | Shane Crowe | 2020-02-17 | Shannon Scott
WWT-01 | WWT-01 | PI15674 | Verified | Tubing needle valve cap is not stainless steel at 10-WWT-PDIT-0005B; WWT Pump Suction Strainer B Pressure Indicating Transmitter, replace cap with stainless | C | I | Gonzalo Pena | McD | 2020-01-08 | Gonzalo Pena | Comm | 2020-01-13 | Gonzalo Pena | 2020-01-20 | Shannon Scott
WWT-01 | WWT-01 | PI15675 | Verified | Seal hole in 10-HTS-CAB-0106; Transmitter Cabinet | C | I | Gonzalo Pena | McD | 2020-01-08 | Gonzalo Pena | Comm | 2020-01-15 | Gonzalo Pena | 2020-02-10 | Shannon Scott
WWT-01 | WWT-01 | PI15676 | Verified | Tighten condolet cover at incoming conduit to 10-HTS-CAB-0106; Transmitter Cabinet | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-07 | Bernard Stasse
WWT-01 | WWT-01 | PI15677 | Verified | Clean up Batch Neutralization Tank Containment | C | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Comm | 2020-01-20 | Alan Huntsman | 2020-02-02 | Shannon Scott
WWT-01 | WWT-01 | PI15678 | Verified | Clean out Batch Neutralization Tank Containment sump | C | C | Alan Huntsman | McD | 2020-01-08 | Alan Huntsman | Comm | 2020-01-20 | Alan Huntsman | 2020-02-02 | Shannon Scott
WWT-01 | WWT-01 | PI15679 | Verified | Clean paint off glass cover at 10-HTS-CAB-0105; Transmitter Cabinet | C | I | Gonzalo Pena | McD | 2020-01-08 | Gonzalo Pena | Comm |  |  | 2020-01-13 | Fred Michael
WWT-01 | WWT-01 | PI15680 | Verified | Flex conduit to 10-WWT-FIT-0015; Flow Indicating Transmitter is broken at connection | B | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-01-28 | Jared Stimpson | 2020-02-02 | Shannon Scott
WWT-01 | WWT-01 | PI15681 | Verified | Line No. 10-10-WWT-0170 needs additional support between10-WWT-V-0017A; Neutralization Tank A Recirc Isolation Valve and 10-WWT-AOV-0013A; Neutralization Tank A Recirc Control Valve | C | P | James Beech | McD | 2020-01-08 | James Beech | Comm | 2020-05-07 | James Beech | 2020-08-10 | Nelson Eichelberger
WWT-01 | WWT-01 | PI15682 | Verified | Clean up loose cable to 10-WWT-AIT-0012; Batch Neutralization Tank A Analysis Indicating Transmitter | C | E | Chris Colvin | McD | 2020-01-08 | Chris Colvin | Comm | 2020-04-29 | Matt Gilmore | 2020-05-12 | Keith Pollock
WWT-01 | WWT-01 | PI15683 | Verified | 10-WWT-AE-0012; Batch Neutralization Tank A Analysis Sensing Element is not working | B | I | Albert Burge | McD | 2020-01-08 | Albert Burge | Comm | 2020-01-16 | Albert Burge | 2020-01-28 | Fred Michael
WWT-01 | WWT-01 | PI15684 | Verified | Need chain wheel operator for 10-WWT-V-0026; Cross Over Isolation Valve, Line no. 10-10-WWT-0160 and 10-10-WWT-0170 | D | P | Michael Law | McD | 2020-01-08 | Michael Law | Comm | 2020-05-11 | Michael Law | 2021-01-05 | Keith Pollock
WWT-01 | WWT-01 | PI15918 | Verified | 10-WWT-FXH-0004 (25% Caustic) & 10-WWT-0003 (Sulfuric Acid) - need supports to relieve stress on tote connections | C | P | James Beech | McD | 2020-01-13 | James Beech | Comm | 2020-05-07 | James Beech | 2020-07-10 | Dave Goldak
WWT-01 | WWT-01 | PI16685 | Verified | 10-WWT-QUIL-0001B - Injection Quill is clogged and causing 'B' pump not to discharge. | B | M | William Mitchell | McD | 2020-02-07 | William Mitchell | Comm | 2020-02-28 | William Mitchell | 2020-02-28 | John Watts
WWT-01 | WWT-01 | PI18139 | Cleared | 10-WWT-AE-0008A, 10-WWT-AE-0008B, 10-WWT-AE-0012 - The pH Probes on both BNS Tanks need to be replaced because neither reads. The pH Probe downstream of Outfall 301 (BNS) does not work. Point is forced to allow discharge. They cannot operate in AUTO and trip the injection pump. This is an environmental concern. | C | I | Albert Burge | McD | 2020-03-20 | Albert Burge | Comm | 2020-05-04 | Albert Burge
YVA-01 | YVA-01 | PI00380 | Verified | Provide all test reports needed for subsystem turnover. | B | E | Sheri Fritz | DAS | 2019-04-02 | Sheri Fritz | Const | 2019-04-22 | Logan Holland | 2019-04-22 | Logan Holland
YVA-01 | YVA-01 | PI00381 | Verified | Install jumpers for transmission line in switchyard 1A. | A | E | Sheri Fritz | DAS | 2019-04-02 | Sheri Fritz | Const | 2019-04-18 | Ayda Chaves | 2019-04-22 | Logan Holland
YVA-01 | YVA-01 | PI00382 | Verified | Seal all conduits for Dashiell components in Switchyard 1A. | B | E | Sheri Fritz | DAS | 2019-04-02 | Sheri Fritz | Const | 2019-04-22 | Logan Holland | 2019-04-22 | Logan Holland
YVA-01 | YVA-01 | PI00383 | Verified | Seal all conduits for McDermott components in Switchyard 1A and the Main PDC. | B | E | Logan Holland | McD | 2019-04-02 | Logan Holland | Const | 2019-06-14 | Logan Holland | 2019-06-14 | Logan Holland
YVA-01 | YVA-01 | PI00384 | Verified | Install fuses in 1A-YVA-CAB-0003 in Switchyard 1A. | B | E | Sheri Fritz | DAS | 2019-04-02 | Sheri Fritz | Const | 2019-04-22 | Logan Holland | 2019-04-22 | Logan Holland
YVA-01 | YVA-01 | PI00385 | Verified | Review / install low point conduit drains at transformer 1A-NQS-GSUT-0001. | B | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-03 | Mike Tabbert | 2019-04-03 | Mike Tabbert
YVA-01 | YVA-01 | PI00388 | Verified | Tag all JBs, cabs. etc. in switchyard 1A. | B | E | Sheri Fritz | DAS | 2019-04-02 | Sheri Fritz | Const | 2019-04-10 | Robert Matthews | 2019-04-22 | Logan Holland
YVA-01 | YVA-01 | PI00389 | Verified | Install earth grounds in 1A-YVA-CAB-0001, panels P1 & P2 in the main PDC. | A | E | Luis Cantu | McD | 2019-04-02 | Luis Cantu | Const | 2019-04-22 | Shannon Savoy | 2019-06-21 | Logan Holland
YVA-01 | YVA-01 | PI00390 | Verified | Complete fence grounding in Unit 1A switchyard. | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-18 | Shannon Savoy | 2019-04-22 | Ayda Chaves
YVA-01 | YVA-01 | PI00391 | Verified | Install fence & gates for Unit 1A switchyard. | A | E | Sheri Fritz | PSC | 2019-04-02 | Sheri Fritz | Const | 2019-04-18 | Ayda Chaves | 2019-04-18 | Ayda Chaves
YVA-01 | YVA-01 | PI00392 | Verified | All cabinets in switchyard and Main PDC to be cleaned after termination completion. | C | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-03 | Mike Tabbert | 2019-04-03 | Mike Tabbert
YVA-01 | YVA-01 | PI00393 | Verified | 10DCSX0229, Terminate Cable | A | E | Sheri Fritz | ITS | 2019-04-02 | Sheri Fritz | Const | 2019-04-08 | Mike Tabbert | 2019-04-08 | Mike Tabbert
YVA-01 | YVA-01 | PI00394 | Verified | 10ZZZK0003, Terminate Cable | A | E | Sheri Fritz | ITS | 2019-04-02 | Sheri Fritz | Const | 2019-04-03 | Mike Tabbert | 2019-04-03 | Mike Tabbert
YVA-01 | YVA-01 | PI00395 | Verified | 10ZZZK0008, Terminate Cable | A | E | Sheri Fritz | ITS | 2019-04-02 | Sheri Fritz | Const | 2019-04-03 | Mike Tabbert | 2019-04-03 | Mike Tabbert
YVA-01 | YVA-01 | PI00396 | Verified | 10ZZZX0009, Terminate Cable | A | E | Sheri Fritz | ITS | 2019-04-02 | Sheri Fritz | Const | 2019-04-03 | Mike Tabbert | 2019-04-03 | Mike Tabbert
YVA-01 | YVA-01 | PI00397 | Verified | 10ZZZX0010, Terminate Cable | A | E | Sheri Fritz | ITS | 2019-04-02 | Sheri Fritz | Const | 2019-04-03 | Mike Tabbert | 2019-04-03 | Mike Tabbert
YVA-01 | YVA-01 | PI00398 | Verified | 1ALANO0001, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-08 | Mike Tabbert | 2019-04-08 | Mike Tabbert
YVA-01 | YVA-01 | PI00399 | Verified | 1ANQSC0087, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-03 | Shannon Savoy | 2019-04-04 | Mike Tabbert
YVA-01 | YVA-01 | PI00400 | Verified | 1ANQSK0014, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-03 | Shannon Savoy | 2019-04-04 | Mike Tabbert
YVA-01 | YVA-01 | PI00401 | Verified | 1AYVAC0029, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-08 | Mike Tabbert | 2019-04-08 | Mike Tabbert
YVA-01 | YVA-01 | PI00402 | Verified | 1AYVAC0037, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-08 | Mike Tabbert | 2019-04-08 | Mike Tabbert
YVA-01 | YVA-01 | PI00403 | Verified | 1AYVAC0044, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-03 | Shannon Savoy | 2019-04-04 | Mike Tabbert
YVA-01 | YVA-01 | PI00405 | Verified | 1AYVAC0110, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-03 | Shannon Savoy | 2019-04-04 | Mike Tabbert
YVA-01 | YVA-01 | PI00406 | Verified | 1AYVAC0119, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-03 | Shannon Savoy | 2019-04-04 | Mike Tabbert
YVA-01 | YVA-01 | PI00407 | Verified | 1AYVAC0120, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-03 | Shannon Savoy | 2019-04-04 | Mike Tabbert
YVA-01 | YVA-01 | PI00408 | Verified | 1AYVAC0130, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-08 | Mike Tabbert | 2019-04-08 | Mike Tabbert
YVA-01 | YVA-01 | PI00409 | Verified | 1AYVAC0133, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-03 | Shannon Savoy | 2019-04-04 | Mike Tabbert
YVA-01 | YVA-01 | PI00410 | Verified | 1AYVAK0008, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-04 | Mike Tabbert | 2019-04-04 | Mike Tabbert
YVA-01 | YVA-01 | PI00411 | Verified | 1AYVAK0012, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-04 | Mike Tabbert | 2019-04-04 | Mike Tabbert
YVA-01 | YVA-01 | PI00412 | Verified | 1AYVAK0013, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-08 | Mike Tabbert | 2019-04-08 | Mike Tabbert
YVA-01 | YVA-01 | PI00413 | Verified | 1AYVAK0014, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-11 | Shannon Savoy | 2019-04-15 | Mike Tabbert
YVA-01 | YVA-01 | PI00414 | Verified | 1AYVAK0015, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-11 | Shannon Savoy | 2019-04-15 | Mike Tabbert
YVA-01 | YVA-01 | PI00415 | Verified | 1AYVAK0020, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-03 | Shannon Savoy | 2019-04-04 | Mike Tabbert
YVA-01 | YVA-01 | PI00416 | Verified | 1AYVAO0144, Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-02 | Shannon Savoy | Const | 2019-04-03 | Shannon Savoy | 2019-04-04 | Mike Tabbert
YVA-01 | YVA-01 | PI00427 | Verified | Check connection bolts for tightness in the GSU 1A TO SOUTH FIRE WALL area. | A | E | Sheri Fritz | NCC | 2019-04-03 | Sheri Fritz | Const | 2019-04-05 | Jason Marshik | 2019-04-05 | Ayda Chaves
YVA-01 | YVA-01 | PI00428 | Verified | Install heaters and conduits/ wiring in the GSU 1A TO SOUTH FIRE WALL area. | A | E | Shannon Savoy | McD | 2019-04-03 | Shannon Savoy | Const | 2019-04-08 | Shannon Savoy | 2019-04-26 | Ayda Chaves
YVA-01 | YVA-01 | PI00633 | Verified | Install foam insulation around chain in static mast. | A | E | Sheri Fritz | DAS | 2019-04-15 | Sheri Fritz | Const | 2019-04-17 | Mike Tabbert | 2019-04-17 | Mike Tabbert
YVA-01 | YVA-01 | PI00634 | Verified | Provided design and install new support for A,B,C arrestors at GSU 1A for correct conductor spacing. | A | E | Sheri Fritz | DAS | 2019-04-17 | Sheri Fritz |  | 2019-04-29 | Robert Matthews | 2019-04-29 | Ayda Chaves
YVA-01 | YVA-01 | PI00653 | Verified | Replace oversized connectors in switchyard fencing poles. | B | E | Dustin Futrell | McD | 2019-04-22 | Dustin Futrell | Comm | 2019-05-07 | Shannon Savoy | 2019-08-07 | Fred Michael
YVA-01 | YVA-01 | PI12701 | Verified | 1A-NQS-GSUT-0001 GSU Transformer - The oil inlet to the Calisto has leak at the fitting. | C | E | Chris Boudreaux | McD | 2019-11-01 | Chris Boudreaux | Comm |  |  | 2020-01-23 | Shannon Scott
YVA-01 | YVA-01 | PI15061 | Verified | Clean up inside 1A-YVA-CAB-0001, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
YVA-01 | YVA-01 | PI15062 | Verified | Seal cable floor penetrations inside 1A-YVA-CAB-0001, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
YVA-01 | YVA-01 | PI15063 | Verified | Replace wiring duct covers inside 1A-YVA-CAB-0001, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
YVA-01 | YVA-01 | PI15064 | Verified | Heat shrink cable/wire tags inside 1A-YVA-CAB-0001, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
YVA-01 | YVA-01 | PI15065 | Verified | Replace cable tags that are too big to heat shrink inside 1A-YVA-CAB-0001, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
YVA-01 | YVA-01 | PI15066 | Verified | 50 OHM BNC Terminator missing at 1A-YVA-CAB-0001, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-29 | Jared Stimpson | 2020-02-05 | Shannon Scott
YVA-01 | YVA-01 | PI15067 | Verified | Clean up inside 1A-YVA-CAB-0002, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
YVA-01 | YVA-01 | PI15068 | Verified | Heat shrink cable/wire tags inside 1A-YVA-CAB-0002, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
YVA-01 | YVA-01 | PI15069 | Verified | Replace cable tags that are too big to heat shrink inside 1A-YVA-CAB-0002 , Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
YVA-01 | YVA-01 | PI15919 | Verified | 1A-NQS-CAB-0001 (Control Cabinet for GSUT 1A) - LV monitor is in alarm and not working. The operator was unable to scroll through to find alarms. | C | E | Mike Tabbert | McD | 2020-01-13 | Mike Tabbert | Comm | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
YVA-01 | YVA-01 | PI16210 | Verified | 1A-NQS-GSUT-0001 -SPX Air Breather has crack & mositure. It's not regenerating when moisture is present. | C | E | Jonathan Donham | McD | 2020-01-20 | Jonathan Donham | Comm | 2020-05-28 | Jonathan Donham | 2020-07-10 | Nelson Eichelberger
YVA-01 | YVA-01 | PI16211 | Verified | 1A-GSUT-0001 - Gauge has water intrusion & ruining the inner components | B | E | Jonathan Donham | McD | 2020-01-20 | Jonathan Donham | Comm | 2020-03-17 | Jonathan Donham | 2020-04-07 | Bernard Stasse
YVA-01 | YVA-01 | PI16212 | Verified | 1A-YVA-PCB-0001 - The PCB cabinet is leaking & has water intrusion, need fix | B | E | Mike Tabbert | McD | 2020-01-20 | Mike Tabbert | Comm | 2020-01-30 | Mike Tabbert | 2020-01-30 | Fred Michael
YVA-01 | YVA-01 | PI16213 | Verified | 1A-YVA-DSW-0001 & 0002 are mislabeled & need panel labels with correct information | C | E | Mike Tabbert | McD | 2020-01-20 | Mike Tabbert | Comm | 2020-01-28 | Mike Tabbert | 2020-02-05 | Shannon Scott
YVA-01 | YVA-01 | PI17235 | Verified | Submit Redline Drawings to Entergy - duplicate punch item | C | E | Mayur Patel | McD | 2020-02-28 | Mayur Patel | Comm | 2020-03-27 | Eric Policarpio | 2020-03-27 | Randy Carpenter
YVA-01 | YVA-01 | PI17236 | Verified | Submit Metering and Relay documentation to Entergy | C | E | Jonathan Donham | McD | 2020-02-28 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2021-03-03 | John Watts
YVA-01 | YVA-01 | PI17237 | Verified | Install cover plate son Metering Panel inside Main PDC | C | E | Jonathan Donham | McD | 2020-02-28 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2021-01-05 | Keith Pollock
YVA-01 | YVA-01 | PI17665 | Verified | 1A-NQS-CAB-0001 - Water leaking into cabinet from Plant West top vent. There also very small amounts getting into the vent on the Plant East side of the cabinet. | C | E | Mike Tabbert | McD | 2020-03-04 | Mike Tabbert | Comm | 2020-03-11 | Mike Tabbert | 2021-02-01 | Dave Goldak
YVA-01 | YVA-01 | PI18120 | Verified | 1A-YVA-PCB-0001 - The B phase on 1A PCB gas pressure is indicating in the yellow and has been for a few days now. | C | E | Jonathan Donham | McD | 2020-03-20 | Jonathan Donham | Comm | 2020-04-09 | Jonathan Donham | 2020-04-30 | John Watts
YVA-01 | YVA-01 | PI18162 | Verified | Calisto not operating properly GSU 1A | C | E | Mike Tabbert | McD | 2020-03-20 | Mike Tabbert | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
YVA-01 | YVA-01 | PI18183 | Open | 87G-1A-1 and 87G-1A-2 - IRIG B time sync is not connected properly. | C | E | Jonathan Donham | McD | 2020-03-24 | Jonathan Donham | Comm
YVA-02 | YVA-02 | PI00478 | Verified | Label wires in 1B-YVA-CAB-0003, 0004, 0005 in the 1B switchyard. | A | E | Sheri Fritz | DAS | 2019-04-05 | Sheri Fritz | Const | 2019-04-08 | Shannon Savoy | 2019-04-11 | Shannon Scott
YVA-02 | YVA-02 | PI00479 | Verified | Seal all conduits. | B | E | Logan Holland | McD | 2019-04-05 | Logan Holland | Const | 2019-06-14 | Logan Holland | 2019-06-14 | Logan Holland
YVA-02 | YVA-02 | PI00480 | Verified | Doors for 1B-YVA-PCB-0001 need bonding grounds attached (1B switchyard). | A | E | Sheri Fritz | DAS | 2019-04-05 | Sheri Fritz | Const | 2019-04-10 | Robert Matthews | 2019-04-17 | Shannon Scott
YVA-02 | YVA-02 | PI00481 | Verified | Label all boxes in the 1B switchyard. | B | E | Sheri Fritz | DAS | 2019-04-05 | Sheri Fritz | Const | 2019-04-10 | Robert Matthews | 2019-04-15 | Mike Tabbert
YVA-02 | YVA-02 | PI00482 | Verified | Label all term. blocks in the 1B switchyard. | A | E | Sheri Fritz | DAS | 2019-04-05 | Sheri Fritz | Const | 2019-04-08 | Shannon Savoy | 2019-04-11 | Shannon Scott
YVA-02 | YVA-02 | PI00483 | Verified | Install Beckwith 87GSUT-1B-1 in the main PDC. | B | E | Chris Boudreaux | McD | 2019-04-05 | Chris Boudreaux | Const | 2019-04-30 | Shannon Savoy | 2019-06-07 | Mike Tabbert
YVA-02 | YVA-02 | PI00484 | Verified | Provide as-builts for termination blocks added to dwg. | B | E | Mike Tabbert | McD | 2019-04-05 | Mike Tabbert | Const | 2019-04-09 | Mike Tabbert | 2019-04-09 | Mike Tabbert
YVA-02 | YVA-02 | PI00518 | Verified | Replaced HV Arrestor - Top of the GSU 1B transformer | A | E | Sheri Fritz | NAAS | 2019-04-05 | Sheri Fritz | Const | 2019-04-17 | Ayda Chaves | 2019-04-17 | Ayda Chaves
YVA-02 | YVA-02 | PI00519 | Verified | Pull and Terminate cable to J.Box 1B-YVA-CAB-0003 for the CVTs. | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-08 | Shannon Savoy | 2019-04-08 | Ayda Chaves
YVA-02 | YVA-02 | PI00520 | Verified | Install wiring between J. Box 1B-YVA-DSW-002/001 & 1B-YVA-GNDS-002 /001 for the Switches. | A | E | Sheri Fritz | DAS | 2019-04-05 | Sheri Fritz | Const | 2019-04-09 | Ayda Chaves | 2019-04-09 | Ayda Chaves
YVA-02 | YVA-02 | PI00521 | Verified | Complete fencing Grounding Unit 1B | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-22 | Shannon Savoy | 2019-04-22 | Ayda Chaves
YVA-02 | YVA-02 | PI00522 | Verified | Install SWYD fence & Gates Unit 1B. | A | E | Sheri Fritz | PSC | 2019-04-05 | Sheri Fritz | Const | 2019-04-18 | Ayda Chaves | 2019-04-18 | Ayda Chaves
YVA-02 | YVA-02 | PI00523 | Verified | 1BNQSK0014, Pull Cable | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-08 | Shannon Savoy | 2019-04-08 | Mike Tabbert
YVA-02 | YVA-02 | PI00524 | Verified | 1BYVAC0002, Pull Cable | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-08 | Shannon Savoy | 2019-04-08 | Mike Tabbert
YVA-02 | YVA-02 | PI00525 | Verified | 1BYVAC0100, Pull Cable | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-05 | Shannon Savoy | 2019-04-08 | Mike Tabbert
YVA-02 | YVA-02 | PI00526 | Verified | 1BLANO0001, Terminate Cable | A | E | Sheri Fritz | ITS | 2019-04-05 | Sheri Fritz | Const | 2019-04-08 | Shannon Savoy | 2019-04-08 | Mike Tabbert
YVA-02 | YVA-02 | PI00527 | Verified | 1BNQSK0014 & 1BNQSK0015 Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-12 | Shannon Savoy | 2019-04-12 | Mike Tabbert
YVA-02 | YVA-02 | PI00529 | Verified | 1BYVAO0143, Terminate Cable | A | E | Sheri Fritz | ITS | 2019-04-05 | Sheri Fritz | Const | 2019-04-08 | Shannon Savoy | 2019-04-08 | Mike Tabbert
YVA-02 | YVA-02 | PI00530 | Verified | All cabinets in switchyard and Main PPDC to be cleaned after termination completion. | A | E | Shannon Savoy | McD | 2019-04-05 | Shannon Savoy | Const | 2019-04-08 | Shannon Savoy | 2019-04-08 | Mike Tabbert
YVA-02 | YVA-02 | PI00531 | Verified | Provide all test reports needed for subsystem turnover. | B | E | Sheri Fritz | DAS | 2019-04-10 | Sheri Fritz | Const | 2019-04-22 | Logan Holland | 2019-04-22 | Logan Holland
YVA-02 | YVA-02 | PI00534 | Verified | Install Foam Insulation around chain in Static Mast. | A | E | Sheri Fritz | DAS | 2019-04-12 | Sheri Fritz | Const | 2019-04-17 | Mike Tabbert | 2019-04-17 | Mike Tabbert
YVA-02 | YVA-02 | PI00632 | Verified | Install jumpers for transmission line in switchyard 1B. | A | E | Sheri Fritz | DAS | 2019-04-15 | Sheri Fritz | Const | 2019-04-17 | Mike Tabbert | 2019-04-17 | Mike Tabbert
YVA-02 | YVA-02 | PI00635 | Verified | Provided design and install new support for A,B,C arrestors at GSU 1B for correct conductor spacing. | A | E | Sheri Fritz | DAS | 2019-04-17 | Sheri Fritz |  | 2019-04-29 | Robert Matthews | 2019-04-29 | Ayda Chaves
YVA-02 | YVA-02 | PI00654 | Verified | Replace oversized connectors in switchyard fencing poles. | B | E | Dustin Futrell | McD | 2019-04-22 | Dustin Futrell | Comm | 2019-06-07 | Shannon Savoy | 2019-08-07 | Fred Michael
YVA-02 | YVA-02 | PI15070 | Verified | Cable 1BYVAC0034 not terminated, has bare ring lug | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YVA-02 | YVA-02 | PI15071 | Verified | Cable 1BYVAC0125-2 not terminated, has bare ring lug | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YVA-02 | YVA-02 | PI15072 | Verified | Cable 1BYVAC0125-1 not terminated, has bare ring lug | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YVA-02 | YVA-02 | PI15073 | Verified | Cable 1BYVAC0014-10 not terminated, not identified as spare | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-07 | Mayur Patel | 2020-04-07 | Bernard Stasse
YVA-02 | YVA-02 | PI15074 | Verified | Cable 1BNQSC0021 not terminated, not identified as spare | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-07 | Mayur Patel | 2020-04-07 | Bernard Stasse
YVA-02 | YVA-02 | PI15075 | Verified | Clean up inside 1B-YVA-CAB-0001, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-15 | Shannon Scott
YVA-02 | YVA-02 | PI15076 | Verified | Seal cable floor penetrations inside 1B-YVA-CAB-0001, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-07 | Bernard Stasse
YVA-02 | YVA-02 | PI15077 | Verified | Replace wiring duct covers inside 1B-YVA-CAB-0001 , Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-30 | Jared Stimpson | 2020-02-05 | Shannon Scott
YVA-02 | YVA-02 | PI15078 | Verified | Heat shrink cable/wire tags inside 1B-YVA-CAB-0001, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YVA-02 | YVA-02 | PI15079 | Verified | Replace cable tags that are too big to heat shrink inside 1B-YVA-CAB-0001 , Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YVA-02 | YVA-02 | PI15080 | Verified | Install missing panel covers at 1B-YVA-CAB-0001, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YVA-02 | YVA-02 | PI15081 | Verified | Need phenolic label for Tag No. 1B-YVA-CAB-0001 (front and back side) Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-15 | Shannon Scott
YVA-02 | YVA-02 | PI15082 | Verified | Dress up loose cable inside 1B-YVA-CAB-0001, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-15 | Shannon Scott
YVA-02 | YVA-02 | PI15083 | Verified | Cables not terminated, not labeled as spares, ends not taped, verify cables and terminate or marks as spare inside 1B-YVA-CAB-0001, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-07 | Mayur Patel | 2020-04-07 | Bernard Stasse
YVA-02 | YVA-02 | PI15084 | Verified | Clean up inside 1B-YVA-CAB-0002, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-15 | Shannon Scott
YVA-02 | YVA-02 | PI15085 | Verified | Need phenolic label for tag no. 1B-YVA-CAB-0002 (backside), Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-15 | Shannon Scott
YVA-02 | YVA-02 | PI15086 | Verified | One cable not terminated, exposed ring lug inside 1B-YVA-CAB-0001, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YVA-02 | YVA-02 | PI15087 | Verified | Trim tie wraps inside 1B-YVA-CAB-0002, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-10 | Fred Michael | 2020-02-15 | Shannon Scott
YVA-02 | YVA-02 | PI16214 | Verified | 1B-YVA-PCB-0001 - The PCB cabinet is leaking & has water intrusion, need fix | B | E | Mike Tabbert | McD | 2020-01-20 | Mike Tabbert | Comm | 2020-01-31 | Mike Tabbert | 2020-02-05 | Shannon Scott
YVA-02 | YVA-02 | PI16215 | Verified | 1B-YVA-DSW-0001 & 0002 are mislabeled & need panel labels with correct information | C | E | Mike Tabbert | McD | 2020-01-20 | Mike Tabbert | Comm | 2020-01-31 | Mike Tabbert | 2020-02-05 | Shannon Scott
YVA-02 | YVA-02 | PI16216 | Verified | Replace LED on 138KV Ground Switch 0002 panel. The closed indication is not illuminating on the main PDC panel Board. | C | E | Jonathan Donham | McD | 2020-01-20 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2020-04-07 | Bernard Stasse
YVA-02 | YVA-02 | PI16217 | Verified | 1B-NQS-GSUT-0001 - The "Yes" button on the 1B GSU Transformer HV Temperature Controller is broken | C | E | Mike Tabbert | McD | 2020-01-20 | Mike Tabbert | Comm | 2020-05-28 | Mike Tabbert | 2021-05-24 | Keith Pollock
YVA-02 | YVA-02 | PI17297 | Verified | Submit Redline Drawings to Entergy - duplicate punch item | C | E | Mayur Patel | McD | 2020-02-28 | Mayur Patel | Comm | 2020-03-27 | Eric Policarpio | 2020-03-27 | Randy Carpenter
YVA-02 | YVA-02 | PI17298 | Verified | Submit Metering and Relay documentation to Entergy | C | E | Jonathan Donham | McD | 2020-02-28 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2021-03-03 | John Watts
YVA-02 | YVA-02 | PI17299 | Verified | Install cover plate son Metering Panel inside Main PDC | C | E | Jonathan Donham | McD | 2020-02-28 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2021-03-03 | John Watts
YVA-02 | YVA-02 | PI17659 | Verified | 1B-NQS-GSUT-0001 - 1B GSUT dehydrating breather has a local indication of a humidity sensor error. | C | E | Jonathan Donham | McD | 2020-03-04 | Jonathan Donham | Comm | 2020-05-19 | Jonathan Donham | 2020-06-09 | Love Kayode
YVA-02 | YVA-02 | PI17666 | Verified | 1B-NQS-CAB-0001 - Water leaking into cabinet from Plant West top vent. There also very small amounts getting into the vent on the Plant East side of the cabinet. | C | E | Mike Tabbert | McD | 2020-03-04 | Mike Tabbert | Comm | 2020-03-06 | Mike Tabbert | 2021-02-01 | Dave Goldak
YVA-02 | YVA-02 | PI18163 | Verified | Calisto not operating properly GSU 1B | C | E | Jonathan Donham | McD | 2020-03-20 | Jonathan Donham | Const | 2020-05-28 | Jonathan Donham | 2021-04-29 | ABB
YVA-02 | YVA-02 | PI18184 | Verified | 87G-1B-1 and 87G-1B-2 - IRIG B time sync is not connected properly. | C | E | Jonathan Donham | McD | 2020-03-24 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2021-04-27 | John Watts
YWA-01 | YWA-01 | PI00742 | Verified | Repair door hinges on 1C-YWA-PCV-0001. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-02 | Shannon Savoy | 2019-05-09 | Mike Tabbert
YWA-01 | YWA-01 | PI00743 | Verified | Clean all structural steel supports and cold galvanize where needed. | A | E | Sheri Fritz | DAS | 2019-04-29 | Sheri Fritz | Const | 2019-05-02 | Robert Matthews | 2019-05-08 | Shannon Scott
YWA-01 | YWA-01 | PI00744 | Verified | Tighten seal tite connectors on all panels. | A | E | Sheri Fritz | DAS | 2019-04-29 | Sheri Fritz | Const | 2019-05-14 | Robert Matthews | 2019-05-14 | Shannon Scott
YWA-01 | YWA-01 | PI00745 | Verified | 1C-YWA-DSW-0001 and 0002 are incorrectly labeled "DWS". | A | E | Sheri Fritz | DAS | 2019-04-29 | Sheri Fritz | Const | 2019-05-02 | Robert Matthews | 2019-05-08 | Shannon Scott
YWA-01 | YWA-01 | PI00746 | Verified | Tighten cable bushing & lock nut inside 1C-YWA-DSW-0002. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-14 | Shannon Savoy | 2019-05-20 | Shannon Scott
YWA-01 | YWA-01 | PI00747 | Verified | Tighten ground inside 1C-YWA-GNDS-002. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-14 | Shannon Savoy | 2019-05-20 | Shannon Scott
YWA-01 | YWA-01 | PI00748 | Verified | Patch concrete foundation in the southeast corner of the switchyard at 1C-YWA-CAB-0003. | B | C | Johnny Campbell | McD | 2019-04-29 | Johnny Campbell | Const | 2019-06-25 | Jack Fields | 2019-06-28 | Shannon Scott
YWA-01 | YWA-01 | PI00749 | Verified | Confirm grounding to ground switch is per design. | A | E | Sheri Fritz | DAS | 2019-04-29 | Sheri Fritz | Const | 2019-05-02 | Robert Matthews | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00750 | Verified | Ground doors inside 1C-YWA-PCV-0001. | A | E | Sheri Fritz | DAS | 2019-04-29 | Sheri Fritz | Const | 2019-05-02 | Robert Matthews | 2019-05-06 | Mike Tabbert
YWA-01 | YWA-01 | PI00751 | Verified | Install hand hole cover on lightning mast. | B | E | Sheri Fritz | DAS | 2019-04-29 | Sheri Fritz | Const | 2019-05-02 | Robert Matthews | 2019-05-06 | Mike Tabbert
YWA-01 | YWA-01 | PI00752 | Verified | Tighten support structure bolts for 1C-YWA-PCV-0001. | C | E | Sheri Fritz | DAS | 2019-04-29 | Sheri Fritz | Const | 2019-05-14 | Robert Matthews | 2019-05-14 | Shannon Scott
YWA-01 | YWA-01 | PI00753 | Verified | Remove sharp edges inside all panels. | A | E | Sheri Fritz | DAS | 2019-04-29 | Sheri Fritz | Const | 2019-05-02 | Robert Matthews | 2019-05-08 | Shannon Scott
YWA-01 | YWA-01 | PI00754 | Verified | Missing condulet cover at 1C-YWA-GNDS-0001. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-02 | Shannon Savoy | 2019-05-08 | Shannon Scott
YWA-01 | YWA-01 | PI00755 | Verified | Missing condulet cover at 1C-YWA-DSW-0001. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-02 | Shannon Savoy | 2019-05-08 | Shannon Scott
YWA-01 | YWA-01 | PI00756 | Verified | Replace lock washer in the ground connector on back of 1C-YWA-GNDS-0001. | A | E | Sheri Fritz | DAS | 2019-04-29 | Sheri Fritz | Const | 2019-05-02 | Robert Matthews | 2019-05-14 | Ayda Chaves
YWA-01 | YWA-01 | PI00757 | Verified | Bolt / washers not fully tightening on many J-Box brackets (weld needs grinding down). | A | E | Sheri Fritz | DAS | 2019-04-29 | Sheri Fritz | Const | 2019-05-14 | Robert Matthews | 2019-05-14 | Shannon Scott
YWA-01 | YWA-01 | PI00758 | Verified | Replace all conduit straps at the transformer. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00759 | Verified | Raise switchyard elevation at the northwest corner at the ladder - hole creates hazard. | C | C | Johnny Campbell | McD | 2019-04-29 | Johnny Campbell | Const | 2019-06-21 | Johnny Campbell | 2019-06-21 | Shannon Scott
YWA-01 | YWA-01 | PI00760 | Verified | Need to add rocks under grating - north-center area of transformer. | B | C | Alan Huntsman | McD | 2019-04-29 | Alan Huntsman | Const | 2020-02-25 | Alan Huntsman | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI00761 | Verified | Tighten all seal tite connectors at the transformer. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-09 | Mike Tabbert
YWA-01 | YWA-01 | PI00762 | Verified | Condulet cover missing gasket (or needs adjusting) at the northeast corner of transformer. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-14 | Shannon Scott
YWA-01 | YWA-01 | PI00763 | Verified | Remove cable protectors on lifting lugs and the lanyard - on transformer. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00764 | Verified | Bushings not installed on seal tite connectors in 1C-NQS-CAB-0001. | D | I | Michael Law | McD | 2019-04-29 | Michael Law | Const | 2020-01-31 | Mike Tabbert | 2020-02-07 | Shannon Scott
YWA-01 | YWA-01 | PI00765 | Verified | Bottom plate missing nut in 1C-NQS-CAB-0001. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-08 | Shannon Scott
YWA-01 | YWA-01 | PI00766 | Verified | Complete all work in 1C-NQS-CAB-0001. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-14 | Shannon Savoy | 2019-05-20 | Shannon Scott
YWA-01 | YWA-01 | PI00767 | Verified | Missing Tranformer Temperture Controller in 1C-NQS-CAB-0001. | C | E | Jonathan Donham | McD | 2019-04-29 | Jonathan Donham | Const | 2020-02-24 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI00768 | Verified | Clean the transformer deck. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-16 | Mike Harris | 2019-05-20 | Shannon Scott
YWA-01 | YWA-01 | PI00769 | Verified | Sharp edges on oil expansion joint flanges at the transformer. | A | E | Mike Tabbert | McD | 2019-04-29 | Mike Tabbert | Const | 2019-05-14 | Shannon Savoy | 2019-05-20 | Shannon Scott
YWA-01 | YWA-01 | PI00770 | Verified | Check all CGB connections at fan JBs for tightness. | A | E | Mike Tabbert | McD | 2019-04-29 | Mike Tabbert | Const | 2019-05-14 | Shannon Savoy | 2019-05-20 | Shannon Scott
YWA-01 | YWA-01 | PI00771 | Verified | Tubing needs support on the west side of the transformer. | D | I | Michael Law | McD | 2019-04-29 | Michael Law | Const | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
YWA-01 | YWA-01 | PI00772 | Verified | Weld down transformer. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-14 | Shannon Savoy | 2019-05-14 | Mike Tabbert
YWA-01 | YWA-01 | PI00773 | Verified | Complete all McDermott paperwork. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-20 | Ed Gober | 2019-05-20 | Ed Gober
YWA-01 | YWA-01 | PI00774 | Verified | Provide all Dashiell paperwork. | A | E | Sheri Fritz | DAS | 2019-04-29 | Sheri Fritz | Const | 2019-05-17 | Sheri Fritz | 2019-05-20 | Ed Gober
YWA-01 | YWA-01 | PI00775 | Verified | Provide all transformer testing documentaion. | A | E | Sheri Fritz | NAAS | 2019-04-29 | Sheri Fritz | Const | 2019-05-17 | Sheri Fritz | 2019-05-20 | Ed Gober
YWA-01 | YWA-01 | PI00776 | Verified | Switchyard 1C, All sealtight to be externally grounded | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00777 | Verified | Switdhyard 1C, All buried conduit to be grounded. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00778 | Verified | Switchyard 1C, Fence grounding needs to be completed. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-09 | Mike Tabbert
YWA-01 | YWA-01 | PI00779 | Verified | 1C-YWA-GNDS-0002 and 1CYWA-DWS-0002, External grounding on sealtight the wroung size. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-02 | Shannon Savoy | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00780 | Verified | 1C-YWA-GNDS-0002, missing Tee-Condulet cover. | B | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-02 | Shannon Savoy | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00781 | Verified | 1C-YWA-GNDS-0002, Sealtight fitting cross threaded. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00782 | Verified | 1C-YWA-GNDS-0002, Broken Microswitch inside cabinet. | A | E | Sheri Fritz | DAS | 2019-04-29 | Sheri Fritz | Const | 2019-05-07 | Shannon Savoy | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00783 | Verified | Switchyard 1C, All panels need to be cleaned. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00784 | Verified | 1C-YWA-PCB-0001, Remove plastic covers from duct bank stub-ups, install permanent covers and grounding bushings. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00785 | Verified | 1C-YWA-GNDS-0001, Missing conduit bushing inside of cabinet. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-02 | Shannon Savoy | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00786 | Verified | 1C-YWA-DWS-0001, Jumper cables have been up against sharp edge and insulation is cut. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00787 | Verified | 1C-NQS-PNL-0001, Clean transformer control panel. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-08 | Mike Tabbert
YWA-01 | YWA-01 | PI00788 | Verified | 1C-NQS-PNL-0001, Factory wiring harness has been damaged from door opening, harness needs to be repaired and rerouted. | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-20 | Dan Dula | 2019-05-21 | Mike Tabbert
YWA-01 | YWA-01 | PI00789 | Verified | 1CNQSC0025, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00790 | Verified | 1CYWAC0101, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-13 | Mike Tabbert
YWA-01 | YWA-01 | PI00791 | Verified | 1CYWAX0002, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00792 | Verified | 1CYWAX0003, Pull and Terminate Cable | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00793 | Verified | 1CNQSC0021, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00794 | Verified | 1CNQSC0025, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-13 | Shannon Savoy | 2019-05-13 | Mike Tabbert
YWA-01 | YWA-01 | PI00795 | Verified | 1CNQSK0001, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00796 | Verified | 1CYWAC0023, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00797 | Verified | 1CYWAC0024, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00798 | Verified | 1CYWAC0027, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00799 | Verified | 1CYWAC0029, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00800 | Verified | 1CYWAC0030, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00801 | Verified | 1CYWAC0031, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00802 | Verified | 1CYWAC0033, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00803 | Verified | 1CYWAC0034, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00804 | Verified | 1CYWAC0035, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00805 | Verified | 1CYWAC0036, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00806 | Verified | 1CYWAC0037, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00807 | Verified | 1CYWAC0101, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-13 | Shannon Savoy | 2019-05-13 | Mike Tabbert
YWA-01 | YWA-01 | PI00808 | Verified | 1CYWAC0109, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00809 | Verified | 1CYWAC0125, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00810 | Verified | 1CYWAK0007, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00811 | Verified | 1CYWAK0008, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00812 | Verified | 1CYWAK0009, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00813 | Verified | 1CYWAK0010, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-13 | Mike Tabbert
YWA-01 | YWA-01 | PI00814 | Verified | 1CYWAK0011, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00815 | Verified | 1CYWAK0012, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00816 | Verified | 1CYWAK0020, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00817 | Verified | 1CYWAO0145, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00818 | Verified | 1CYWAX0002, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00819 | Verified | 1CYWAX0003, Complete From Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00820 | Verified | 1CNQSC0009, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00821 | Verified | 1CNQSC0025, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00822 | Verified | 1CNQSX0001, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00823 | Verified | 1CYWAC0003, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00824 | Verified | 1CYWAC0007, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00825 | Verified | 1CYWAC0010, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00826 | Verified | 1CYWAC0014, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00827 | Verified | 1CYWAC0018, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00828 | Verified | 1CYWAC0026, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-04-30 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00829 | Verified | 1CYWAC0101, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-13 | Shannon Savoy | 2019-05-13 | Mike Tabbert
YWA-01 | YWA-01 | PI00830 | Verified | 1CYWAC0108, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00831 | Verified | 1CYWAC0110, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00832 | Verified | 1CYWAC0111, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-13 | Mike Tabbert
YWA-01 | YWA-01 | PI00833 | Verified | 1CYWAC0121, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00834 | Verified | 1CYWAK0020, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-03 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00835 | Verified | 1CYWAX0002, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI00836 | Verified | 1CYWAX0003, Complete to Termination | A | E | Shannon Savoy | McD | 2019-04-29 | Shannon Savoy | Const | 2019-05-07 | Shannon Savoy | 2019-05-07 | Mike Tabbert
YWA-01 | YWA-01 | PI01007 | Verified | 1C-YWA-PCV-0001 - Bad trip coil on phase A. | A | E | Sheri Fritz | DAS | 2019-05-08 | Sheri Fritz | Const | 2019-05-14 | Robert Matthews | 2019-05-14 | Mike Tabbert
YWA-01 | YWA-01 | PI10252 | Verified | 1C-NQS-CAB-0001 - Control panel door is damaged & needs replaced. | C | E | Chris Boudreaux | McD | 2019-10-24 | Chris Boudreaux | Comm |  |  | 2020-01-23 | Shannon Scott
YWA-01 | YWA-01 | PI15088 | Verified | Clean up inside 1C-YWA-CAB-0002, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI15089 | Verified | Need phenolic label for tag no. 1C-YWA-CAB-0002 (front and back side), Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2021-01-05 | Keith Pollock
YWA-01 | YWA-01 | PI15090 | Verified | Replace wiring duct covers inside 1C-YWA-CAB-0002 , Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI15091 | Verified | Seal cable floor penetrations inside inside 1C-YWA-CAB-0002 , Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI15092 | Verified | Heat shrink cable tags inside 1C-YWA-CAB-0002, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI15093 | Verified | Replace cable/wire tags that are too big to heat shrink inside 1C-YWA-CAB-0002, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI15094 | Verified | Clean up inside 1C-YWA-CAB-0001, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI15095 | Verified | Need phenolic label for tag no. 1C-YWA-CAB-0001 (front side) | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI15096 | Verified | Heat shrink cable tags inside 1C-YWA-CAB-0001, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI15097 | Verified | Replace cable/wire tags that are too big to heat shrink inside 1C-YWA-CAB-0001, Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI15098 | Verified | Replace wiring duct covers inside 1C-YWA-CAB-0001 , Main PDC | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-26 | Mike Tabbert | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI15099 | Verified | Cables not terminated, verify and identify as spares or terminate at 1C-YWA-CAB-0001, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI15100 | Verified | 50 OHM BNC Terminator missing at 1C-YWA-CAB-0001, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-29 | Jared Stimpson | 2020-02-05 | Shannon Scott
YWA-01 | YWA-01 | PI15101 | Verified | Cables not terminated, verify and identify as spares or terminate at 1C-YWA-CAB-0002, Main PDC | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-07 | Bernard Stasse
YWA-01 | YWA-01 | PI17232 | Verified | Submit Redline Drawings to Entergy - duplicate punch item | C | E | Mayur Patel | McD | 2020-02-28 | Mayur Patel | Comm | 2020-03-27 | Eric Policarpio | 2020-03-27 | Randy Carpenter
YWA-01 | YWA-01 | PI17233 | Verified | Submit Metering and Relay documentation to Entergy | C | E | Jonathan Donham | McD | 2020-02-28 | Jonathan Donham | Comm | 2020-03-31 | Jonathan Donham | 2021-03-03 | John Watts
YWA-01 | YWA-01 | PI17234 | Verified | Install cover plate son Metering Panel inside Main PDC | C | E | Jonathan Donham | McD | 2020-02-28 | Jonathan Donham | Comm | 2020-03-10 | Jonathan Donham | 2021-01-05 | Keith Pollock
YWA-01 | YWA-01 | PI17829 | Verified | 87GSUT-1C-2 - Repair 'IRIG OK' (and any other) issues on SEL-487E relay in the Main PDC. | C | E | Jonathan Donham | McD | 2020-03-16 | Jonathan Donham | Const | 2020-03-31 | Jonathan Donham | 2020-06-04 | Cintrel Spears
YWA-01 | YWA-01 | PI17830 | Verified | 87/21P2-1C - A red LED is illuminating with no description. | C | E | Mike Tabbert | McD | 2020-03-16 | Mike Tabbert | Const | 2020-06-08 | Mike Tabbert | 2020-06-15 | Cintrel Spears
YWA-01 | YWA-01 | PI17831 | Verified | 87/21P1-1C - Two red LEDs are illuminating with no descriptions. | C | E | Jonathan Donham | McD | 2020-03-16 | Jonathan Donham | Const | 2020-03-31 | Jonathan Donham | 2020-06-04 | Cintrel Spears
YWA-01 | YWA-01 | PI18065 | Open | 1C-NQS-CAB-0001 - Lumasmart RTD temperature monitor is not working properly. | C | E | Mike Tabbert | McD | 2020-03-18 | Mike Tabbert | Comm
YWA-01 | YWA-01 | PI18066 | Cleared | 1C-NQS-CAB-0001 - The high voltage winding temp monitor is not working properly and is always in alarm. | C | E | Jonathan Donham | McD | 2020-03-18 | Jonathan Donham | Comm | 2020-05-28 | Jonathan Donham
YWA-01 | YWA-01 | PI18164 | Verified | Calisto not operating properly GSU 1C | C | E | Mike Tabbert | McD | 2020-03-20 | Mike Tabbert | Const | 2020-06-11 | Jason Ezell | 2020-06-11 | Jason Ezell
DEM-02 | DEM-02 | PI04980 | Verified | Install blind flange on both flush ports and drain ports at floccuant pump skid. | A | P | James Beech | McD | 2019-09-12 | James Beech | Const |  |  | 2019-10-19 | Kelvin Cook
DEM-02 | DEM-02 | PI09792 | Verified | Test Package DEM-T-01 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-19 | Kelvin Cook
DEM-02 | DEM-02 | PI09793 | Verified | Test Package DEM-T-02 need to be tested | A | P | James Beech | McD | 2019-10-22 | James Beech | Const | 2020-03-27 | James Beech | 2020-04-02 | Michael Law
DEM-02 | DEM-02 | PI09794 | Verified | Test Package DEM-T-03 need to be tested | A | P | James Beech | McD | 2019-10-22 | James Beech | Const | 2020-03-11 | Tim Green | 2020-04-02 | Michael Law
DEM-02 | DEM-02 | PI09795 | Verified | Test Package DEM-T-02 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2020-01-20 | Kelvin Cook
DEM-02 | DEM-02 | PI09796 | Verified | Test Package DEM-T-03 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2020-01-20 | Kelvin Cook
DEM-02 | DEM-02 | PI09791 | Verified | Test Package DEM-T-04 need to be tested | A | P | Kelvin Cook | McD | 2019-10-22 | Kelvin Cook | Const |  |  | 2019-12-19 | Kelvin Cook
DEM-02 | DEM-02 | PI16137 | Verified | Verify all ubolts are tight on ISO 1C-DEM-PD-P40-0350-01. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-17 | Charlie English | 2020-01-17 | Kelvin Cook
DEM-02 | DEM-02 | PI16138 | Verified | Verify all ubolts are tight on ISO 1C-DEM-PD-P40-0350-02. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-17 | Charlie English | 2020-01-17 | Kelvin Cook
DEM-02 | DEM-02 | PI16139 | Verified | Slope issue on Iso 1C-DEM-PD-P40-0350-02 just off support 1C-DEM-PD-HGR-0055. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-02-24 | Tim Green | 2020-03-03 | Michael Law
DEM-02 | DEM-02 | PI16140 | Verified | Remove Concrete from drain grill on Iso 1C-DEM-PD-0350-02. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const |  |  | 2020-01-25 | Kelvin Cook
DEM-02 | DEM-02 | PI16141 | Verified | Floor drain 02 Missing grill on Iso 1C-DEM-PD-P40-0350-03. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-22 | Tim Green | 2020-01-25 | Kelvin Cook
DEM-02 | DEM-02 | PI16142 | Verified | Level support 1C-DEM-PD-HGR-0045 on Iso 1C-DEM-PD-P40-0350-03. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const |  |  | 2020-01-24 | Kelvin Cook
DEM-02 | DEM-02 | PI16143 | Verified | On Iso 1C-DEM-PD-P40-0350-03 future connection need to be made at roof drain. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-02-24 | Tim Green | 2020-03-03 | Michael Law
DEM-02 | DEM-02 | PI16144 | Verified | On Iso 1C-DEM-PD-P40-0350-03 first and last floor drain need to be modified by eng for drain covers. | C | C | Michael Law | McD | 2020-01-16 | Michael Law | Const | 2020-04-09 | Michael Law | 2020-04-09 | Michael Law
DEM-02 | DEM-02 | PI16145 | Verified | Verify that all ubolts are tight on Iso 1C-DEM-PD-P40-0350-04. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-17 | Charlie English | 2020-01-17 | Ethan Byrd
DEM-02 | DEM-02 | PI16146 | Verified | On Iso 1C-DEM-PD-P40-0355-01 support 1C-DEM-PD-HGR-0068 & 0070 have loose nuts. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-17 | Charlie English | 2020-01-17 | Ethan Byrd
DEM-02 | DEM-02 | PI16147 | Verified | On Iso 1C-DEM-PD-P40-0355-01, 2 of the 3 floor drain needs a grill. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-22 | Tim Green | 2020-01-24 | Kelvin Cook
DEM-02 | DEM-02 | PI16148 | Verified | On ISO 1C-DEM-PD-P40-0355-02 tighten ubolt on support 1C-DEM-PD-HGR-0072. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-17 | Charlie English | 2020-01-17 | Ethan Byrd
DEM-02 | DEM-02 | PI16149 | Verified | On ISO 1C-DEM-PD-P40-0355-02 relocate support 1C-DEM-PD-HGR-0074 to the south/ add shim. | A | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-17 | Charlie English | 2020-01-17 | Ethan Byrd
DEM-02 | DEM-02 | PI16150 | Verified | On ISO 1C-DEM-PD-P40-0355-02 floor drain needs a grill. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-22 | Tim Green | 2020-01-24 | Kelvin Cook
DEM-02 | DEM-02 | PI16151 | Verified | On ISO 1C-DEM-PD-P40-0355-03 supports 1C-DEM-PD-HGR-0079 & 0080 have loose nuts at ubolt. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-17 | Charlie English | 2020-01-17 | Ethan Byrd
DEM-02 | DEM-02 | PI16152 | Verified | On ISO 1C-DEM-PD-P40-0355-03 supports 1C-DEM-PD-HGR-0077 has loose ubolt. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-17 | Charlie English | 2020-01-17 | Ethan Byrd
DEM-02 | DEM-02 | PI16153 | Verified | On ISO 1C-DEM-PD-P40-0355-03, 2 of the 3 floor drain needs a grill. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-22 | Tim Green | 2020-01-24 | Kelvin Cook
DEM-02 | DEM-02 | PI16154 | Verified | Tag all valves on PID 10-DEM-ME-PID-0007. | C | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-05-04 | Michael Law | 2020-05-04 | Michael Law
DEM-02 | DEM-02 | PI16155 | Verified | On ISO 10-DEM-PD-P41-0700-01 relocate valve 10-DEM-V-0700 stop. Make operator friendly. Underneath steps. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-17 | Charlie English | 2020-01-17 | Ethan Byrd
DEM-02 | DEM-02 | PI16156 | Verified | On Iso 1A-DEM-PD-P41-0105-01 missing ubolt on support 1A-FWS-PD-HGR-0173. | B | P | James Beech | McD | 2020-01-16 | James Beech | Const | 2020-01-17 | Charlie English | 2020-01-17 | Ethan Byrd
DEM-02 | DEM-02 | PI16157 | Verified | Red line Iso 1C-DEM-PD-P40-0355-02. | C | P | Kelvin Cook | McD | 2020-01-16 | Kelvin Cook | Const | 2020-01-22 | Tim Green | 2020-01-24 | Kelvin Cook
DEM-02 | DEM-02 | PI16665 | Verified | Tighten u-bolts on the common east/west run header - STG mezz north side. | A | P | James Beech | McD | 2020-02-07 | James Beech | Const | 2020-02-10 | Tim Green | 2020-02-11 | Kelvin Cook
DEM-02 | DEM-02 | PI16666 | Verified | Complete welding on 2 supports on the common east/west run header - STG mezz north side. | A | P | James Beech | McD | 2020-02-07 | James Beech | Const | 2020-02-10 | Tim Green | 2020-02-11 | Kelvin Cook
DEM-02 | DEM-02 | PI16667 | Verified | Prime & paint all welds - system wide. | C | X | Johnny Campbell | McD | 2020-02-07 | Johnny Campbell | Const | 2020-04-06 | Johnny Campbell | 2020-04-24 | Mark Williamson
COP-01 | COP-01 | PI16694 | Verified | 10-COP-CP-0001 in the control room - label panel. | C | E | Chris Colvin | McD | 2020-02-11 | Chris Colvin | Const | 2020-04-01 | Chris Colvin | 2020-04-02 | Mike Tabbert
COP-01 | COP-01 | PI16695 | Verified | 10-COP-CP-0001 in the control room - needs 3/4" Hoffman plug. | B | E | Chris Colvin | McD | 2020-02-11 | Chris Colvin | Const |  |  | 2020-02-13 | Mike Tabbert
COP-01 | COP-01 | PI16696 | Verified | 10-COP-CP-0001 in the control room - tighten conduit clamps. | B | E | Chris Colvin | McD | 2020-02-11 | Chris Colvin | Const |  |  | 2020-02-13 | Mike Tabbert
COP-01 | COP-01 | PI16697 | Verified | 10-COP-CP-0001 in the control room - tighten wall mounting screws. | B | E | Chris Colvin | McD | 2020-02-11 | Chris Colvin | Const |  |  | 2020-02-13 | Mike Tabbert
COP-01 | COP-01 | PI16698 | Verified | Label sirens: 10-COP-SIRN-0001, 0002, 0003 & 0004. | C | E | Chris Colvin | McD | 2020-02-11 | Chris Colvin | Const | 2020-04-02 | Mike Tabbert | 2020-04-02 | Mike Tabbert
COP-01 | COP-01 | PI16699 | Verified | 10-COP-JB-0001 - east side of STG operating deck - label JB. | C | E | Chris Colvin | McD | 2020-02-11 | Chris Colvin | Const | 2020-03-31 | Matt Gilmore | 2020-04-02 | Mike Tabbert
COP-01 | COP-01 | PI16700 | Verified | 10-COP-JB-0001 - east side of STG operating deck - install larger sized terminal blocks. | A | E | Chris Colvin | McD | 2020-02-11 | Chris Colvin | Const |  |  | 2020-02-13 | Mike Tabbert
COP-01 | COP-01 | PI16701 | Verified | Red-line drawing LK-1C-203-PL-EE-EQP-0003 to show 10-COP-SIRN-0003. | B | E | Mike Tabbert | McD | 2020-02-11 | Mike Tabbert | Const |  |  | 2020-02-11 | Mike Tabbert
COP-01 | COP-01 | PI17759 | Verified | 10-COP-JB-0001 needs junction box tag on the box in the Control Room | C | E | Chris Colvin | McD | 2020-03-10 | Chris Colvin | Const | 2020-04-16 | Mike Tabbert | 2020-06-02 | Keith Pollock
COP-01 | COP-01 | PI17760 | Verified | Emergency notification system cannot be heard on the Plant North Side of the Cooling Tower when the plant is running | C | E | Chris Colvin | McD | 2020-03-10 | Chris Colvin | Const | 2021-08-15 | Seaney | 2021-08-15 | John Watts
COP-01 | COP-01 | PI17761 | Verified | Emergency notification system cannot be heard in the Demin Building when the plant is running | C | E | Chris Colvin | McD | 2020-03-10 | Chris Colvin | Const | 2021-08-15 | Seaney | 2021-08-15 | John Watts
IAS-05 | IAS-05 | PI01550 | Verified | ISO 10-IAS-PD-P41-0505-01 pipe spool PS-10-IAS-P41-0505-01-511-1 & PS-10-IAS-P41-0505-01-511-2 not installed | A | P | Terry Deaton | McD | 2019-06-26 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01551 | Verified | ISO 10-IAS-PD-P41-0505-02 is not installed | A | P | Terry Deaton | McD | 2019-06-26 | Terry Deaton | Const | 2019-08-01 | Terry Deaton | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01552 | Verified | On ISO 10-IAS-PD-P41-0506-01 threaded cap not installed | A | P | Terry Deaton | McD | 2019-06-26 | Terry Deaton | Const | 2019-07-19 | Terry Deaton | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01553 | Verified | On ISO 10-IAS-PD-P41-0506-01 pipe support 10-IAS-PD-HGR-0655 2 anchor bolts missing | A | P | Terry Deaton | McD | 2019-06-26 | Terry Deaton | Const | 2019-06-28 | Terry Deaton | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01554 | Verified | On ISO 10-IAS-PD-P41-0515-01 pipe support 10-IAS-PD-HGR-0682 is not installed | A | P | Terry Deaton | McD | 2019-06-26 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-07-26 | Kelvin Cook
IAS-05 | IAS-05 | PI01555 | Verified | On ISO 10-IAS-PD-P41-0515-01 pipe spool PS-10-IAS-P41-0515-01-531-1 & 2 are not installed | A | P | Terry Deaton | McD | 2019-06-26 | Terry Deaton | Const | 2019-07-26 | Terry Deaton | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01556 | Verified | ISO 10-IAS-PD-P41-0515-02 is not installed | A | P | Terry Deaton | McD | 2019-06-26 | Terry Deaton | Const | 2019-08-02 | Terry Deaton | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01557 | Verified | ISO 10-IAS-PD-P41-0515-03 is not installed | A | P | Terry Deaton | McD | 2019-06-26 | Terry Deaton | Const | 2019-08-03 | Terry Deaton | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01558 | Verified | ISO 10-IAS-PD-P41-0515-04 Spools 0515-05, 04, 03, 02, 01 is not installed | A | P | Terry Deaton | McD | 2019-06-26 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-27 | Kelvin Cook
IAS-05 | IAS-05 | PI01559 | Verified | ISO 10-IAS-PD-P41-0525-01 pipe spool is PS-10-IAS-P41-0525-01-531-4 is not installed | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-07-26 | Kelvin Cook
IAS-05 | IAS-05 | PI01560 | Verified | ISO 10-IAS-PD-P41-0525-02 pipe support 10-IAS-PD-HGR-0713 ss wrap & worm clamp. U bolt or not? | B | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-07-26 | Kelvin Cook
IAS-05 | IAS-05 | PI01561 | Verified | ISO 10-IAS-PD-P41-0525-03 pipe support 10-IAS-PD-HGR-0719 worm gear clamp is missing | B | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01562 | Verified | ISO 10-IAS-PD-P41-0525-03 pipe support 10-IAS-PD-HGR-0718 worm gear clamp is missing | B | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01563 | Verified | ISO 10-IAS-PD-P41-0525-03 pipe support 10-IAS-PD-HGR-0718 Center ss wrap on support | B | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-07-26 | Kelvin Cook
IAS-05 | IAS-05 | PI01564 | Verified | ISO 10-IAS-PD-P41-0525-03 pipe support 10-IAS-PD-HGR-0716 ss worm clamp missing | B | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01565 | Verified | ISO 10-IAS-PD-P41-0525-04 pipe support 10-IAS-PD-HGR-0707 missing clamp | B | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01566 | Verified | ISO 10-IAS-PD-P41-0525-04 pipe support 10-IAS-PD-HGR-0704 missing clamp | B | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01567 | Verified | ISO 10-IAS-PD-P41-0525-04 pipe support 10-IAS-PD-HGR-0703 missing clamp | B | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01568 | Verified | ISO 10-IAS-PD-P41-0525-05 pipe support 10-IAS-PD-HGR-0708 not installed | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-07-26 | Kelvin Cook
IAS-05 | IAS-05 | PI01569 | Verified | ISO 10-IAS-PD-P41-0525-05 pipe support 10-IAS-PD-HGR-0709 not installed | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-07-26 | Kelvin Cook
IAS-05 | IAS-05 | PI01570 | Verified | ISO 10-IAS-PD-P41-0530-01 pipe spool PS-10-IAS-P41-0530-01-531-2 is not installed | B | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-07-19 | Damon Turner | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01571 | Verified | ISO 10-IAS-PD-P41-0530-02 is not installed | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01572 | Verified | ISO 10-IAS-PD-P41-0564-01 pipe support 10-IAS-PD-HGR-0710 & 0711 ss wrap & clamp and ubolt missing | B | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-06-28 | Damon Turner | 2019-08-14 | Kelvin Cook
IAS-05 | IAS-05 | PI01573 | Verified | ISO 10-IAS-PD-P41-0505-01 needs supports engineering to resolve | B | P | Tim Gallegos | McD | 2019-06-26 | Tim Gallegos | Const | 2019-07-22 | Tim Gallegos | 2019-07-22 | Kelvin Cook
IAS-05 | IAS-05 | PI01574 | Verified | ISO 10-IAS-PD-P41-0505-02 needs supports engineering to resolve | B | P | Tim Gallegos | McD | 2019-06-26 | Tim Gallegos | Const | 2019-07-22 | Tim Gallegos | 2019-07-22 | Kelvin Cook
IAS-05 | IAS-05 | PI01575 | Verified | ISO 10-IAS-PD-P41-0530-01 at wall penetration elevation bust with pipe & tray on support go from 36" to 24" | B | P | Kelvin Cook | McD | 2019-06-26 | Kelvin Cook | Const | 2019-07-19 | Kelvin Cook | 2019-07-19 | Kelvin Cook
IAS-05 | IAS-05 | PI01583 | Verified | Tighten bottom bolt on valve 10-IAS-V-0525. Northeast corner inside water treatment bldg. | A | P | Damon Turner | McD | 2019-06-26 | Damon Turner | Const | 2019-07-10 | Damon Turner | 2019-07-26 | Blake Boudreaux
IAS-05 | IAS-05 | PI02497 | Verified | LK-10-IAS-PD-P41-0505-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-08-02 | Terry Deaton | 2019-08-02 | Tom Noble
IAS-05 | IAS-05 | PI02498 | Verified | LK-10-IAS-PD-P41-0515-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
IAS-05 | IAS-05 | PI02499 | Verified | LK-10-IAS-PD-P41-0515-04 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
IAS-05 | IAS-05 | PI02500 | Verified | LK-10-IAS-PD-P41-0525-04 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
IAS-05 | IAS-05 | PI02501 | Verified | LK-10-IAS-PD-P41-0530-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
IAS-05 | IAS-05 | PI02502 | Verified | LK-10-IAS-PD-P41-0530-02 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-08-06 | Terry Deaton | 2019-08-06 | Tom Noble
IAS-05 | IAS-05 | PI02503 | Verified | LK-10-IAS-PD-P41-0564-01 - Need Welds Cleared | A | P | Terry Deaton | McD | 2019-07-22 | Terry Deaton | Const | 2019-08-07 | Tom Noble | 2019-08-07 | Tom Noble
IAS-05 | IAS-05 | PI03824 | Verified | Complete pipe test & submit CCFs to turnover. | A | P | Terry Deaton | McD | 2019-08-13 | Terry Deaton | Const | 2019-08-27 | Kelvin Cook | 2019-08-27 | Ed Gober
IAS-05 | IAS-05 | PI04326 | Verified | On ISO 10-IAS-PD-P41-0515-04 pipe support 10-IAS-PD-HGR-0676 & 0677 are not installed. | B | P | Damon Turner | McD | 2019-08-19 | Damon Turner | Const | 2019-09-05 | Damon Turner | 2019-09-18 | Kelvin Cook
IAS-05 | IAS-05 | PI04327 | Verified | On ISO 10-IAS-PD-P41-0515-04 install two supports per Eng detail. | A | P | Terry Deaton | McD | 2019-08-19 | Terry Deaton | Const | 2019-08-21 | Damon Turner | 2019-08-27 | Kelvin Cook
IAS-05 | IAS-05 | PI04328 | Verified | On ISO 10-IAS-PD-P41-0515-04 pipe support 10-IAS-PD-HGR-0678 and 0679 install ss wrap and clamp. | B | P | Terry Deaton | McD | 2019-08-19 | Terry Deaton | Const | 2019-08-20 | Terry Deaton | 2019-08-20 | Kelvin Cook
IAS-05 | IAS-05 | PI04329 | Verified | On ISO 10-IAS-PD-P41-0530-02 install supports steel per the detail. | B | P | Damon Turner | McD | 2019-08-19 | Damon Turner | Const | 2019-09-05 | Damon Turner | 2019-09-18 | Kelvin Cook
IAS-05 | IAS-05 | PI04665 | Verified | Tag all valves | C | P | Tim Green | McD | 2019-08-28 | Tim Green | Const | 2021-01-22 | Eric Policarpio | 2021-01-22 | Eric Policarpio
IAS-05 | IAS-05 | PI09679 | Verified | Seal instrument air piping penetration at North wall of Demin Water Building, Line No.2-10-IAS-0525 | C | P | Bobby Williams | McD | 2019-10-16 | Bobby Williams | Comm | 2020-03-18 | Bobby Williams | 2020-04-08 | Bernard Stasse
IAS-05 | IAS-05 | PI09680 | Verified | Tag all system components - duplicate punch please see PI04665 EP 2/4 | C | P | James Beech | McD | 2019-10-16 | James Beech | Comm | 2020-02-04 | Eric Policarpio | 2020-03-09 | Dave Goldak
IAS-05 | IAS-05 | PI09681 | Verified | Remove all tape, tie-wraps, rope, wire from system piping | C | P | James Beech | McD | 2019-10-16 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-05 | IAS-05 | PI09682 | Verified | Loose bolts on 10-IAS-V-0525; Demin Water Bldg Instrument Air Header 2" isolation valve, Line No. 2-10-IAS-0525 | C | P | James Beech | McD | 2019-10-16 | James Beech | Comm | 2020-01-02 | Billy Williams | 2020-01-10 | Blake Boudreaux
IAS-05 | IAS-05 | PI09683 | Verified | Instrument Air Line No. 2-10-IAS-0525 is rubbing on Demin Water Line No. 2-10-WTD-0310, to UF/RO CIP Storage Tank | C | P | James Beech | McD | 2019-10-16 | James Beech | Comm | 2020-01-07 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-05 | IAS-05 | PI09684 | Verified | Instrument Air Line No. 2-10-IAS-0530 needs support, Instrument Air supply to Waste Water Treatment Area | C | P | James Beech | McD | 2019-10-16 | James Beech | Comm | 2020-02-04 | James Beech | 2020-04-08 | Bernard Stasse
IAS-05 | IAS-05 | PI09685 | Verified | Bolts missing and valve handle bent at 10-IAS-V-0250; .75 inch Instrument Air supply to RWS Area Oily Water Sump Pump | C | P | James Beech | McD | 2019-10-16 | James Beech | Comm | 2020-01-02 | Bobby Williams | 2020-01-10 | Blake Boudreaux
IAS-05 | IAS-05 | PI09686 | Verified | No access to 10-IAS-V-0516; .75" Instrument Air supply to Clarifier Polymer Blender | D | S | Michael Law | McD | 2019-10-16 | Michael Law | Comm | 2020-04-16 | Michael Law | 2020-04-16 | Keith Pollock
MWS-02 | MWS-02 | PI06107 | Verified | LK-10-SWS-PD-P41-0333-01 - Needs Welds Cleared | A | P | James Beech | McD | 2019-09-13 | James Beech | Const |  |  | 2019-10-10 | Tom Noble
MWS-02 | MWS-02 | PI06108 | Verified | LK-10-SWS-PD-P41-0333-02 - Needs Welds Cleared | A | P | James Beech | McD | 2019-09-13 | James Beech | Const |  |  | 2020-01-28 | Tom Noble
MWS-02 | MWS-02 | PI06110 | Verified | LK-10-SWS-PD-P41-0375-01 - Needs Welds Cleared | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-09 | Tom Noble | 2019-10-09 | Tom Noble
MWS-02 | MWS-02 | PI06111 | Verified | LK-10-SWS-PD-P41-0376-01 - Needs Welds Cleared | A | P | James Beech | McD | 2019-09-13 | James Beech | Const | 2019-10-09 | Tom Noble | 2019-10-09 | Tom Noble
MWS-02 | MWS-02 | PI02639 | Verified | LK-10-SAS-PD-P41-0218-01 - Need Welds Cleared | A | P | Bobby Williams | McD | 2019-07-23 | Bobby Williams | Const | 2019-10-09 | Tom Noble | 2019-10-09 | Tom Noble
MWS-02 | MWS-02 | PI04893 | Verified | ISO 10-SAS-PD-P41-0218-01 is not installed | A | P | Bobby Williams | McD | 2019-09-10 | Bobby Williams | Const | 2019-10-30 | Bobby Williams | 2019-12-06 | Kelvin Cook
MWS-02 | MWS-02 | PI04894 | Verified | ISO 10-SAS-PD-P41-0219-01 is not installed | A | P | Bobby Williams | McD | 2019-09-10 | Bobby Williams | Const | 2019-10-30 | Bobby Williams | 2019-12-15 | Kelvin Cook
MWS-02 | MWS-02 | PI04895 | Verified | ISO 10-SAS-PD-P41-0219-02 is not installed | A | P | Bobby Williams | McD | 2019-09-10 | Bobby Williams | Const | 2019-10-30 | Bobby Williams | 2019-12-06 | Kelvin Cook
MWS-02 | MWS-02 | PI02640 | Verified | LK-10-SAS-PD-P41-0219-02 - Need Welds Cleared | A | P | James Beech | McD | 2019-07-23 | James Beech | Const | 2019-09-05 | Damon Turner | 2019-10-10 | Tom Noble
MWS-02 | MWS-02 | PI07325 | Verified | ISO 10-MWS-PD-P40-0144-01 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI07326 | Verified | ISO 10-MWS-PD-P40-0144-02 is not intalled | A | P | James Beech | McD | 2019-09-27 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI05149 | Verified | At Filter Press area - complete all installation. | B | P | James Beech | McD | 2019-09-12 | James Beech | Const |  |  | 2019-11-23 | Kelvin Cook
MWS-02 | MWS-02 | PI09283 | Verified | 10MWSX0156, From Termination | A | E | Chris Colvin | McD | 2019-10-08 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI09311 | Verified | 10MWSX0156, To Termination | A | E | Chris Colvin | McD | 2019-10-08 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI08276 | Verified | 10NJSL0014A, From Termination | A | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI08277 | Verified | 10NJSL0014B, From Termination | A | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI08278 | Verified | 10NJSL0014C, From Termination | A | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI08279 | Verified | 10NJSL0014G, From Termination | A | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI08291 | Verified | 10NJSL0014A, To Termination | A | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI08292 | Verified | 10NJSL0014B, To Termination | A | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI08293 | Verified | 10NJSL0014C, To Termination | A | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI08294 | Verified | 10NJSL0014G, To Termination | A | E | Chris Colvin | McD | 2019-10-01 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI12868 | Verified | 10-SWS-PD-P41-0333-02 install valves 10-SWS-V-0335 and 0336 | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12869 | Verified | 10-MWS--PD-P40-0144-01 install isolation kit | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12870 | Verified | 10-MWS--PD-P40-0144-02 install isolation kit | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12871 | Verified | 10-MWS--PD-P40-1010-04 install isolation kit | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12872 | Verified | 10-MWS--PD-P40-1010-05 install isolation kit | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Al Canniff | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12873 | Verified | 10-MWS--PD-P40-1010-08 install isolation kit | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12874 | Verified | 10-MWS--PD-P40-1015-01 install isolation kit | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12875 | Verified | 10-MWS-PD-P41-1200-01 install 10-MWS-V-1200 | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12876 | Verified | 10-MWS-PD-P41-1300-01 install 10-MWS-V-1300 | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12877 | Verified | 10-MWS-PD-P41-1305-01 install 10-MWS-V-1305 | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Gallegos | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12878 | Verified | 10-MWS-PD-P41-1402-01 install 10-MWS-V-1403 | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12879 | Verified | 10-MWS-PD-P41-1406-01 install 10-MWS-V-1406A | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12880 | Verified | 10-MWS-PD-P41-1406-02 install 10-MWS-V-1407 | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12881 | Verified | 10-MWS-PD-P41-1408-01 install 10-MWS-V-1408 | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2020-01-13 | Tim Green | 2020-01-14 | Ethan Byrd
MWS-02 | MWS-02 | PI12882 | Verified | 10-MWS-PD-P41-1205-01 install 10-MWS-V-1206 | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12883 | Verified | 10-MWS-PD-P41-1205-01 install 10-MWS-V-1207 | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2019-12-30 | Tim Green | 2019-12-31 | Kelvin Cook
MWS-02 | MWS-02 | PI12884 | Verified | 10-MWS-PD-P41-1205-01 install 10-MWS-CHK-1206 | A | P | James Beech | McD | 2019-11-11 | James Beech | Const | 2020-01-13 | Tim Green | 2020-01-14 | Ethan Byrd
MWS-02 | MWS-02 | PI13879 | Verified | 1B-MWS-PI-1089 - replace gauge with silicone filled diaphragm gauge combo. | B | I | Gonzalo Pena | McD | 2019-12-03 | Gonzalo Pena | Comm | 2020-03-09 | Tim Green | 2020-03-09 | Michael Law
MWS-02 | MWS-02 | PI15237 | Verified | 10-NJS-PNL-0009; Filter Press 480V Panelboard not installed | C | E | Chris Colvin | McD | 2020-01-06 | Chris Colvin | Comm |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15365 | Verified | Tag all valves. | C | P | James Beech | McD | 2020-01-07 | James Beech | Const | 2020-04-28 | Michael Law | 2020-04-28 | Michael Law
MWS-02 | MWS-02 | PI15366 | Verified | Tag all equipment. | C | M | Shane Crowe | McD | 2020-01-07 | Shane Crowe | Const | 2020-01-15 | Shane Crowe | 2020-01-24 | Kelvin Cook
MWS-02 | MWS-02 | PI15367 | Verified | Secure Filter Press trough. | A | M | Shane Crowe | McD | 2020-01-07 | Shane Crowe | Const | 2020-01-15 | Shane Crowe | 2020-01-20 | Shane Crowe
MWS-02 | MWS-02 | PI15368 | Verified | Grout all supports. | C | C | Alan Huntsman | McD | 2020-01-07 | Alan Huntsman | Const | 2020-03-18 | Johnny Campbell | 2020-04-02 | Michael Law
MWS-02 | MWS-02 | PI15369 | Verified | Install Polymer Totes 10-MWS-T-1250 and 10-MWS-T-1350 and flex hoses. | B | M | William Mitchell | McD | 2020-01-07 | William Mitchell | Comm |  |  | 2020-01-30 | Michael Law
MWS-02 | MWS-02 | PI15370 | Verified | Clean couplings on pumps 10-MWS-P-1040A and 1040B. | A | M | Shane Crowe | McD | 2020-01-07 | Shane Crowe | Const | 2020-01-15 | Shane Crowe | 2020-01-20 | Shane Crowe
MWS-02 | MWS-02 | PI15371 | Verified | Perform clean & close on 10-MWS-THK-1000. | A | M | Shane Crowe | McD | 2020-01-07 | Shane Crowe | Const | 2020-01-29 | Alan Huntsman | 2020-01-29 | Shane Crowe
MWS-02 | MWS-02 | PI15373 | Verified | 10-MWS-PD-P40-1010-04: Modify the grating to a 1" opening around the pipe and install toe plate. | C | S | Bobby Williams | McD | 2020-01-07 | Bobby Williams | Const | 2020-02-19 | Bobby Williams | 2020-02-19 | Michael Law
MWS-02 | MWS-02 | PI15374 | Verified | 10-MWS-PD-P40-1010-05: Modify the grating to a 1" opening around both pipes and install toe plate. | C | S | Bobby Williams | McD | 2020-01-07 | Bobby Williams | Const | 2020-02-19 | Bobby Williams | 2020-02-19 | Michael Law
MWS-02 | MWS-02 | PI15375 | Verified | 10-MWS-PD-P40-1014-01: Modify the grating to a 1" opening around the pipe and install toe plate. | C | S | Bobby Williams | McD | 2020-01-07 | Bobby Williams | Const | 2020-02-19 | Bobby Williams | 2020-02-19 | Michael Law
MWS-02 | MWS-02 | PI15376 | Verified | 10-MWS-PD-P41-1333-01: 10-MWS-PCV-1336 not installed. | A | P | James Beech | McD | 2020-01-07 | James Beech | Const |  |  | 2020-01-29 | Kelvin Cook
MWS-02 | MWS-02 | PI15377 | Verified | 10-MWS-PD-P41-1400-01: Enlarge pipe penetration at 10-MWS-SKD-1400B. Pipe is currently rubbing against equipment. | B | P | James Beech | McD | 2020-01-07 | James Beech | Const | 2020-01-13 | Tim Green | 2020-01-20 | Ethan Byrd
MWS-02 | MWS-02 | PI15378 | Verified | 10-MWS-PD-P41-1478-07: Modify the grating to a 1" opening around the pipe and install toe plate. | C | S | Bobby Williams | McD | 2020-01-07 | Bobby Williams | Const | 2020-02-19 | Bobby Williams | 2020-02-19 | Michael Law
MWS-02 | MWS-02 | PI15379 | Verified | Touch up paint required inside 10-MWS-THK-1000. | A | X | Jorge Alexander | McD | 2020-01-07 | Jorge Alexander | Const | 2020-01-29 | Alan Huntsman | 2020-01-29 | Shane Crowe
MWS-02 | MWS-02 | PI15862 | Verified | 10-MWS-FIT-1102 - attach bonding grounds on each side. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15863 | Verified | 10-MWS-FIT-1102 - label wires inside transmitter. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15864 | Verified | Wrap cable guards on cables for 10-MWS-M-1100A & at entry to sump. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15865 | Verified | Need a 6" dropout for cables from 10-MWS-JB-1100 to the gutter tray. | B | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const | 2020-02-27 | Fred Michael | 2020-03-02 | Mike Tabbert
MWS-02 | MWS-02 | PI15866 | Verified | Seal conduits at 10-MWS-JB-1100. | B | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-09 | Mike Tabbert
MWS-02 | MWS-02 | PI15867 | Verified | Cable tray to the 1100 sump needs cable tray number. | B | E | Chris Caywood | McD | 2020-01-10 | Chris Caywood | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15868 | Verified | Need receptacle for plug for 10-MWS-SV-1415. | B | E | Mike Tabbert | McD | 2020-01-10 | Mike Tabbert | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15869 | Verified | 10-MWS-CP-0002 - needs ground. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15870 | Verified | 10-MWS-CP-0002 - seal conduits. | B | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const | 2020-03-07 | Matt Gilmore | 2020-03-09 | Mike Tabbert
MWS-02 | MWS-02 | PI15871 | Verified | Tag all components. | C | I | Gonzalo Pena | McD | 2020-01-10 | Gonzalo Pena | Const | 2020-01-15 | Gonzalo Pena | 2020-01-22 | Michael Law
MWS-02 | MWS-02 | PI15872 | Verified | Ground seal tite on 10-MWS-AOV-1091 on the filter press. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15873 | Verified | 10-MWS-PIT-103 needs ground at the filter press. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15874 | Verified | Label cable tray on the north side of the filter press. | C | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const | 2020-04-16 | Chris Colvin | 2020-04-21 | Mike Tabbert
MWS-02 | MWS-02 | PI15875 | Verified | Complete cable tray grounds at filter press at both ends. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15876 | Verified | Ground the motor on the filter press. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15877 | Verified | Ground the thickener platform. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15878 | Verified | Tag all panels. | C | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15879 | Verified | Ground 10-MWS-JB-1400A. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15880 | Verified | Ground 10-MWS-JB-1400B. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15881 | Verified | Ground 10-MWS-JB-1150. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15882 | Verified | 10-MWS-JB-1400A - label wires. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15883 | Verified | 10-MWS-JB-1400B - label wires. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15884 | Verified | Pour concrete at electrical stub ups on the south side of the polymer skid. | C | C | Alan Huntsman | McD | 2020-01-10 | Alan Huntsman | Const | 2020-03-13 | Johnny Campbell | 2020-03-16 | Mike Tabbert
MWS-02 | MWS-02 | PI15885 | Verified | Attach all grounds at the elec. Stub ups on the south side of the polymer skid. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15886 | Verified | 10-MWS-DRV-1040B - move cables in panel in the top right corner off of sharp edge. | A | E | Chris Colvin | McD | 2020-01-10 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15887 | Verified | Replace tubing for 10-MWS-AOV-1042A. | A | I | Gonzalo Pena | McD | 2020-01-10 | Gonzalo Pena | Const | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
MWS-02 | MWS-02 | PI15888 | Verified | Check all tubing fittings on the filter press feed skid. | A | I | Gonzalo Pena | McD | 2020-01-10 | Gonzalo Pena | Const | 2020-01-13 | Gonzalo Pena | 2020-01-13 | Fred Michael
MWS-02 | MWS-02 | PI15920 | Verified | 10MWSC0102, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15921 | Verified | 10MWSC0103, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15922 | Verified | 10MWSC0105, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15923 | Verified | 10MWSC0106, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15924 | Verified | 10MWSC0108, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15925 | Verified | 10MWSC0110, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15926 | Verified | 10MWSC0116, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15927 | Verified | 10MWSC0117, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15928 | Verified | 10MWSC0118, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15929 | Verified | 10MWSC0120, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15930 | Verified | 10MWSC0121, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15931 | Verified | 10MWSK0054, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15932 | Verified | 10MWSK0057, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-28 | Mike Tabbert
MWS-02 | MWS-02 | PI15933 | Verified | 10MWSK0060, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15934 | Verified | 10MWSK0061, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15935 | Verified | 10MWSK0063, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15936 | Verified | 10MWSK0068, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15937 | Verified | 10MWSK0073, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15938 | Verified | 10MWSK0074, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15939 | Verified | 10MWSK0075, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15940 | Verified | 10MWSK0076, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15941 | Verified | 10MWSK0077, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15942 | Verified | 10MWSK0081, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI15943 | Verified | 10MWSK0085, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI15944 | Verified | 10MWSK0091, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15945 | Verified | 10MWSK0094, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI15946 | Verified | 10MWSK0095, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15947 | Verified | 10MWSK0096, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI15948 | Verified | 10MWSK0097, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI15949 | Verified | 10MWSK0122, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15950 | Verified | 10MWSK2001, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15951 | Verified | 10MWSL0003A, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15952 | Verified | 10MWSL0003B, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15953 | Verified | 10MWSL0003C, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15954 | Verified | 10MWSL0003G, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15955 | Verified | 10MWSL0004A, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15956 | Verified | 10MWSL0004B, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15957 | Verified | 10MWSL0004C, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15958 | Verified | 10MWSL0004G, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15959 | Verified | 10MWSL0005A, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15960 | Verified | 10MWSL0005B, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15961 | Verified | 10MWSL0005C, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15962 | Verified | 10MWSL0005G, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15963 | Verified | 10MWSL0006A, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15964 | Verified | 10MWSL0006B, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15965 | Verified | 10MWSL0006C, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15966 | Verified | 10MWSL0006G, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15967 | Verified | 10MWSL0006N, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15968 | Verified | 10MWSX0108, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI15969 | Verified | 10MWSX0120, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15970 | Verified | 10MWSX0130, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15971 | Verified | 10MWSX0131, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI15972 | Verified | 10MWSX0132, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15973 | Verified | 10MWSX0148, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15974 | Verified | 10MWSX0149, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI15975 | Verified | 10MWSX0156, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15976 | Verified | 10NJSL0014A, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-28 | Mike Tabbert
MWS-02 | MWS-02 | PI15977 | Verified | 10NJSL0014B, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI15978 | Verified | 10NJSL0014C, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI15979 | Verified | 10NJSL0014G, From termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI15980 | Verified | 10MWSC0066, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15981 | Verified | 10MWSC0067, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15982 | Verified | 10MWSC0102, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI15983 | Verified | 10MWSC0103, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI15984 | Verified | 10MWSC0104, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-20 | Fred Michael
MWS-02 | MWS-02 | PI15985 | Verified | 10MWSC0105, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI15986 | Verified | 10MWSC0106, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI15987 | Verified | 10MWSC0107, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI15988 | Verified | 10MWSC0108, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-02-13 | Mike Tabbert
MWS-02 | MWS-02 | PI15989 | Verified | 10MWSC0110, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-02-13 | Mike Tabbert
MWS-02 | MWS-02 | PI15990 | Verified | 10MWSC0116, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15991 | Verified | 10MWSC0117, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15992 | Verified | 10MWSC0118, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI15993 | Verified | 10MWSC0120, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI15994 | Verified | 10MWSK0054, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI15995 | Verified | 10MWSK0060, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI15996 | Verified | 10MWSK0061, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI15997 | Verified | 10MWSK0063, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI15998 | Verified | 10MWSK0068, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-24 | Mike Tabbert
MWS-02 | MWS-02 | PI15999 | Verified | 10MWSK0074, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI16000 | Verified | 10MWSK0075, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI16001 | Verified | 10MWSK0076, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI16002 | Verified | 10MWSK0081, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI16003 | Verified | 10MWSK0085, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI16004 | Verified | 10MWSK0091, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI16005 | Verified | 10MWSK0094, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI16006 | Verified | 10MWSK0095, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI16007 | Verified | 10MWSK0096, To Termination | B | E | Mike Tabbert | McD | 2020-01-13 | Mike Tabbert | Const | 2020-02-26 | Mike Tabbert | 2020-02-26 | Mike Tabbert
MWS-02 | MWS-02 | PI16008 | Verified | 10MWSK0097, To Termination | B | E | Mike Tabbert | McD | 2020-01-13 | Mike Tabbert | Const | 2020-02-26 | Mike Tabbert | 2020-02-26 | Mike Tabbert
MWS-02 | MWS-02 | PI16009 | Verified | 10MWSK0122, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI16010 | Verified | 10MWSK2001, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI16011 | Verified | 10MWSL0006A, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI16012 | Verified | 10MWSL0006B, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI16013 | Verified | 10MWSL0006C, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI16014 | Verified | 10MWSL0006G, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI16015 | Verified | 10MWSL0006N, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI16016 | Verified | 10MWSX0108, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI16017 | Verified | 10MWSX0129, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI16018 | Verified | 10MWSX0131, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Chris Colvin | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI16019 | Verified | 10MWSX0134, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-17 | Mike Tabbert
MWS-02 | MWS-02 | PI16020 | Verified | 10MWSX0135, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI16021 | Verified | 10MWSX0148, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI16022 | Verified | 10MWSX0149, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-15 | Mike Tabbert
MWS-02 | MWS-02 | PI16023 | Verified | 10MWSX0156, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-27 | Mike Tabbert
MWS-02 | MWS-02 | PI16024 | Verified | 10NJSL0014A, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-24 | Mike Tabbert
MWS-02 | MWS-02 | PI16025 | Verified | 10NJSL0014B, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-24 | Mike Tabbert
MWS-02 | MWS-02 | PI16026 | Verified | 10NJSL0014C, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-24 | Mike Tabbert
MWS-02 | MWS-02 | PI16027 | Verified | 10NJSL0014G, To Termination | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const |  |  | 2020-01-24 | Mike Tabbert
MWS-02 | MWS-02 | PI16028 | Verified | Install MCC Bucket for 10-MWS-JB-1400A | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Mike Tabbert | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI16029 | Verified | Install MCC Bucket for 10-MWS-JB-1400B | A | E | Chris Colvin | McD | 2020-01-13 | Chris Colvin | Const | 2020-01-21 | Mike Tabbert | 2020-01-22 | Mike Tabbert
MWS-02 | MWS-02 | PI17135 | Verified | 10-MWS-H-1150; Filter Press Polymer Injection Water Heater Panel needs label | C | E | Chris Colvin | McD | 2020-02-22 | Chris Colvin | Comm | 2020-04-22 | Matt Gilmore | 2020-08-17 | Dave Goldak
MWS-02 | MWS-02 | PI17136 | Verified | 10-MWS-H-1150; Filter Press Polymer Injection Water Heater Panel Temperature Control Indicator is not working | B | E | Jonathan Donham | McD | 2020-02-22 | Jonathan Donham | Comm | 2020-03-02 | Jonathan Donham | 2020-03-05 | Nelson Eichelberger
MWS-02 | MWS-02 | PI17137 | Verified | 10-MWS-P-1200 A&B; Thickener Emulsion Polymer Pumps .5 inch suction line needs additional support | C | P | James Beech | McD | 2020-02-22 | James Beech | Comm | 2020-05-05 | James Beech | 2021-05-24 | Keith Pollock
MWS-02 | MWS-02 | PI17138 | Verified | 10-MWS-P-1200 A&B; Thickener Emulsion Polymer Pumps .5 inch discharge line needs additional support | C | P | James Beech | McD | 2020-02-22 | James Beech | Comm | 2020-05-05 | James Beech | 2021-05-24 | Keith Pollock
MWS-02 | MWS-02 | PI17139 | Verified | Clean up Thickener Emulsion Polymer Pump skid | C | C | Alan Huntsman | McD | 2020-02-22 | Alan Huntsman | Comm | 2020-03-13 | Johnny Campbell | 2020-08-17 | Dave Goldak
MWS-02 | MWS-02 | PI17140 | Verified | Missing switch at 10-MWS-CP-1200; Thickener Emulsion Polymer Makedown System Control Panel | B | E | Mike Tabbert | McD | 2020-02-22 | Mike Tabbert | Comm | 2020-03-25 | Mike Tabbert | 2021-04-26 | Keith Pollock
MWS-02 | MWS-02 | PI17142 | Verified | Align Filter Press building rain gutters to drains | C | C | Sheri Fritz | MOO | 2020-02-22 | Sheri Fritz | Comm | 2020-03-04 | Dave Goldak | 2020-03-04 | Dave Goldak
MWS-02 | MWS-02 | PI17143 | Verified | Filter Press Roll Off Box curb needs to be extended 3 feet to the West, currently dumpster does not extend far enough West to catch all filter press cake when released | C | C | Brooks Baker | McD | 2020-02-22 | Brooks Baker | Comm | 2020-07-16 | Brooks Baker | 2020-08-17 | Dave Goldak
MWS-02 | MWS-02 | PI17144 | Verified | Finish roof for Air Compressor and Thickener Emulsion Polymer Pump building | C | C | Sheri Fritz | MOO | 2020-02-22 | Sheri Fritz | Comm | 2020-03-04 | Dave Goldak | 2020-03-04 | Dave Goldak
MWS-02 | MWS-02 | PI17145 | Verified | Reinstall coupling guard at 10-MWS-P-1040A; Filter Press Feed Pump A | B | M | William Mitchell | McD | 2020-02-22 | William Mitchell | Comm | 2020-03-17 | William Mitchell | 2020-07-28 | Keith Pollock
MWS-02 | MWS-02 | PI17146 | Verified | Reinstall coupling guard at 10-MWS-P-1040B; Filter Press Feed Pump B | B | M | William Mitchell | McD | 2020-02-22 | William Mitchell | Comm | 2020-03-17 | William Mitchell | 2020-07-28 | Keith Pollock
MWS-02 | MWS-02 | PI17147 | Verified | Check 10-MWS-DRY-1440b; Filter Press Air Dryer operation, dessicant needs to be changed | C | M | William Mitchell | McD | 2020-02-22 | William Mitchell | Comm | 2020-04-20 | William Mitchell | 2021-06-17 | John Watts
MWS-02 | MWS-02 | PI17148 | Verified | Need 90 on Sludge Thickener sample lines at West side of tank | D | P | Charles Worthington | McD | 2020-02-22 | Charles Worthington | Comm | 2020-04-16 | Keith Pollock | 2020-04-16 | Keith Pollock
MWS-02 | MWS-02 | PI18104 | Verified | The 2 filtrate sump pumps located at the filter press need to have shaft guarding put in place around packing gland area. Install shaft guards | C | M | Shane Crowe | McD | 2020-03-19 | Shane Crowe | Comm | 2020-03-27 | Shane Crowe | 2020-03-31 | John Watts
MWS-02 | MWS-02 | PI18141 | Verified | 10-MWS-FLT-1080 - Filter Press cannot be operated properly. It's inconsistent and not producing solid cake. | C | M | William Mitchell | McD | 2020-03-20 | William Mitchell | Comm | 2020-04-20 | William Mitchell | 2021-02-01 | Dave Goldak
MWS-02 | MWS-02 | PI18199 | Verified | Veolia Commissioning Field Service Report to submit | C | M | William Mitchell | McD | 2020-03-30 | William Mitchell | Comm | 2020-04-23 | William Mitchell | 2020-04-23 | Eric Policarpio
MWS-02 | MWS-02 | PI18263 | Verified | The filter press needs to have machine caurding installed at each corner of the press to prevent personnel from bypassing the PSD (light curtain) interlock. This is a requirement by OSHA when utilizing PSD devices as a gaurding mechanism. | D | C | Charles Worthington | McD | 2020-05-06 | Charles Worthington | Const | 2020-07-22 | Bryan Sturgies | 2020-11-17 | Dave Goldak
MWS-02 | MWS-02 | PI18264 | Verified | On the filter press west side, when the dump door is open there is a significant gap that a person could inadvertantly fall into. Recommend extending the grating approximately 18 inchesto close the gap when the dump doors are open. | D | C | Charles Worthington | McD | 2020-05-06 | Charles Worthington | Const | 2020-07-22 | Bryan Sturgies | 2020-11-17 | Dave Goldak
ZZZ-01 | ZZZ-01 | PI04608 | Verified | Install End Of Line Resistors in the Main PDC. | B | E | Mike Tabbert | McD | 2019-08-24 | Mike Tabbert | Const | 2019-08-29 | Mike Tabbert | 2019-09-04 | Logan Holland
ZZZ-01 | ZZZ-01 | PI15102 | Verified | 10-ZZZ-QE-0001; Weather Station Precipitation Sensor not installed, outside Main PDC, North end | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-29 | Jared Stimpson | 2020-02-05 | Shannon Scott
ZZZ-01 | ZZZ-01 | PI15103 | Verified | Short hold down anchors at Weather Station instrument stanchion base plate, outside of Main PDC, North end | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-04-14 | Chris Colvin | 2020-08-10 | Nelson Eichelberger
ZZZ-01 | ZZZ-01 | PI15104 | Verified | Weather Station instrumentation tags are hanging together on instrument rack, need to be hung from instrumentation | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-29 | Jared Stimpson | 2020-02-05 | Shannon Scott
ZZZ-01 | ZZZ-01 | PI15105 | Verified | 10-ZZZ-AT-0001; Weather Station Humidity Transmitter needs tag, outside of Main PDC, North end | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-03-07 | Matt Gilmore | 2020-04-07 | Bernard Stasse
ZZZ-01 | ZZZ-01 | PI15106 | Verified | 10-ZZZ-TIT-0001; Weather Station Ambient Temperature Transmitter needs tag, also available tag labeled as PIT, outside of Main PDC, North end | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-29 | Jared Stimpson | 2020-02-07 | Shannon Scott
ZZZ-01 | ZZZ-01 | PI15107 | Verified | 10-ZZZ-PT-0001; Weather Station Atmospheric Pressure Transmitter needs tag, outside of Main PDC, North end | B | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-01-29 | Jared Stimpson | 2020-02-05 | Shannon Scott
ZZZ-01 | ZZZ-01 | PI15108 | Verified | Need phenolic label for tag no. 1A-ZZZ-CP-0001; Satellite Clock Panel, Northwest side of GT A Control Package | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-02-27 | Fred Michael | 2020-04-07 | Bernard Stasse
ZZZ-01 | ZZZ-01 | PI15109 | Verified | Need phenolic label for tag no. 1B-ZZZ-CP-0001; Satellite Clock Panel, Northwest side of GT A Control Package | C | E | Chris Colvin | McD | 2020-01-02 | Chris Colvin | Comm | 2020-04-16 | Chris Colvin | 2020-10-06 | Dave Goldak
INSUL-01 | INSUL-01 | PI18687 | Verified | 1-1 1B-MSS-V-8128, Valve body not insulated | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18688 | Verified | 1-2 1B-MSS-V-1137, Valve body not insulated | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18689 | Verified | 1-3 1B-SSS-SRV-0420, Not insulated | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18690 | Verified | 1-4 1B-HRS-PV-8428, Complete insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18691 | Verified | 1-5 1B-SSS-V-8061, Sample tubing insulation not complete | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18692 | Verified | 1-6 1B-CRS-V-8434, Complete line insulation, top of HRSG, south west. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18693 | Verified | 1-7 CCW line complete insulation, top of HRSG, south west. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18694 | Verified | 1-8 1B-FWS-CHK-8117, complete insulation of valve | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18695 | Verified | 1-9 1B-FWS-V-8144, complete insulation of valve | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18696 | Verified | 1-10 1B-FWS-V-8413B, complete tube insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18697 | Verified | 1-11 1B-MSS-JB-8012, drum level water column not insulated, all drum leve columns not insulated | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18698 | Verified | 1-12 1B-MSS-V-8114, Tube bundle not insulated. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18699 | Verified | 1-13 1B-MSS-V-8049, Douple tube bundle not insulated. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18700 | Verified | 1-14 1B-HBH-V-8012, Insulate tube bundle. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18701 | Verified | 1-15 1B-MSS-V-8106, Insulate tube bundle. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18702 | Verified | 1-16 1B-MSS-V-8106, Insulate other end of tubing. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18703 | Verified | 1-17 1B-MSS-V-8032, complete tube bundle insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18704 | Verified | 1-18 1B-HTS-CAB-0311, complete tube splice insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18705 | Verified | 1-19 1B-HBH-SKD-0110, complete line insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18706 | Verified | 1-20 1B-LPS-MOV-8714, complete valve body insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18707 | Verified | 1-21 1B-LPS-V-8223, complete all tube insulation in the area. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18708 | Verified | 1-22 1B-SSS-SRV-0220, top and bottom complete tube insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18709 | Verified | 1-23 1B-LPS-CHK-8711, complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-01 | INSUL-01 | PI18710 | Verified | 1-24 1B-LPS-MOV-8710, complete valve insulation flange. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18711 | Verified | 1-25 1B-SSS-V-8016, missing end cap and complete tube insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-21 | Mike Tabbert | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18712 | Verified | 1-26 1B-MSS-MOV-8014, complete valve insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18713 | Verified | 1-27 1B-IPS-V-8307, complete tube insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18714 | Open | 1-28 1B-IPS-MOV-8311, 1B-IPS-CHK-8308, complete valve insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const
INSUL-01 | INSUL-01 | PI18715 | Verified | 1-29 1B-MBS-V-8904, complete tube insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18716 | Verified | 1-30 1 inch line needs under water drum platform east side. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-21 | Mike Tabbert | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18717 | Verified | 1-31 HP drum level valve complete insulation east side. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18718 | Verified | 1-32 1B-HBH-V-8272, complete tube insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18719 | Verified | 1-33 1B-FWS-V-8214, complete tube insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-21 | Mike Tabbert | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18720 | Verified | 1-34 top of LP drum level column complete tube insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18721 | Verified | 1-35 below LP drum chalk joint. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-21 | Mike Tabbert | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18722 | Verified | 1-36 1B-CNM-V-8524, complete valve insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18723 | Verified | 1-37 1B-CNM-V-8525, complete valve insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18724 | Verified | 1-38 1B-FWS-CHK-8201, complete valve insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-01 | INSUL-01 | PI18725 | Verified | 1-39 1B-LPS-V-8610, complete tube insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18726 | Verified | 1-40 1B-SSS-SRV-0920, complete tube insulation top and bottom | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18727 | Verified | 1-41 1B-FWS-V-8208, Complete valve insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-01 | INSUL-01 | PI18728 | Verified | 1-42 1B-CNM-V-8512, Complete valve insulation flange | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const |  |  | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18729 | Verified | 1-43 1B-FWS-SRV-8205, 90 degree elbow not insulated | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-21 | Mike Tabbert | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18730 | Verified | 1-44 Elbow no cladding below water drum | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18731 | Verified | 1-45 T cladding not complete east side platform | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-21 | Mike Tabbert | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18732 | Verified | 1-46 main steam lower 90 degree elbow complete cladding | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18733 | Verified | 1-47 south west side 3rd platform down tube bundles not insulated | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18734 | Verified | 1-48 complete insulation south west 3rd platform down | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18735 | Verified | 1-49 finger rack, replace temporary insulation with permanent | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18736 | CLeared | 1-50 Ammonia line 4th level up secure blanket and 5th level | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-07-20 | Richard McSpadden | 2021-07-23 | John Watts
INSUL-01 | INSUL-01 | PI18737 | Verified | 1-51 Finish gas train insulation and cap at duct burner skid | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-21 | Mike Tabbert | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18738 | Verified | 1-52 Duct burner gas train flange blankets do not fit | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18739 | Verified | 1-53 Remove heat trace at gas train | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18740 | Verified | 1-54 Complete anti sweat at presure relief valve gas train | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18741 | Verified | 1-55 Complete anti sweat on gas train bypass line | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18742 | Verified | 1-56 install blankets on valves 1B-FGS-V-0263 and 1B-FGS-V-0264 | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18743 | Verified | 1-57 Tape joint line 260 gas train up stream of 0263 | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18744 | Verified | 1-58 Gas train valve 260 blanket to small | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18745 | Verified | 1-59 1B-2110B complete valve insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18746 | Verified | 1-60 1B-MBH04AA711 install end cap, reinstall blanket | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18747 | Verified | 1-61 1B-3831B 1" line complete insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18748 | Verified | 1-62 replace end caps vent from air filter | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18749 | Verified | 1-63 install blanket at flange of turbine enclosure cooling air | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18750 | Verified | 1-64 cooling air line flange, blanket is to small, large flange needs more blanket cooling air filter | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18751 | Verified | 1-65 MBH05AA144 GT cooling air bleed valve needs insulated | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18752 | Verified | 1-66 90 degree elbow needs cladding complete at air cooler. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18753 | Verified | 1-67 1B blow down sump, insulate all tubing | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18754 | Verified | 1-68 1B-MBL-V-0012A needs blanket | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18755 | Verified | 1-69 1B-MBL-V-8808 complete insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18756 | Verified | 1-70 1B-ASF-V-8085 / 84 complete insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18757 | Verified | 1-73 1B-ASF-CHK-8074 complete insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18758 | Verified | 1-72 ground level flange from water drum needs insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18759 | Verified | 1-73 service water connection at ammonia skid insulate tubing, cladding at valve | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18760 | Verified | 1-74 1BHBH05AA101, bypass line needs to be insulated. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18761 | Verified | 1-75 1BMBH05AA101, Valve flange needs insulation completed. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-01 | INSUL-01 | PI18762 | Verified | 1-76 1B-HTS-CAB-0102, Complete tube insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18763 | Verified | 1-77 Calk blankets in area around 1B-HTS-CAB-0307. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18764 | Verified | 1-78 Service water valve west of AFS skid modify insulation so valve will operate. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18765 | Verified | 1-79 Calk valve at potable water 1B-DWS-H-0010. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18766 | Verified | 1-80 Caulk 90 degree elbow phospate skid. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18767 | Verified | 1-81 1B-HRSG-phospate skid complete insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18768 | Verified | 1-82 Complete cladding gas line at 20 foot elevation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18769 | Verified | 1-83 1B-FWS-V-0054A Complete tubing insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18770 | Verified | 1-84 1B-FWS-V-0054A, Complete insulation at flange | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18771 | Verified | 1-85 1B-FWS-V-0055A, Complete insulation at flange | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18772 | Verified | 1-86 1B-FWS-V-0070A, Complete insulation at flange | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18773 | Verified | 1-87 1B-FWS-V-0050B, Complete tubing insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18774 | Verified | 1-88 1B-FWS-PV-0551, Complete tubing insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18775 | Cleared | 1-89 1B-FWS-V-0554, Complete insulation at flange | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-07-20 | Richard McSpadden | 2021-07-23 | John Watts
INSUL-01 | INSUL-01 | PI18776 | Verified | 1-90 1B-FWS-V-0209A, Complete insulation at flange | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18777 | Verified | 1-91A 1B-FWS-V-0209A, Complete insulation on downstream 90 degree elbow. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18778 | Verified | 1-91B 1B-FWS-V-0209B, Complete insulation on downstream 90 degree elbow. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18779 | Verified | 1-92 1B-FWS-V-0209B, Complete insulation on valve body. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18780 | Verified | 1-93 1B-FWS-CHK-0156B, Complete insulation on valve. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18781 | Verified | 1-94 1B-FWS-CHK-0156A, Complete insulation on valve. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18782 | Verified | 1-95 1B-FWS-V-0523B, Complete tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18783 | Verified | 1-96 1B-FWS-V-0055B, Complete valve insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18784 | Verified | 1-97 1B-FWS-V-6070B, Complete valve insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18785 | Verified | 1-98 1B-FWS-V-0155B, Complete bypass insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18786 | Verified | 1-99 1B-FWS-V-0158A, Complete bypass insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18787 | Verified | 1-100 3-1B-FWS-0508-151X1-PP-1.0 Needs personal protection. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18788 | Verified | 1-101 1B-FWS-AOV-0252, Bypass needs end cap, valve body needs completion | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-01 | INSUL-01 | PI18789 | Verified | 1-102 Complete insulation onall gas train vent pipes. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18790 | Verified | 1-103 1B-FWS-V-260B, Complete tube insulation top and bottom. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18791 | Verified | 1-104 12 inch fuel gas line 210, complete cladding. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18792 | Verified | 1-105 1B-see white flag, complete tube insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18793 | Open | 1-106 1B-FWS-V-0271, four valves in a row, complete insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const
INSUL-01 | INSUL-01 | PI18794 | Verified | 1-107 Complete all insulation above boiler feedwater buildings. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18795 | Verified | 1-108 Insulate drain fom sample building 1B. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18796 | Verified | 1-109 Insulater demin line at sample building 1B. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18797 | Verified | 1-110 Complete antisweat on gas train 1B, blankets, end caps, etc.. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18798 | Verified | 1-111 Complete insulation on due point heater skid. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18799 | Verified | 1-112 Complete fuel gas heater skid insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-21 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18800 | Verified | 1-113 Complete gas scrubber skid insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-05-12 | Eric Policarpio | 2021-05-12 | John Watts
INSUL-01 | INSUL-01 | PI18801 | Verified | 1-114 Complete inlet filter skid insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18802 | Verified | 1-115 90 degree elbow cladding has come apart, HP Steam main pipe rack and finger rack. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18803 | Cleared | 1-116 1B-CRS-PIT-0030, complete tubing insulation at CRS conection. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-07-20 | Richard McSpadden | 2021-07-23 | John Watts
INSUL-01 | INSUL-01 | PI18804 | Verified | 1-117 HP-Water Flange, west side 15 foot elevation needs to be insulated. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18805 | Verified | 1-118 1B-MSS-PIT-0030, Complete tubing insulation at MSS connection. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-05-12 | Eric Policarpio | 2021-05-12 | John Watts
INSUL-01 | INSUL-01 | PI18806 | Verified | 1-119 MSS 90 degree elbow cladding has come apart at expansion loopabove gas train. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18807 | Verified | 1-120 Hot reheat 90 degree onto main pipe rack cladding coming apart. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-01 | INSUL-01 | PI18808 | Verified | 1-121 FWS line not complete above CTG 1B in main pipe rack. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18809 | Verified | 1-122 FWS line not complete middle main pipe rack. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18810 | Verified | 1-123 1BMBL03AA923, complete drain line insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18811 | Verified | 1-124 Cladding coning apart horizontal run cooling air intake deck. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18812 | Verified | 1-125 1BMBL03AA921, complete drain line insulation | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18813 | Verified | 1-126 Cladding coming apart vertial run cooling air 90 degree elbow. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18814 | Verified | 1-127 Service water riser insulate heat trace, intake deck evap cooler control skid reinstall blankets on vendor instruments. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-07-21 | Richard McSpadden | 2020-08-05 | Mike Tabbert
INSUL-01 | INSUL-01 | PI18815 | Verified | 1-128 Riser going into intake, move band away from support. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18816 | Verified | 1-129 CTS calking at exhuast fans | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18817 | Verified | 1-130 CTS cladding coming apart at exhuast fans | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18818 | Verified | 1-131 insulate drain and water connection to shower at control package B | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18819 | Verified | 1-132 2-1B-CTS-0110-15201-PP, 2-1B-CTS-0101-60201-PP, 1-1B-CTS-0116-15201-PP, Needs personal Protection. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-01 | INSUL-01 | PI18875 | Verified | 1B CRS. Damage and gaps in cladding, three locations, Ele. 531-10 | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18876 | Verified | 1B HRSG Sampling and IPS PV at Ele. 531-10 platform #22 SW Corner of HRSG 1B | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18877 | Verified | 1B HRSG IPS down-comer, finish transition, Ele. 544 | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const | 2021-05-12 | Eric Policarpio | 2021-05-12 | John Watts
INSUL-01 | INSUL-01 | PI18878 | Verified | 1B MSS, gaps in cladding at Ele. 539, two items, one located in horizontal elbow to finger rack, one located on underside of elbow on down comer. | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18879 | Verified | 1B-IPS-PV-8303, complete insulation of valve body. | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18880 | Verified | HRSG 1B Sampling system, Complete insulation and cladding | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18881 | Open | HRSG 1B Sampling system, Complete heat trace insulation | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const
INSUL-01 | INSUL-01 | PI18882 | Verified | HRSG 1B Sampling system, Complete insulation and caulk end caps | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18883 | Verified | HRSG 1B Sampling system, Cualk required at numerous loactions, valves, transitions etc. | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-01 | INSUL-01 | PI18884 | Verified | 1B-HRSG, Ele. 556-4, Complete insulation on FWS line through grating. May require enlarging the hole through the grating. | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-01 | INSUL-01 | PI18885 | Open | 1B HRSG Elev 556-4, Complete tubing insulation | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const
INSUL-01 | INSUL-01 | PI18886 | Open | 1B HRSG Elev 556-4, Complete insulation 1B-FWS-CHK-8050 | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const
INSUL-01 | INSUL-01 | PI18887 | Open | 1B HRSG Elev 556-4, Complete insulation at HTS Valves 1B-IPS-V-8312 A/B | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const
INSUL-01 | INSUL-01 | PI18888 | Open | 1B HRSG Elev 500, complete all A-Tape at sample bundles. | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const
INSUL-01 | INSUL-01 | PI18889 | Verified | 1B HRSG Elev 500, complete insulation cooling water | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-01 | INSUL-01 | PI18890 | Verified | 1B HRSG Elev 500, complete all complete all insulation heat trace at sample tubing | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-01 | INSUL-01 | PI18891 | Verified | 1B HRSG Elev 578-2, 1B-MBL-V-8123 Complete insulation at heat traced valve body. | C | Q | Richard McSpadden | PCI | 2020-07-02 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI18907 | Verified | 2-1 MSS end cap needs to be installed, top of HRSG | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18908 | Verified | 2-2 1A-SSS-SCL-0600 Tube bundle needs insulation both ends | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18909 | Verified | 2-3 1A-SSS-SCL-0500, Tube bundle needs insulation both ends. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18910 | Verified | 2-4 1A-MSS-V-8430, Tube bundle needs insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18911 | Verified | 2-5 1A-MSS-V-8131, Tube bundle needs insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18912 | Verified | 2-6 1A-MSS-PV-8129, Valve needs insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18913 | Verified | 2-7 1A-HRS-V-8427, Valve needs insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18914 | Verified | 2-8 1A-MSS-SRV-8128, Valve needs insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18915 | Verified | 2-9 1A-SSS-V-8426, Tube bundle needs insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18916 | Verified | 2-10 Insulate flanges on CRS pipe. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-02 | INSUL-02 | PI18917 | Open | 2-11 Insulate drain on CRS pipe. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI18918 | Verified | 2-12 1A-SSS-V-0721, Caulk tube insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18919 | Verified | 2-13 1A-MSS-V-8038, Tube bundle needs insulation | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18920 | Verified | 2-14 1A-MSS-V-8119, Insulate condensate pots and tubing. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18921 | Verified | 2-15 1A-SSS-V-8061, Insulate tube bundle and tubing that is heat traced. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18922 | Verified | 2-16 Insulate flanges on MSS pipe. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-02 | INSUL-02 | PI18923 | Verified | 2-17 1A-FWS-V-8122, Insulate valve. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18924 | Open | 2-18 1A-FWS-CHK-8117, Insulate Valve. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI18925 | Verified | 2-19 1A-FWS-V-8116D, Insulate tube bundle. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18926 | Verified | 2-20 1A-FWS-V-8116B, Insulate tube bundle. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18927 | Verified | 2-21 1A-FWS-V-8144, Insulate valve up to flange. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18928 | Verified | 2-22 1A-CRS-V-8434, Need end cap on insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18929 | Verified | 2-23 Support MI cable splice, tied with rope now. | C | E | Richard McSpadden | TRI | 2020-07-14 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18930 | Verified | 2-24 1A-FWS-V-8416, Insulate and hard cover replace MI cable on flanges. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18931 | Verified | 2-25 1A-FWS-V-8413C, Insulate tube bundle. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18932 | Open | 2-26 1A-MSS-V-8101, Insulate pipe through decking, need decking cut. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI18933 | Verified | 2-27 1A-MSS-JB-8012, Insulate water column. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI18934 | Verified | 2-28 1A-MSS-V-8071, Insulate water column. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI18935 | Verified | 2-29 1A-MSS-V-8071, Complete insulation on tube bundles. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18936 | Verified | 2-30 Water drum penetration needs to be completed. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18937 | Open | 2-31 1A-HTS-CAB-0314, MI Cable is obstructing ladder, Triad to reroute | C | E | Richard McSpadden | TRI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI18938 | Verified | 2-32 1A-HTS-CAB-0314, Caulk tube bundle insulation in this area. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18939 | Verified | 2-33 1A-HBH-CHK-8013, Insulate tube bundles, finish elbows. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18940 | Verified | 2-34 1A-MSS-V-8110, Insulate elbow and caulk tube bundle. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18941 | Verified | 2-35 1A-MSS-V-8059 / 8047 Caulk all tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18942 | Verified | 2-36 1A-MSS-V-8059 / 8047, repair damage. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18943 | Verified | 2-37 1A-MSS-V-8114, Caulk all tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18944 | Verified | 2-38 1A-IPS-V-8235 / 8223, Complete all tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18945 | Verified | 2-39 1A-IPS-V-8235 / 8223, Insulate condensate pot. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18946 | Verified | 2-40 1A-SSS-SRV-0220, Complete tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18947 | Verified | 2-41 1A-SSS-V-8718, Complete tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18948 | Verified | 2-42 1A-LPS-V-8714, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18949 | Closed | 2-43 1A-LPS-MOV-8710, Complete tubing insulation | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-07-26 | Richard McSpadden | 2021-07-27 | John Watts
INSUL-02 | INSUL-02 | PI18950 | Verified | 2-44 1A-MSS-V-8016, Complete tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18951 | Verified | 2-45 1A-LPS-V-8709, Complete all the insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18952 | Verified | 2-46 1A-LPS-V-6797, Complete valve body insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI18953 | Verified | 2-47 1AMSS-MOV-8014, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18954 | Cleared | 2-48 1A-MSS-SRV-8707, Complete piping insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden
INSUL-02 | INSUL-02 | PI18955 | Verified | 2-49 1A-LPS-SRV-8707, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18956 | Verified | 2-50 1A-IPS-V-8307, Cualk tube insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18957 | Verified | 2-51 1A-SSS-V-8081, Compete tube bundle insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18958 | Verified | 2-52 1A-MBS-V-8904, Complete tube bundle insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18959 | Verified | 2-53 1A-MSS-V-8018, Complete tube bundle insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18960 | Verified | 2-54 Incomplete IP insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18961 | Open | 2-55 1A-MSS-SRV-8043, Restore blanket insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-07-26 | Richard McSpadden | 2021-07-27 | John Watts
INSUL-02 | INSUL-02 | PI18962 | Verified | 2-56 1A-LPS-MOV-8311 / 8308, Complete insulation on valves. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI18963 | Open | 2-57 1A-LPS-MOV-8308 Bypass, complete insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI18964 | Verified | 2-58 1A-IPS-V-8241 / 42, Complete condensate pot and tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18965 | Verified | 2-59 1A-IPS-JB-8208, Insulate water column. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18966 | Verified | 2-60 1A-IPS-V-8241, Complete insulation at drum penetration. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18967 | Verified | 2-61 1A-IPS-V-8239, Complete condensate and pot insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18968 | Verified | 2-62 1A-IPS-V-8237, Complete tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18969 | Verified | 2-63 1A-IPS-V-8273, Complete tube bundle insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18970 | Verified | 2-64 1A-FWS-V-0215, 8207A/8214/8208, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18971 | Verified | 2-65 1A-FWS-V-8207D, Complete tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18972 | Verified | 2-66 1A-FWS-V-8206, Complete tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18973 | Open | 2-67 1A-CNM-V-8572, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI18974 | Verified | 2-68 1A-LPS, Complete water column, condensate pot and all tubing. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18975 | Verified | 2-69 1A-SSS-V-8529, Complete tube bundle insulation and flange connection. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18976 | Verified | 2-70 1A-CNM-TV-8505, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18977 | Verified | 2-71 1A-CNM-V-8503, Complete tube bundle insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18978 | Verified | 2-72 1A-CNM-V-8522, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI18979 | Verified | 2-73 1A-CNM-V-8524, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18980 | Open | 2-74 1A-CNM-MOV-8571, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI18981 | Open | 2-75 1A-CNM-CHK-8501, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI18982 | Open | 2-76 1A-CNM-V-8522, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI18983 | Verified | 2-77 1A-LPS-V-8618, Complete tube bundle insulation, condensate pot and valve piping. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18984 | Verified | 2-78 1A-FWS-CHK-8201, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18985 | Verified | 2-79 1A-FWS-MOV-800, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI18986 | Verified | 2-80 1A-FWS-V-8008, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-25 | Eric Policarpio | 2020-11-25 | Dave Goldak
INSUL-02 | INSUL-02 | PI18987 | Verified | 2-81 1A-SSS--V-0321, Complete tube bundle insulation, condensate pot and valve pipind. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18988 | Verified | 2-82 1A-LPS-V-8601, Complete tube bundle insulation, support heat trace conduit. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18989 | Verified | 2-83 1A-SSS-V-0922, Valve will not operate with cladding. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18990 | Verified | 2-84 1A-IPS-V-8205B, Drum level site gauge not insulated. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI18991 | Verified | 2-85 AFS piping connection to HRSG blanket coming loose. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18992 | Verified | 2-86 1A-FWS-V-0578B, Two 1 1/2" Lines not insulated. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18993 | Verified | 2-87 Insulation not cladded. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18994 | Verified | 2-88 1A-FWS-HNR-0613, Hanger not insulated, pipe supports under cable tray not insulated. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18995 | Verified | 2-89 1X-FWS-V-8002E, Reinsulate heat trace. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18996 | Verified | 2-90 Insulate drains below cable tray. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18997 | Verified | 2-91 Condensate pots and tube bundles on finger rack need insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18998 | Verified | 2-92 Tube bundle needs insulation main steam at finger rack. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-02 | INSUL-02 | PI18999 | Verified | 2-93 Caulk trim on down comers to blow down tank. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19000 | Verified | 2-94 AFS inlet pipe to HRSG missing blankets. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI19001 | Verified | 2-95 1A-MBS-V-8902C, Complete tube bundle insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19002 | Verified | 2-96 Drain cladding coming apart. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19003 | Verified | 2-97 1A-MBL-MOV-8021, 50' elevation finish cladding, fix penetration in grating. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19004 | Closed | 2-98 30' elevation support needs insulation fill in hole. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-07-26 | Richard McSpadden | 2021-07-27 | John Watts
INSUL-02 | INSUL-02 | PI19005 | Verified | 2-99 Gas train anti sweat needs end cap at V-8103 | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19006 | Verified | 2-100 1A-FGS-V-0260 / 63 blanket is to small, gap inbetween blankets. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19007 | Verified | 2-101 Need end caps and blankets gas train bypass line. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19008 | Verified | 2-102 1A-FGS-PCV-0260A, Valve and flange blanket to small. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19009 | Verified | 2-103 SRV, anti seat pipe to valve, 1A-FGS-V-0280B remove heat trace. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19010 | Verified | 2-104 Flange blanket below SRV to small. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19011 | Verified | 2-105 1A-FGS-FIT-8100, Blanket to small. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19012 | Verified | 2-106 Blow down restoration per entergy, at blow down tank. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19013 | Open | 2-107 1AMBL-V-8114, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19014 | Open | 2-108 Reheater drain , bos out for beam flange movement and caulk joint below. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-07-27 | Richard McSpadden | 2021-07-29 | John Watts
INSUL-02 | INSUL-02 | PI19015 | Verified | 2-109 1A-ASF-CHK-8074 / V-6075, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI19016 | Verified | 22-110, HP water, Caps need to be installed at 4 places at entrance to bottom of HRSG. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19017 | Verified | 2-111 1A, Service water at blow down sump, insulate all tubing. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI19018 | Verified | 2-112 1A-MBL-V-0014, valve will not operate with cladding. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI19019 | Verified | 2-113 Econimizer drains need end caps at entrance to HRSG. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19020 | Verified | 2-114 Finish pipe insulation econimizer drain | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19021 | Open | 2-115 1A-ASF-V-8264 / CHK-8263, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19022 | Verified | 2-116 1A-MBL-V-8266, Caulking of all joints in area. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19023 | Verified | 2-117 1A-MBL-V-8645, Complete pipe insulation, caulk all joints. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI19024 | Open | 2-118 1A-ASF-CHK-8643 / 8644 Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19025 | Verified | 2-119 1A-Down comer from IP steam drum insulate flange. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19026 | Cleared | 2-120 1A-MBL_LSH-8705 / LSH-8305, Insulate flanges , MBL-V-8301 Insulate heat trace. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2021-07-29 | John Watts
INSUL-02 | INSUL-02 | PI19027 | Verified | 2-121 1A Sample building, insulate all sample tubing, insulate all chiller piping. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19028 | Verified | 2-122 1A HP water storage drum pipe hanger needs complete insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19029 | Verified | 2-123 1A-CRS-PIT-8401, Complete tube bundle insulation and root valve piping. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19030 | Verified | 2-124 1A South west corner 30' elevation cladding coming apart. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19031 | Verified | 2-125 1A Service water at gas purge building needs valve cuaked. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19032 | Verified | 2-126 Fuel gas filter inlet and outlet flange needs insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19033 | Verified | 2-127 Fuel gas scrubber flanges need insulation, fuel gas scrubber valves (3) need insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-02-01 | Eric Policarpio | 2021-02-01 | Dave Goldak
INSUL-02 | INSUL-02 | PI19034 | Verified | 2-128 Fuel gas orfice flange needs insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19035 | Verified | 2-129 1A-FWS-V-0265B, Complete pipe insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19036 | Verified | 2-130 1A Fuel gas drain end cap and cualk at heater. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19037 | Verified | 2-131 1AMBP01AA702 fuel gas temperture control valve needs insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19038 | Verified | 2-132 1A Flow meter spool insulate all flanges. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19039 | Verified | 2-133 1A Gas vent line needs insulation completed. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19040 | Verified | 2-134 Complete lines on dew point heater that are heat traced. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19041 | Verified | 2-135 1A-FGS-V-0211 / 0210, Anti sweat blankets on inlet valve and flanges. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19042 | Verified | 2-136 Demin water to sample building, complete insulation on support shoe. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19043 | Verified | 2-137 90 degree elbow on fuel gas drain line needs insulation complete. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19044 | Verified | 2-138 Complete insulation on nitrogen purge line to gas. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19045 | Verified | 2-139 Insulate sample building drain line, demin line and potable water. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19046 | Verified | 2-140 1A Phosphate skid finish pipe and valve for connection to tote and connection to tank. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19047 | Verified | 2-141 Condensate valve at phosphate skid needs complete insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19048 | Verified | 2-142 Shower drain and connection point needs insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI19049 | Verified | 2-143 AA-BFP, Insulate suction and discharge lines. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-05-12 | Eric Policarpio | 2021-05-12 | John Watts
INSUL-02 | INSUL-02 | PI19050 | Verified | 2-144 AB-BFP, Insulate suction and discharge lines. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-05-12 | Eric Policarpio | 2021-05-12 | John Watts
INSUL-02 | INSUL-02 | PI19051 | Verified | 2-145 AA-BFP, Complete tube insulation under platform. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-15 | Eric Policarpio | 2021-01-15 | Dave Goldak
INSUL-02 | INSUL-02 | PI19052 | Verified | 2-146 AB-BFP, Complete tube insulation under platform. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-15 | Eric Policarpio | 2021-01-15 | Dave Goldak
INSUL-02 | INSUL-02 | PI19053 | Verified | 2-147 Service water screen deck 90 degree elbow fix cladding. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19054 | Verified | 2-148 FWS flange screen deck, insulate flange and tubing. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-02-22 | Eric Policarpio | 2021-02-22 | Dave Goldak
INSUL-02 | INSUL-02 | PI19055 | Open | All MI cables on screen deck need to be routed neatly. | C | E | Richard McSpadden | TRI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19056 | Verified | Heat trace cables hanging out of conduit screen deck. | C | E | Richard McSpadden | TRI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19057 | Verified | 2-149 1A-HTS-CAB-0204, Complete tube bundle insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19058 | Open | 2-150 1A-FWS-AOV-0265, FV-0269, V-0271, CHK-0272, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19059 | Verified | 2-151 AB Insulation has been stripped off strainer and valves. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI19060 | Verified | 2-152 Three strainer valves need insulation complete. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-02 | INSUL-02 | PI19061 | Verified | 2-153 1B-FWS-CHK--0206B, 1A-FWS-V-0209B, 1A-FWS-V-0521, CHK-010156B, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-07-26 | Richard McSpadden | 2021-07-27 | John Watts
INSUL-02 | INSUL-02 | PI19062 | Verified | 2-154 FWS-V-0209A, CHK-0156A, CHK-0206A, V-0521, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-02-22 | Eric Policarpio | 2021-02-22 | Dave Goldak
INSUL-02 | INSUL-02 | PI19063 | Verified | 2-155 MI Cable needs to be reinstalled on1B-FWS-SRV-0549. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI19064 | Verified | 2-156 Area above AA strainer, complete all tube bundle insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19065 | Verified | 2-157 FWS-V-0054A, 55A,70 Complete valve insulation, blanket stripped off of strainer. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI19066 | Verified | 2-158 Insulate large flange water drum down comer. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19067 | Open | 2-159 Deicing pipe inlet deck underside of 90 degree elbow needs caulk and topside coming apart. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-07-27 | Richard McSpadden | 2021-07-29 | John Watts
INSUL-02 | INSUL-02 | PI19068 | Verified | 2-160 Deicing pipe inlet deck 90 degree elbow horizontal cladding coming apart. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-02-01 | Eric Policarpio | 2021-02-01 | Dave Goldak
INSUL-02 | INSUL-02 | PI19069 | Verified | 2-161 1AMBL03AA921, Valves and piping need insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19070 | Open | 2-162 1AMBL03AA101, Valve flange needs insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19071 | Open | 2-163 1AMBL03AA704 Transition hard cover needs repair, cladding on south side of valve coming apart, valve flange need insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19072 | Verified | 2-164 1AMBL03AA934, Valves and piping need insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19073 | Verified | 2-165 South side of T cladding coming apart. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-02-01 | Eric Policarpio | 2021-02-01 | Dave Goldak
INSUL-02 | INSUL-02 | PI19074 | Verified | 2-166 Elbow going into inlet cladding coming apart, support cladding and insulation damaged from expansion, lower support needs caulk. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-02-01 | Eric Policarpio | 2021-02-01 | Dave Goldak
INSUL-02 | INSUL-02 | PI19075 | Verified | 2-167 1AMBL03AA924, Valves and piping need insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19076 | Open | 2-168 1AMBL03AA703, Valve needs flange insulated, cladding coming apart on south side, support shoe damaging cladding underside. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19077 | Verified | 2-169 Remove or complete service water riser heat trace at evap skid. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19078 | Verified | 2-170 Secure all heated blankets on evap skid. | C | Q | James Strange | PCI | 2020-07-14 | James Strange | Const | 2021-02-01 | Eric Policarpio | 2021-02-01 | Dave Goldak
INSUL-02 | INSUL-02 | PI19079 | Verified | 2-171 1A-FGS-V-319C, Gas vent line needs insulation complete under case cooling valve deck. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19080 | Open | 2-172 Case cooling valves need insulation complete, also line needs complete. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19081 | Verified | 2-173 Fuel gas vents 2-1A-CTS-0101-602D1, 2-1A-CTS-0110-152D1, 1-1A-CTS-0116-152D1, Require personal protection. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19082 | Verified | 2-174 Blanket coming loose on case cooling pipe entrance to CTG enclosure, cladding needs complete. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19083 | Verified | 2-175 Cladding coming loose main pipe rack behind cable tray MSS in rack. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19084 | Verified | 2-176 Caps on closed cooling water west side of generator, cope into horizontal. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI19085 | Verified | 2-177 Service water valve needs cladding and caulk. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19086 | Verified | 2-178 Deicing line 90 degree elbow behind lube oil enclosure cladding coming apart. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19087 | Verified | 2-179 Need flange blanket at entrance to CTG enclosure east side 6" pipe. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19088 | Verified | 2-180 1A-FWS-V-0532A, Cladding missing on riser to main pipe rack. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19089 | Verified | 2-181 Cooling air cooler flange at top needs blanket reattached. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19090 | Verified | 2-182 1A-HTS-CAB-0308, Complete all tubing insulation in area. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19091 | Verified | 2-183 1A-DWS-SWR-0016, Insulate drain and connection point to shower. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19092 | Open | 2-185 1A-CCW-V-0456B, 3 valves in area need modification to allow operation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19093 | Verified | 2-185 Service water valve at lube oil needs cladding and caulk. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19094 | Verified | 2-186 1AMBR01AA604, Insulate valves and piping. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-08-20 | Mike Tabbert | 2020-08-20 | Mike Tabbert
INSUL-02 | INSUL-02 | PI19095 | Verified | 2-187 Cooling air cooler pipe on top of cooler needs flange insulated and blanket adjusted, 90 degree elbow cladding coming apart top of pipe, 2 flanges on outlet south side, one flange on north side needs insulation. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI19096 | Verified | 2-188 Deicing top side of pipe insulation in between lube oil and CTG cladding coming apart. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19097 | Verified | 2-189 90 degree elbow east of control valve cladding coming apart. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19098 | Verified | 2-190 1B-HTS-CAB-0206, Tube bundles for each instrument need insulation at far end of tube. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-02 | INSUL-02 | PI19099 | Verified | 2-191 1AMBH05AA101, Valve needs flange insulated. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19100 | Verified | 2-192 Cooling air filter missing 1 halve of blanket at flange. | C | Q | Richard McSpadden | PCI | 2020-07-14 | Richard McSpadden | Const | 2020-11-17 | Eric Policarpio | 2020-11-17 | Dave Goldak
INSUL-02 | INSUL-02 | PI19169 | Verified | 1A-HRSG Ele 532, Northwest, FWS, Complete tubing insulation, Insulate pipe flange. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2021-02-01 | Eric Policarpio | 2021-02-01 | Dave Goldak
INSUL-02 | INSUL-02 | PI19170 | Open | 1A-HRSG Ele 532, Northwest, Complete tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19171 | Open | 1A-HRSG Ele 540, Northwest, Install cladding band. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2021-07-27 | Richard McSpadden | 2021-07-29 | John Watts
INSUL-02 | INSUL-02 | PI19172 | Verified | 1A between HRSG and finger rack, ele. 540, insulate FWS check valve. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19173 | Verified | 1A HRSG Ele 555 Nortwest, repair / replace damaged FWS insulation and cladding. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2021-02-01 | Eric Policarpio | 2021-02-01 | Dave Goldak
INSUL-02 | INSUL-02 | PI19174 | Open | 1A HRSG Ele 577 Northwest, insulate 1A-FWS-V-8614 to flanges on body. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19175 | Open | 1A HRSG Ele 577 Northwest, Complete insulation at HTS bundle splice, behind 1A-HTS-CAB-0105 | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19176 | Open | 1A HRSG Ele 577 Northwest, Insulate HTS at 1A-SSS-V-8615 & 8616 | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19177 | Verified | 1A HRSG southwest ele 519 replace missing cladding band. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19178 | Verified | 1A-HRSG Southwest Ele 531-10, Insulate 1A-IPS-PV-8303. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19179 | Verified | 1A-CRS at finger rack repair damage. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19180 | Verified | 1A CRS in finger rack Ele 532, Repair CRS cladding damage location #2 | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19181 | Verified | 1A CRS piping southwest Ele 540, Repair separation in cladding above finger rack. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19182 | Open | 1A HRSG Southwest Ele 532, Install band and close end of cladding at MSS down comer elbow. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19183 | Verified | 1A HRSG HRS down comer ele 540, Repair cladding damage underside of down comer elbow. Location #1 | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2021-02-01 | Dave Goldak
INSUL-02 | INSUL-02 | PI19184 | Verified | 1A HRSG HRS down comer (horizontal) Elev. 540, Repair damage in cladding Location #2 | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19185 | Verified | 1A HRSG Southwest El. 540, Install missing insulation and cladding at pipe support. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19186 | Verified | 1A Finger rack southwest Ele 544, Complete LPS heat trace / insulation, repair severed MI cable. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2021-02-01 | Eric Policarpio | 2021-02-01 | Dave Goldak
INSUL-02 | INSUL-02 | PI19187 | Open | 1A HRSG sothwest Ele. 556, Complete FWS insulation in progress, Insulate 1A-FWS-CHK-8060 body. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const
INSUL-02 | INSUL-02 | PI19188 | Verified | 1A-HRSG Southwest Ele. 578, Seal/Caulk around valve handles. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19189 | Verified | 1A HRSG Southwest Ele. 588, Under main deck HP steam drum, Replace incorrect insulation at thermowell, Replace missing cladding. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-02 | INSUL-02 | PI19190 | Verified | 1A HRSG Southwest (under top deck HRS piping) Ele. 595, Complete small bore insulation and cladding under top deck HRS pipe. | C | Q | Richard McSpadden | PCI | 2020-07-21 | Richard McSpadden | Const | 2021-07-26 | Richard McSpadden | 2021-07-27 | John Watts
INSUL-03 | INSUL-03 | PI18820 | Verified | 3-1 Complete service water valve, operator deck south east. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18821 | Verified | 3-2 HP steam bypass, complete insulation root valve to tubing. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18822 | Verified | 3-3 1X-FWS-V-8002E, Complete tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18823 | Verified | 3-4 1B-MSS-V-0014, Insulate drain flange and two valve bodies AOV-86 and 87 | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-12-08 | Eric Policarpio | 2020-12-08 | Dave Goldak
INSUL-03 | INSUL-03 | PI18824 | Verified | 3-5 1A-MSS-V-0043, Insulate drain flange and two valve bodies AOV-86 and 87. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18825 | Verified | 3-6 1X-FWS-V-8001B, Complete tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18826 | Verified | 3-7 1A-MSS-V-0020, Complete valve and pipe insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18827 | Verified | 3-8 1B-MSS-V-0020, Complete valve and pipe insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18828 | Verified | 3-9 1A-HP-steam bypass, complete root valve and tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18829 | Verified | 3-10 1A-HRSG-HP-Feedwater, caulking around plugs and pipe support. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18830 | Verified | 3-11 1A-MSS-V-0025, Complete insulation on valve and flange to west and caulk joints. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18831 | Verified | 3-12 1B-HRS-TV-0087, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18832 | Verified | 3-13 1B-HRS-V-0081B, Complete tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18833 | Verified | 3-14 1A-HRS-V-0081B, Complete tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18834 | Verified | 3-15 1A-HRS-TV-0087, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18835 | Verified | 3-16 1A-HRS-V-0088, Complete bypass insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18836 | Verified | 3-17 1B-HRS-V-0088, Complete bypass insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18837 | Verified | 3-18 1B-HRS-V-0025, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18838 | Verified | 3-19 1A-HRS-V-0025, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18839 | Verified | 3-20 1A-HRH-Bypass, Complete insulation of flanges and vent line. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18840 | Verified | 3-21 1B-HRH-Bypass, Complete insulation of flanges and vent line. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18841 | Verified | 3-22 10-CCW-V-0158A, Complete valve and flange insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18842 | Verified | 3-23 10-CCW-T-0300, Complete insulation at water column. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18843 | Verified | 3-24 1B-MSS-MOV-1052, Complete valve and pipe insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18844 | Verified | 3-25 1B-MSS-MOV-0050, Complete valve insulation and small diameter 90 dgree elbow. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18845 | Verified | 3-26 1B-HRS-V-0020/0021, Complete valve insulation, cladding coming apart below valves. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18846 | Verified | 3-27 2-10-CCW-0188, Complete cladding of line. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18847 | Verified | 3-28 1B-LPS-MOV-0050, Complete valve insulation and bypass lines. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18848 | Verified | 3-29 1A-MSS-P40-0040, Complete line insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18849 | Open | 3-30 1A-CRS-V-0015, Complete valve flange insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const
INSUL-03 | INSUL-03 | PI18850 | Open | 3-31 1B-CRS-V-0015, Complete valve flange insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const
INSUL-03 | INSUL-03 | PI18851 | Verified | 3-32 1A-LPS-MOV-0050, Complete valve and bypass insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18852 | Verified | 3-33 HP Steam Below Grading, insulate root valves and pots to tubing. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-12-08 | Albert Burge | 2020-12-08 | Dave Goldak
INSUL-03 | INSUL-03 | PI18853 | Open | 3-34 1A/1B-CRS-MOV-0010, Complete flange insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const
INSUL-03 | INSUL-03 | PI18854 | Verified | 3-35 Complete tube insulation NE Mez | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-02-22 | Eric Policarpio | 2021-02-22 | Dave Goldak
INSUL-03 | INSUL-03 | PI18855 | Verified | 3-36 1CCold Reheat, Complete insulation on small valves (2) below grading, drain level pots complete insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2021-02-01 | Eric Policarpio | 2021-02-01 | Dave Goldak
INSUL-03 | INSUL-03 | PI18856 | Verified | 3-37 Complete root valve and tubing insulation below grading at 1A-MSS-MOV-0050. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18857 | Verified | 3-38 1B-HRS-V-0020/21, Complete insulation on valves and line. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18858 | Verified | 3-39 1A-MSS-MOV-0050, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18859 | Verified | 3-40 1C-ASF-V-0030, Complete valve body insulation, bypass valves and line. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18860 | Verified | 3-41 1C-ASF-PV-0035, Complete valve body insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18861 | Verified | 3-42 1C-ASF-V-0012, Complete valve body insulation and bypass valves and lines. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18862 | Verified | 3-43 1C-ASF-PIT-0018A, Complete tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18863 | Verified | 3-44 1C-ASF-V-0017, Complete valve and bypass insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18864 | Verified | 3-45 1C-ASF-V-0010, Complete valve and bypass insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18865 | Verified | 3-46 1C-ASF-SRV-0019, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI18866 | Verified | 3-47 1C-ASF-DESH-0120, Complete flange insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18867 | Open | 3-48 1C-ASF-CHK-9710 / 1C-ASF-MOV-9700, Complete flange insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const
INSUL-03 | INSUL-03 | PI18868 | Verified | 3-49 1C-ASF-V-0181, Complete valve and bypass line (2). | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-12-16 | Eric Policarpio | 2020-12-16 | Dave Goldak
INSUL-03 | INSUL-03 | PI18869 | Verified | 3-50 LP steam to bypass condenser, insulate all flanges. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18870 | Verified | 3-51 1C-HTS-CAB-0201, Complete tube insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2021-02-01 | Dave Goldak
INSUL-03 | INSUL-03 | PI18871 | Open | 3-52 1C-STE-AOV-9550, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const
INSUL-03 | INSUL-03 | PI18872 | Verified | 3-53 10-STE-MOV-9540, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-12-16 | Eric Policarpio | 2020-12-16 | Dave Goldak
INSUL-03 | INSUL-03 | PI18873 | Verified | 3-54 Insulate spool flange above 10-STE-MOV-9540. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI18874 | Verified | 3-55 Condenser vacuum vents need personal protection. | C | Q | Richard McSpadden | PCI | 2020-06-30 | Richard McSpadden | Const | 2020-12-08 | Eric Policarpio | 2020-12-08 | Dave Goldak
INSUL-03 | INSUL-03 | PI19101 | Verified | 3-200 1C-MSS-FY-0040, Complete cladding on valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI19102 | Verified | 3-201 1C-MSS-V-0013, Complete valve insulation. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2021-02-22 | Dave Goldak
INSUL-03 | INSUL-03 | PI19103 | Verified | 3-202 Main steam valve blankets need to be reattached, reposition top blanket after scaffold is down. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19104 | Verified | 3-203 Main steam sample / drain valves need cladding on insulation, 2 places. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19105 | Verified | 3-204 1C-MSS-FY-0030, Valve insulation needs cladding complete. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19106 | Verified | 3-205 1C-MSS-V-0030, valve needs insulation complete. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19107 | Verified | 3-206 1C-SDS-MOV-9010B, 2 locations cladding needs repair coming apart from expansion. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19108 | Verified | 3-207 1C-HRS-FY-0030 / 40, Valves and piping need insulation replaced, also drain pot on 40. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19109 | Verified | 3-208 1C-STE-MOV-9505, 9501, 9503, Three valves need insulation and cladding complete. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19110 | Verified | 3-209 1C-ASF-LAHH-0075, Insulate drain level columns and ball valve. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-16 | Eric Policarpio | 2020-12-16 | Dave Goldak
INSUL-03 | INSUL-03 | PI19111 | Verified | 3-210 1C-HTS-CAB-0202, Insulate tube bundle at root valve. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19112 | Verified | 3-211 1C-SSS-SC1-0100, Insulate all tubing in area and tube bundle at far end of tube, Insulate closed cooling water valves in area. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19113 | Verified | 3-212 Hot reheat drip legs A&B, reinsulate, Entergy asked to remove insulation. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19114 | Verified | 3-213 superheater spray, complete insulation tap to 1C-ASF-V-0058. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19115 | Verified | 3-214 Insulate steam drain line at east side STG, main pipe rack. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19116 | Verified | 3-215 Remove scaffold leg, complete cladding east side STG main pipe rack. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19117 | Verified | 3-216 Superheater spray to 1C-ASF-DESH-0110, complete line insulation. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19118 | Verified | 3-217 1C-CRS-V-0041, Complete insulationat heat trace. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19119 | Verified | 3-218 1C-CRS-TE-0042, Complete insulation at thermowell. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19120 | Verified | 3-219 Complete insulation at heat trace #3415 Mezz Deck. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19121 | Verified | 3-220 Complete heat trace insulation #3287. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19122 | Verified | 3-221 Complete heat trace insulation low preasure steam. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI19123 | Verified | 3-222 Insulation blanket at strainer door, LPS. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI19124 | Verified | 3-223 1C-STE-MOV-9509, 1C-STE-PV-9507, Complete valve insulation to flange. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19125 | Verified | 3-224 1C-HTS-CAB-0203, Complet heat trace and insulation 2 locations. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19126 | Verified | 3-225 1C-HTS-CAB-0205, Complete heat trace insulation 1 location. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19127 | Verified | 3-226 1C-LPS, Insulate drain level columns 2 locations. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-16 | Eric Policarpio | 2020-12-16 | Dave Goldak
INSUL-03 | INSUL-03 | PI19128 | Verified | 3-227, Complete insulation, drain line below LPS valve tag 3402. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19129 | Verified | 3-228 1C-HRS-V-0022, Complete insulation on valves, line and all tubing in this area. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19130 | Verified | 3-229 1C-STE-AOV-9512, 1C-STE-MOV-9510, Complete valve insulation restoration. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19131 | Verified | 3-230 1C-LPS-LEHL-0060, Insulate drain level columns. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-16 | Eric Policarpio | 2020-12-16 | Dave Goldak
INSUL-03 | INSUL-03 | PI19132 | Verified | 3-231 1C-SDS-AOV-9620A, Insulate valve body. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-14 | Mike Tabbert | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19133 | Verified | 3-232 1C-SDS-AOV-9620B, Insulate valve body. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19134 | Verified | 3-233 Turbine casing drain, overhead lines paint is burnt off. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-08 | Eric Policarpio | 2020-12-08 | Dave Goldak
INSUL-03 | INSUL-03 | PI19135 | Verified | 3-234 1C-HRS-V-0025, Insulate valves and line, and all tubing in area above coming off turbine. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI19136 | Verified | 3-235 Service water valve and pipe finish insulation. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19137 | Verified | 3-236 Insulate 4 closed cooling water drain tubes underside of generator. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-08 | Eric Policarpio | 2020-12-08 | Dave Goldak
INSUL-03 | INSUL-03 | PI19138 | Verified | 3-237 10-CCW-V-0133, Insulate valve. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19139 | Verified | 3-238 Insulate vents and tubing CCW above heat exchanger. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-08 | Eric Policarpio | 2020-12-08 | Dave Goldak
INSUL-03 | INSUL-03 | PI19140 | Verified | 3-239 1A-HTS-CAB-0301, Insulate CCW valves, tubing and 90 degree elbowin area, level indicator east and west side of condenser. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-16 | Eric Policarpio | 2020-12-16 | Dave Goldak
INSUL-03 | INSUL-03 | PI19141 | Verified | 3-240 10-CCW-V-0121B, Insulate valves, caulk tubing insulation. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI19142 | Verified | 3-241 10-HTS-CAB-0108, Insulate valves, tubing, caulk tubing insulation, insulate top of safety relief valve that is heat traced area of heat exchangers. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI19143 | Verified | 3-242 10-HTS-CAB-0205, insulate tubing at root valve, insulate root valve that is heat traced. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI19144 | Verified | 3-243 10-CCW-V-0137, Insulate valve, insulate vent at top of pipe 10-CCW-V-0149A, 10-CCW-V-0101B, 10-CCW-V-0149B, 10CCW-V-0147B. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19145 | Verified | 3-244 1C-CCW-V-0216B, 0215B, Insulate valves and flange, insulate flange on south line. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19146 | Verified | 3-245 Complete insulation on stator cooling skid. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19147 | Verified | 3-246 West end of condensor, above and below grating, 12 valves need insulation, water columns need insulation, inlets to condensor need insulation. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI19148 | Verified | 3-247 Vacuum skid, complete all insulation. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-08 | Eric Policarpio | 2020-12-08 | Dave Goldak
INSUL-03 | INSUL-03 | PI19149 | Verified | 3-248 Lube oil heat exchangers area, insulate 3 drain valves on CCW piping. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19150 | Verified | 3-249 CCW line needs drain valve insulated above lighting panel. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const |  |  | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19151 | Verified | 3-250 Turbine drain lines at compressor need insulation 4 places, and on mez deck. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-08 | Eric Policarpio | 2020-12-08 | Dave Goldak
INSUL-03 | INSUL-03 | PI19152 | Verified | 3-251 1C-CCW-SRV-0326B, need insulated. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19153 | Verified | 3-252 Complete all insulation area from hydralic unit to condensor, floor to mez. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-08 | Eric Policarpio | 2020-12-08 | Dave Goldak
INSUL-03 | INSUL-03 | PI19154 | Verified | MI cable not terminated in hydralic unit area. | C | E | Richard McSpadden | TRI | 2020-07-20 | Richard McSpadden | Const | 2020-12-08 | Eric Policarpio | 2020-12-08 | Dave Goldak
INSUL-03 | INSUL-03 | PI19155 | Verified | 3-253 1.5-1C-STE-0019, Insulate pipe going into drain. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-03 | Eric Policarpio | 2020-12-03 | Dave Goldak
INSUL-03 | INSUL-03 | PI19156 | Verified | 3-254 1C-CNM-V-0030, 1C-SDS-V-0100, Insulate piping valves and drains. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-12-08 | Dave Goldak
INSUL-03 | INSUL-03 | PI19157 | Verified | 3-255 Circulating water, 4 root valves, 2 preasure relief valves need insulation. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19158 | Verified | 3-256 Insulate anylizers CCW at platform. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19159 | Verified | 3-257 Insulate potable water flange from underground at shower, insulate shower drain and connection point. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19160 | Open | 3-258 Condensate pump area, finish tubing, finish valves, finish piping and safety relief valve. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const
INSUL-03 | INSUL-03 | PI19161 | Verified | 3-259 Hot reheat above concondensate pumps, insulate water column drains, 2 one inch pipes all the way to compressors. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-12-08 | Eric Policarpio | 2020-12-08 | Dave Goldak
INSUL-03 | INSUL-03 | PI19162 | Verified | 3-260 Cold reheat valve above 1C-HTS-CAB-0200 needs insulation, cladding is coming apart north of valve. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19163 | Verified | 3-261 Complete insulation on steam drain line going under condensate lines. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19164 | Verified | 3-262 Complete insulation on service water line underground stub up east end STG. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19165 | Verified | 3-262 Trace and insulate sample tubes entrance to sample building 1C, demin line both ends. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2021-02-22 | Eric Policarpio | 2021-02-22 | Dave Goldak
INSUL-03 | INSUL-03 | PI19166 | Verified | 3-264 Need personal protection on legs of steam drains tank. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2021-02-22 | Eric Policarpio | 2021-02-22 | Dave Goldak
INSUL-03 | INSUL-03 | PI19167 | Verified | 3-265 Repair cladding on elbows, steam drain to underground. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2020-08-07 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-03 | INSUL-03 | PI19168 | Verified | 3-266 10-DWS-V-0100, Valve will not operate with cladding. | C | Q | Richard McSpadden | PCI | 2020-07-20 | Richard McSpadden | Const | 2021-01-15 | Eric Policarpio | 2021-01-15 | Dave Goldak
INSUL-04 | INSUL-04 | PI19191 | Verified | 4-1 10-RWS-AIT-0110, Caulk insulation blanket. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19192 | Verified | 4-2 10-RWS-AIT-0110, Caulk tube bundle insulation blanket. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19193 | Verified | 4-3 10-RWS-CAB-5000B, Condulet cover missing heat trace. | C | E | Richard McSpadden | TRI | 2020-07-31 | Richard McSpadden | Const | 2020-12-16 | Eric Policarpio | 2020-12-16 | Dave Goldak
INSUL-04 | INSUL-04 | PI19194 | Verified | 4-4 10-RWS-ARV-0103, Caulk insulation blanket. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19195 | Verified | 4-5 10-RWS-ARV-0109, Caulk insulation blanket. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19196 | Verified | 4-6 10-RWS-CP-0200, Insulate drain on skid. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19197 | Verified | 4-7 Caulk insulation blanket southwest corner flocculant line. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19198 | Verified | 4-8 Replace blankets around flocculent tank 3 places. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-04 | INSUL-04 | PI19199 | Verified | 4-9 Service water at aqueous ammonia needs caulking | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19200 | Verified | 4-10 Complete insulation at aqueous ammonia shower, drain and water connection. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-04 | INSUL-04 | PI19201 | Verified | 4-11 Insulate and caulk presure relief at aqueous ammonia water heater. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19202 | Verified | 4-13 1B Fuel gas filter seperator, complete skid insulation. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19203 | Verified | 4-14 1A Fuel gas filter seperator, complete skid insulation. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19204 | Verified | 4-15 Heat trace box, no power feed, east end of cooling tower. | C | E | Richard McSpadden | TRI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19205 | Verified | 4-16 Isulate over heat trace, east end cooling tower. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19206 | Verified | 4-17 Caulk valve for service water north end of cooling tower. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19207 | Verified | 4-18 Caulk heat trace box north end of cooling tower. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19208 | Verified | 4-19 Caulk heat trace box north end of cooling tower. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19209 | Verified | 4-20 Install band on chem feed pipe going under cooling tower make-up water pipe northwest corner cooling tower. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19210 | Verified | 4-21 Insulate anylizer probe. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19211 | Verified | 4-22 10-HTS-CAB-0100, Complete insulation of tube bundles. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19212 | Verified | 4-23 Recaulk joint coming down from cable tray northwest corner of cooling tower. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19213 | Verified | 4-24 Recaulk joint end of cable tray west end of cooling tower. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19214 | Verified | 4-25 Insulate probes north end of cooling tower sump. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2021-02-01 | Eric Policarpio | 2021-02-01 | Dave Goldak
INSUL-04 | INSUL-04 | PI19215 | Verified | 4-26 10-HTS-CAB-0300, complete insulation of tube bundles. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19216 | Verified | 4-27 Caulk tube bundles insulation under platform and above platform northside. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19217 | Verified | 4-28 Caulk tube bundles insulation under platform and above platform southside. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19218 | Verified | 4-29 Complete insulation at cooling tower chemical feed skids, and piping. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-12-16 | Eric Policarpio | 2020-12-16 | Dave Goldak
INSUL-04 | INSUL-04 | PI19219 | Verified | 4-30 Insulate presure relief valve, water heater at cooling tower chem feed. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-04 | INSUL-04 | PI19220 | Verified | 4-31 10-MWS-CP-1300, Complete skid insulation. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-04 | INSUL-04 | PI19221 | Verified | 4-32 Complete insulation shower drain and connection point at filter press. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-11-11 | Albert Burge | 2020-11-11 | Dave Goldak
INSUL-04 | INSUL-04 | PI19222 | Verified | 4-33 10-MWS-CP-1200, Complete insulation of flexable lines on skid. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-12-16 | Eric Policarpio | 2020-12-16 | Dave Goldak
INSUL-04 | INSUL-04 | PI19223 | Verified | 4-34 Leak on water heater at filter press, fix leak so insulation can be completed. | C | P | Tim Green | McD | 2020-07-31 | Tim Green | Const | 2020-10-22 | Jason Ezell | 2020-12-03 | Dave Goldak
INSUL-04 | INSUL-04 | PI19224 | Verified | 4-35 Caulk cladding around service air receiver drain. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19225 | Verified | 4-36 Sodium Hydroxide Tank, and skid, complete insulation. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-04 | INSUL-04 | PI19226 | Open | 4-37 Heat trace box should be rasied up along with drain before insulating, drain cover needs to be cut to fit. | C | E | Richard McSpadden | TRI | 2020-07-31 | Richard McSpadden | Const
INSUL-04 | INSUL-04 | PI19227 | Verified | 4-38 10-MWS-V-0805, Insulate spool at valve. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2021-01-05 | Eric Policarpio | 2021-01-05 | Dave Goldak
INSUL-04 | INSUL-04 | PI19228 | Verified | 4-39 Caulk blanket seams around 10-MWS-M-0100A. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19229 | Verified | 4-40 Cut tails on banding around 10-MWS-M-0100A. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19230 | Verified | 4-41 Caulk tube bundle insulation north east corner clarifier tank. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19231 | Verified | 4-42 Complete insulation onsluge tank drain. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19232 | Verified | 4-43 10-MWS-V-0035, Complete insulation at drain valve. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-04 | INSUL-04 | PI19233 | Verified | 4-44 Tube bundle insulation caukng at sludge tank skid. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19234 | Verified | 4-45 Sludge tank skid insulate 4 valves and 2 tube bundles. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-12 | Richard McSpadden | 2020-08-24 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19235 | Verified | 4-46 10-HTS-CAB-0101, Insulate tube bundle. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19236 | Verified | 4-47 Insulate pupms and lines north side of clarifier. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19237 | Verified | 4-48 10-MWS-P-0510A, Insulate pump and lines on north side disk filter west. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19238 | Verified | 4-49 Insulate anylizer at 10-MWS-V-0011. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19239 | Verified | 4-50 Insulate 10-MWS-AE-0012. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-04 | INSUL-04 | PI19240 | Verified | 4-51 Support conduit at 10-MWS-AE-0012 | C | E | Richard McSpadden | TRI | 2020-07-31 | Richard McSpadden | Const |  |  | 2020-12-03 | Dave Goldak
INSUL-04 | INSUL-04 | PI19241 | Verified | 4-52 10-MWS-Quill-0470, Leaking custic, insulation needs to be completed. | C | P | Tim Green | McD | 2020-07-31 | Tim Green | Const | 2020-10-22 | Jason Ezell | 2020-11-11 | Dave Goldak
INSUL-04 | INSUL-04 | PI19242 | Verified | 4-53 10-MWS-V-0014, Complete insulation of anylizer probe. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-04 | INSUL-04 | PI19243 | Verified | 4-59 Complete insulation area south of polymer building. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-12-16 | Eric Policarpio | 2020-12-16 | Dave Goldak
INSUL-04 | INSUL-04 | PI19244 | Verified | 4-60 10-MWS-CP-0220, Skid leaks, complete insulation. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-12-16 | Eric Policarpio | 2020-12-16 | Dave Goldak
INSUL-04 | INSUL-04 | PI19245 | Open | 4-61 Complete line insulation at Coagulant Tank. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const
INSUL-04 | INSUL-04 | PI19246 | Verified | 4-62 Complete insulation on dry polymer vacumm skid. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-12-16 | Eric Policarpio | 2020-12-16 | Dave Goldak
INSUL-04 | INSUL-04 | PI19247 | Verified | 4-63 Top of clarifier, cover heat trace raw water line, install drains on condulets. | C | E | Richard McSpadden | TRI | 2020-07-31 | Richard McSpadden | Const | 2021-02-01 | Eric Policarpio | 2021-02-01 | Dave Goldak
INSUL-04 | INSUL-04 | PI19248 | Verified | 4-64 Relocate heat trace box pump suction 10-SWS-M-0100B. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19249 | Verified | 4-65 Complete insulation of oily water seperator. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19250 | Verified | 4-66 Complete insulation of waste water area. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-11-17 | Richard McSpadden | 2020-12-03 | Dave Goldak
INSUL-04 | INSUL-04 | PI19251 | Verified | 4-67 Complete waste water shower drain and water connection point. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19252 | Verified | 4-68 Complete service water piping north side demin building. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-04 | INSUL-04 | PI19253 | Verified | 4-69 Complete insulation 3 feet inside demin building, service water and chem lines. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-11-11 | Eric Policarpio | 2020-11-11 | Dave Goldak
INSUL-04 | INSUL-04 | PI19254 | Verified | 4-70 Heat Trace and insulate potable water entrance into demin building. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2021-05-24 | Eric Policarpio | 2021-05-24 | Keith Pollock
INSUL-04 | INSUL-04 | PI19255 | Verified | 4-71 All pipe entrance, north east corner of demin building, do they need heat trace and insulation. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert
INSUL-04 | INSUL-04 | PI19256 | Verified | 4-72 10-HTS-CAB-0104, Complete tube bundle insulation and presure gauge line. | C | Q | Richard McSpadden | PCI | 2020-07-31 | Richard McSpadden | Const | 2020-08-14 | Richard McSpadden | 2020-08-14 | Mike Tabbert